## User Interface
This sheet provides typical values of Liquid pressure recovery factor, FL, Valve style modifier, Fd and Differential pressure
ratio of incipient cavitation, xFz, based on flow capacity and valve size for use in IEC noise calculations. These values
are based on a reliable sources, but will vary from one manufacturer to another. For Fd calculations, automatic entry of valve
rated capacity is only valid for valve sizes on the "Tables" tab.
| Unit Selection | Flag # | Flag Value | Options |  |  |  |  | Callculation of Cv/d2
| Valve flow Capacity | 1 | 1 | 1 = Cv 2 = Kv |  |  |  |  | Valve cap. In Cv | 180 | 180 | 180 | 180
| Valve size | 2 | 1 | 1 = inch, 2 = DN |  |  |  |  | Valve size in Inch | 4 | ===> | ===> | ===>
|  | Case 1 | Case 2 | Case 3 | Case 4 |  |  |  | Cv/d2 | 11.25 | 11.25 | 11.25 | 11.25
| Flow capacity: Cv | 180 | 180 | 180 | 180 | Data input
| Valve size: inch | 4 | ======> | ======> | ======> | Final results
Automatically filled or
Typical FL values based on the flow capacity and valve size above | [5 empty] | replaced by user with
known value
| Valve type | Liquid pressure recovery factor, FL
| Globe, 4 port cage | 0.82773 | 0.82773 | 0.82773 | 0.82773
| Globe, Parabolic plug | 0.84183 | 0.84183 | 0.84183 | 0.84183
| Rotary eccentric plug | 0.78425 | 0.78425 | 0.78425 | 0.78425
| Segment ball | 0.81962 | 0.81962 | 0.81962 | 0.81962
| Butterfly, high Perf. eccentric | 0.75614 | 0.75614 | 0.75614 | 0.75614
| Full ball | 0.82373 | 0.82373 | 0.82373 | 0.82373
Typical Fd values based on the flow capacity and valve size above
[6 empty] | Rated (100%) | These values have been filled in from the Tables tab. |  | Calculation of
| Valve type | Valve style modifier, Fd |  |  |  | open Cv | The user can overwrite them with known values. For this calculation only capacity in Column H must by in Cv. (Kv * 1.17 = Cv) |  | Relative Flow Coef. | Case 1 | Case 2 | Case 3 | Case 4
| Globe, 4 port cage | 0.38857 | 0.38857 | 0.38857 | 0.38857 | 235 | 235 | Copy cells in Column I to Column H to restore automatic entry of rated Cv. Choose "Paste formulas" |  | 0.76596 | 0.76596 | 0.76596 | 0.76596
to keep green fill in Column H
| Globe, Parabolic plug flow to open | 0.44423 | 0.44423 | 0.44423 | 0.44423 | 190 | 190 |  |  | 0.94737 | 0.94737 | 0.94737 | 0.94737
| Rotary eccentric plug | 0.34578 | 0.34578 | 0.34578 | 0.34578 | 240 | 240 |  |  | 0.75 | 0.75 | 0.75 | 0.75
| Segment ball | 0.67258 | 0.67258 | 0.67258 | 0.67258 | 620 | 620 |  |  | 0.29032 | 0.29032 | 0.29032 | 0.29032
| Butterfly, high Perf. eccentric | 0.46229 | 0.46229 | 0.46229 | 0.46229 | 400 | 400 |  |  | 0.45 | 0.45 | 0.45 | 0.45
| Full ball (Standard port) | 0.97989 | 0.97989 | 0.97989 | 0.97989 | 550 | 550 |  |  | 0.32727 | 0.32727 | 0.32727 | 0.32727
Fd calculation
For Full ball valve
Typical xFz values based on the flow capacity and valve size above | [8 empty] | Relative Cv | 0.32727 | 0.32727 | 0.32727 | 0.32727
|  | Differential pressure ratio of incipient | [6 empty] | Relatve travel | 0.71556 | 0.71556 | 0.71556 | 0.71556
| Valve type | cavitation, xFz | [6 empty] | Fd_FB | 0.97989 | 0.97989 | 0.97989 | 0.97989
Typical xFz values based on the flow capacity and valve size above
| Globe, 4 port cage | 0.21465 | 0.21465 | 0.21465 | 0.21465
| Globe, Parabolic plug | 0.52873 | 0.52873 | 0.52873 | 0.52873
| Rotary eccentric plug | 0.32856 | 0.32856 | 0.32856 | 0.32856
| Segment ball | 0.31163 | 0.31163 | 0.31163 | 0.31163
| Butterfly, high Perf. eccentric | 0.2489 | 0.2489 | 0.2489 | 0.2489
| Full ball | 0.31311 | 0.31311 | 0.31311 | 0.31311

## Read Me
Excel® Worksheet for Estimating FL, Fd and xFz
for use in the IEC Noise Worksheets
About the worksheet
This worksheet is distributed at no charge on an as-is basis. The author does not assume any liability for its use.
No claim of copyright is made, as it is the author’s intention that it should be in the public domain for use by anyone who wishes to.
The worksheet calculates typical FL, Fd and xFz parameters for use in the IEC aerodynamic and hydrodynamic noise worksheets when manufacturer’s data is not available. The Fd calculation can be used in control valve sizing for non-turbulent flow. It is preferable to use parameters from your preferred manufacturer whenever they are available. The worksheet calculations are based on the user’s input of valve size and required valve capacity calculated by a valve sizing program or worksheet. The calculation methods for FL and xFz are based on data from a source that the author believes to be reliable. The calculation method for Fd is based on the IEC Aerodynamic noise prediction method, IEC 60534-8-3 2010 Ed 3, Table 2, with one exception. Table 2 does not have data for full ball valves. The Fd calculation for full ball valves is based on data from a reliable source that tabulates Fd as a function of relative valve travel.
The worksheet is protected to prevent accidental changes. It can be un-protected by simply clicking “Unprotect Sheet” on the review tab. No password is required. If you choose to unprotect the sheet, you do so at your own risk.
Using the worksheet
The worksheet is originally configured for valve flow capacity to be in units of Cv and valve size to be in units of “inch.” In Cells D8 and D9 the user can change the configuration for valve capacity to be in units of Kv and valve size to be in “DN.”
To use the worksheet, enter up to four calculated required valve capacities (from a valve sizing program or worksheet) and the valve size.
Below the data entry area are the calculated typical parameters for several common control valve styles.
Calculated results only appear after valve flow capacity and size have been entered.

## Tables
Tables of rated Cv vs valve size used in the Fd calculations.
Globe, Cage | TABLE_GC
Valve size (inch) | 1 | 1.5 | 2 | 2.5 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24
Rated Cv (100%) | 18 | 37 | 75 | 100 | 145 | 235 | 380 | 600 | 950 | 1280 | 1750 | 2300 | 3400 | 4700 | 6700
Globe, Parabolic | TABLE_GP
Valve size (inch) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6
Rated Cv (100%) | 7 | 9 | 13.5 | 28 | 49 | 100 | 190 | 295
Eccentric Rotary Plug | TABLE_RP
Valve size (inch) | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10
Rated Cv (100%) | 15 | 31 | 52 | 140 | 240 | 520 | 870 | 1330
Segment | TABLE_SEG
Valve size (inch) | 1 | 1.5 | 2 | 2.5 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 20 | 24 | 28 | 32
Rated Cv (100%) | 45 | 110 | 180 | 280 | 420 | 620 | 1260 | 2030 | 3210 | 4490 | 6440 | 8510 | 1320 | 19700 | 25300 | 32000
TABLE_BF (150# high performance butterfly)
H.P. ButterflY Eccentric
Valve size (inch) | 2.5 | 3 | 4 | 5 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 24 | 28 | 30 | 32 | 36 | 40 | 42 | 48 | 54 | 56 | 60
Rated Cv (100%) | 78 | 165 | 400 | 650 | 1050 | 2200 | 3300 | 5100 | 5800 | 8000 | 10500 | 14000 | 21600 | 30000 | 34000 | 41000 | 55500 | 75000 | 82650 | 108300 | 133500 | 144000 | 159000
Full Ball (Std. port) | TABLE_FB
Valve size (inch) | 0.5 | 0.75 | 1 | 1.5 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20
Rated Cv (100%) | 9 | 19 | 45 | 125 | 165 | 350 | 550 | 765 | 1890 | 3900 | 6700 | 5100 | 8100 | 11000 | 16000