## Sheet1
|  | Name of cell | User inputs and
|  | to the right | Calculated formulas
Minimum design flow |  | Qmin | 80 | USER INPUT
Maximum design flow |  | Qmax | 550 | USER INPUT
Valve inlet pressure at minimum design flow |  | P_1_minQ | 56.7 | USER INPUT
Valve inlet pressure at maximum design flow |  | P_1_maxQ | 46.7 | USER INPUT
Valve pressure drop at minimum des. flow |  | DELTA_P_minQ | 32 | USER INPUT
Valve pressure drop at maximum des. flow |  | DELTA_P_maxQ | 20 | USER INPUT |  |  | FORMULAS
Valve outlet pressure at minimum design flow |  | P_2_minQ | 24.7 | INTREMEDIATE CALC |  |  | =P_1_minQ-DELTA_P_minQ
Valve outlet pressure at maximum design flow |  | P_2_maxQ | 26.7 | INTREMEDIATE CALC |  |  | =P_1_maxQ-DELTA_P_maxQ
P1 change between P_1_minQ and P_1_maxQ |  | dp_up | 10 | INTREMEDIATE CALC |  |  | =P_1_minQ-P_1_maxQ
Upstream system resistance factor |  | R_up | 3.3772e-05 | INTREMEDIATE CALC |  |  | =dp_up/(Qmax^2-Qmin^(2))
P2 change between P_2_maxQ and P_2_minQ |  | dp_dn | 2 | INTREMEDIATE CALC |  |  | =P_2_maxQ-P_2_minQ
Downstream system resistance factor |  | R_dn | 6.7545e-06 | INTREMEDIATE CALC |  |  | =dp_dn/(Qmax^2-Qmin^2)
Upstream system press drop at min flow |  | dpup_minQ | 0.21614 | INTREMEDIATE CALC |  |  | =R_up*Qmin^2
Downstream system press drop at min flow |  | dpdn_minQ | 0.043229 | INTREMEDIATE CALC |  |  | =R_dn*Qmin^2
CALCULATE P1, P2 AND DP AT A GIVEN FLOW USING PROCESS MODEL
Given flow |  | Q_i | 766 | USER INPUT
P1 at this iteration flow rate |  | P1_Qi | 37.1 | CALCULATED RESULT |  |  | =P_1_minQ-(Q_i^2*R_up)+dpup_minQ
Delta P at this iteration flow rate |  | DELTA_P_Qi | 8.48 | CALCULATED RESULT |  |  | =P1_Qi-P2_Qi
P2 at this iteration flow rate |  | P2_Qi | 28.62 | CALCULATED RESULT |  |  | =P_2_minQ+(Q_i^2*R_dn)-dpdn_minQ
Fully
Open
|  |  | Tabulated Data for Installed Flow graph | [7 empty] | Flow
(1) Relative flow, Q | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
(2) Flow = Relative flow X Flow @ h=1.0 | 0 | 76.6 | 153.2 | 229.8 | 306.4 | 383 | 459.6 | 536.2 | 612.8 | 689.4 | 766
(3) P1 |  | 56.7185 | 56.12 | 55.13 | 53.75 | 51.96 | 49.78 | 47.21 | 44.23 | 40.87 | 37.1
(4) Delta P |  | 32.0222 | 31.3107 | 30.12 | 28.45 | 26.31 | 23.7 | 20.61 | 17.04 | 13 | 8.48
(5) Cv | 0 | 13.5 | 27.4 | 42.1 | 58.2 | 76.5 | 98.2 | 126 | 165 | 232 | 418
(6) Relative travel, h | 0 | 0.217 | 0.327 | 0.413 | 0.487 | 0.558 | 0.631 | 0.712 | 0.8 | 0.884 | 0.999
(1) Relatve flow is always 0.0 to 1.
(2) Calculated from fully open flow and relative flow. E.g. C35 = C34 * $L35
(3) Calculated by process model
(4) Calculated by process model
(5) Calculated with user's preferred valve sizing software
(6) Calculated with user's preferred valve sizing software
(Relative travel is valve % travel / 100)
Make a graph of Relative Flow vs Relative Valve Travel
Menu Insert Chart Scatter
Right click inside the empty chart. Click "Select Data"
In the “Select Data Source” dialog, under “Legend Entries” Click on “Add.”
For “Series name:” type “Installed Relative Flow vs. Relative Travel.”
Under “Series values:”
1. Place the insertion point in the field “Series X values:” and select all
of the row of values you have entered for “Relative Travel” (B39 thru L39).
2. Place the insertion point in the field “Series Y values:” Delete the entry
“+(1).” Then select all of the row of values you have entered for “Relative Flow"
(B34 thru L34)
Click “OK” twice
Locate where the minimum and maximum specified flows intersect the installed flow graph from your valve sizing
calculations at the specified minimum and maximum flow rates. (Percent open divided by 100)
Tabulated Data for Installed Gain graph
(1) Valve relative travel, h | 0 | 0.217 | 0.327 | 0.413 | 0.487 | 0.558 | 0.631 | 0.712 | 0.8 | 0.884 | 0.999
(2) Relative flow, Q/Qmax | 0 | 0.13927 | 0.27855 | 0.41782 | 0.55709 | 0.69636 | 0.83564 | 0.97491 | 1.1142 | 1.2535 | 1.3927
(3) Delta (Q/Qmax) | 0 | 0.27855 | 0.27855 | 0.27855 | 0.27855 | 0.27855 | 0.27855 | 0.27855 | 0.27855 | 0.27855
(4) Delta h | 0 | 0.327 | 0.196 | 0.16 | 0.145 | 0.144 | 0.154 | 0.169 | 0.172 | 0.199
(5) Gain, D(Q/Qmax)/Dh |  | 0.85182 | 1.4212 | 1.7409 | 1.921 | 1.9343 | 1.8087 | 1.6482 | 1.6195 | 1.3997
(1) Copied from relative travel in installed characteristic calculation
(2)Flow from installed characteristic calculation divided by Qmax (Qmax is the maximum design flow). E.g. C73 = C35/Qmax
(3) Relative flow from next column - relative flow from previous column. E.g. C74 = D73-B73
(4) Relative travel from next column - relative travel from previous column. E.g. C75 = D72-B72
(5) Delta (Q/Qmax) / Delta h E.g, C76 = C74/C75
Make a graph of Installed Gain vs Q/Qmax (Note that Qmax is the maximum user specified required flow rate)
Menu Insert Chart Scatter
Right click inside the empty chart. Click "Select Data"
In the “Select Data Source” dialog, under “Legend Entries” Click on “Add.”
For “Series name:” type “Installed Gain”
Under “Series values:”
1. Place the insertion point in the field “Series X values:” and select all
of the row of values for “Relative flow, Q/Qmax”:.
2. Place the insertion point in the field “Series Y values:” Delete the entry
“+(1).” Then select all of the row of value for “Gain, D(Q/Qmax)/Dh"
Click “OK” twice
Note that 1.0 on the Q/Qmax scale represens the users specified maximum
required flow, Qmax.
The minimum design flow on the Q/Qmax scale is at Qmin/Qmax