## Instructions
DOUBLE CLICK THE ICON TO THE LEFT TO READ THE
INSTRUCTIONS FOR THIS WORKBOOK.
The instruction booklet will open in a new Acrobat window.
The main user interface for this workbook is on the Vallve Sizing tab.
Your expereince with this workbook will be significantly enhanced it you read
the INTRODUCTION and USING THE WORKBOOK sections.

## Valve Sizing
CONTROL VALVE SIZING: STEAM, VAPOR - Mass |  | TAG: | PV123 |  |  |  |  | Available Cv table names |  | Scroll to the right to view the intermediate calculations | Valve sizing per ISA S75.01.01 2007
Flow | lbm/h | W | 2700 | 7200 | 14400 | 18000 |  | BALL_FP | Full Port Ball Valve |  | DESCRIPTION OF VARIABLE | Eq | NAME OF VARIABLE | FORMULA
Inlet pressure | psiA | P_1 | 90 | 88.6 | 83.7 | 80 |  | BALL_RP | Reduced Port Ball Valve |  | CALCULATED IN COLUMN "S" |  | CALCULATED IN COLUMN "S"
Inlet temperature | F | T_1 | 100 | 100 | 100 | 100 |  | BALL_SEG | Segment Ball valve |  | Pressure drop ratio | 9 | x | 0.33333 | 0.3228 | 0.28315 | 0.25
Pressure drop | psi | DELTA_P | 30 | 28.6 | 23.7 | 20 |  | HPBF_150 | High Perf. Buttefly Cl 150 |  | Ratio of specific heats factor | 11 | F_GAMMA | 1 | 1 | 1 | 1
Density | lbm/ft^3 | RHO | 0.43414 | 0.42739 | 0.40375 | 0.3859 |  | HPBF_300 | High Perf. Buttefly Cl 300 |  | Absolute temperature |  | T_abs | 559.67 | 559.67 | 559.67 | 559.67
Molecular mass |  | M | 28.97 |  |  |  |  | HPBF_600 | High Perf. Buttefly Cl 600
Specific heat ratio |  | GAMMA | 1.4 |  |  |  |  | GC_EQ | Globe Cage Guided =% |  | WITHOUT REDUCERS
Choked press drop ratio factor |  | x_T | 0.63729 | 0.6229 | 0.55102 | 0.4504 | 4 | GC_LIN | Globe Cage Guided linear |  | Expansion factor | 12 | Y | 0.82565 | 0.82726 | 0.82871 | 0.81498
Liquid press. Recovery factor |  | F_L | 0.92296 | 0.89285 | 0.82994 | 0.77802 | 1, 3 | GP_EQ | Globe Parabolic Plug =% |  | C Non choked | 5 | C_NonCh | 14.3149 | 39.327 | 88.741 | 125.5942
Valve style modifier |  | F_D | 0.78001 | 0.8486 | 0.9233 | 0.95562 | 1, 3 | GP_LIN | Globe Parabolic Plug Linear |  | C Choked | 5 | C_Ch | 12.8153 | 35.1127 | 79.0366 | 114.3302
Valve correction - accoustic efficiency, Ah |  | A_ETA | -3.6 |  |  |  | 1, 3 | ROT_PLUG | Eccentric Rotary Plug |  | Choked pressure drop ratio | 10 | CH_x | 0.63729 | 0.6229 | 0.55102 | 0.4504
Strouhal number (peak) |  | St_P | 0.3 |  |  |  | 1, 3 |  |  |  | Select C Non choked or C choked |  | Select_C_Non_or_C_Ch | 14.3149 | 39.327 | 88.741 | 125.5942
Inlet pipe diameter | inch | D_1 | 6 | [7 empty] | (This is the initial guess for
Outlet pipe diameter | inch | D_2 | 6 | [7 empty] | the following iterative calculations)
Valve size | inch | d | 3 |  |  |  | 5
Valve Cv table |  | Cv_Table | BALL_SEG | [7 empty] | WITH REDUCERS
Outlet pipe wall thickness | inch | T_S | 0.28 |  |  |  | 1 |  |  |  | Reducer velocity head coefficients | 18 | ZETA_1 | 0.28125 | ======> | ======> | ======>
Contraction coeff. for valve outlet |  | BETA | 0.75 |  |  |  | 1, 2 |  |  |  |  | 17 | ZETA_B1 | 0.9375 | ======> | ======> | ======>
Atmospheric pressure outside pipe | psiA | p_a | 14.696 |  |  |  | 1 |  |  |  |  | 19 | ZETA_2 | 0.5625 | ======> | ======> | ======>
Required flow coef. (Cv or Kv) | Cv | C_ | 14.3307 | 39.6575 | 92.5767 | 136.2431 | 1 = This entry is only used in the IEC noise calculation. |  |  |  |  | 17 | ZETA_B2 | 0.9375 | ======> | ======> | ======>
Flow calculated from C_ above | lbm/h |  | 2700 | 7200 | 14400 | 18000 | 2 = Beta is used when valve outlet exceeds Mach 0.3, 0.75 is typical. |  |  |  | Sum of velocity head coefficients | 16 | SIGMA_ZETA | 0.84375 | ======> | ======> | ======>
Outlet velocity | Mach |  | 0.045525 | 0.1214 | 0.2428 | 0.3035 | Consult valve manufacturer. |  |  |  | Sum of upstream velocity head coef |  | SIGMA_ZETA_1 | 1.2188 | ======> | ======> | ======>
Sound pressure level | dB(A) |  | 78.8425 | 84.648 | 87.5188 | 87.6417 | 3 = Values automatically copied from the "xT, FL, Fd, Aeta, Stp" tab. Can be overridden manually.
Travel | % |  | 22.3954 | 40.1192 | 61.3343 | 73.4643 | 4 = See "xT, FL, Fd, Aeta, Stp" tab for typical values. |  |  |  | Beginning of iterative calculation
[5 empty] | Data input | Calculated values | 5 = See "Valve Travel" tab for supported valve sizes. |  |  |  | Assumed C for iterative purposes |  | C_i | 14.3149 | 39.327 | 88.741 | 125.5942
Unit selection: | 1 | 1 = US; 2 = SI (Cv, bar); 3 = SI (Cv, kPa); 4 = SI (Kv, bar); 5 = SI (Kv, kPa) |  |  |  |  | 6 = A valid "Cv table" name must be entered for SPL and Travel results. |  |  |  | Piping geometry factor | 15 | F_P | 0.9988 | 0.99107 | 0.95687 | 0.91878
Valve & pipe dia., wall thickness: | 1 | 1 = inch & Cv 2 = mm & Cv 3 = mm & Kv | [8 empty] | Choked Pres drop ratio factor with reducers | 22 | x_TP | 0.63756 | 0.62511 | 0.56492 | 0.48203
[11 empty] | Expansion factor | 12 | Y_W_Reducers | 0.82572 | 0.82787 | 0.83292 | 0.82712
[11 empty] | C Non choked w/ reducers | 5 | C_NonCh_W_Reducers | 14.3307 | 39.652 | 92.2711 | 134.6908
[11 empty] | C Choked w/ reducers | 5 | C_Ch_W_Reducers | 12.8279 | 35.3663 | 81.5759 | 120.2859
[11 empty] | Choked pressure drop ratio w/ reducers | 10 | CH_x_W_Reducers | 0.63756 | 0.62511 | 0.56492 | 0.48203
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.652 | 92.2711 | 134.6908
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.652 | 92.2711 | 134.6908
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95362 | 0.90822
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56598 | 0.48625
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83324 | 0.82862
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6574 | 92.5519 | 136.01
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7785 | 121.1546
| The cells below (RowS 44 46) detrmine if any input data is missing. | [9 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56598 | 0.48625
| If it is, error messages are blanked out of the calculated results. | [9 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6574 | 92.5519 | 136.01
| DATA1 | DATA2 | DATA3 | DATA4
For sizing calculations | 883477562018.4858 | 2.1275e+12 | 2.7837e+12 | 2.1926e+12 | [6 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6574 | 92.5519 | 136.01
| N_DAT1 | N_DAT2 | N_DAT3 | N_DAT4 | [6 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95335 | 0.90665
For noise calculations | -2.3995 | -272.7401 | -275.8374 | -267.6365 | [6 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56606 | 0.48688
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82884
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5746 | 136.2079
These Numerical constants are set by the units choises set by the user below the user interface | [10 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.795 | 121.285
which incllude all the options suported by the ISA Standard | [10 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56606 | 0.48688
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5746 | 136.2079
Numerical constants
N_2 | 890 | [9 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5746 | 136.2079
N_5 | 1000 | [9 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90642
N_6 | 63.3 | [9 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48698
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
FLAG_A ** | 1 | 1= Inlet Temp entered in F is converted to R in T_abs field | [8 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5765 | 136.2378
|  | 2= Inlet Temp entered in C is coverted to K in T_abs field | [8 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7963 | 121.3047
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48698
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5765 | 136.2378
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5765 | 136.2378
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5766 | 136.2423
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3077
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5766 | 136.2423
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5766 | 136.2423
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.243
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3081
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.243
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.243
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Assumed C for iterative purposes |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 |  | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Choked Pres drop ratio factor with reducers | 22 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 |  | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | C Non choked w/ reducers | 5 |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | C Choked w/ reducers | 5 |  | 12.8279 | 35.3705 | 81.7964 | 121.3082
[11 empty] | Choked pressure drop ratio w/ reducers | 10 |  | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select C Non choked or C choked |  |  | 14.3307 | 39.6575 | 92.5767 | 136.2431
Confirmation that the calculated C will produce the given flow rate
[11 empty] | Final C calculated above |  | Final_Calculated_C | 14.3307 | 39.6575 | 92.5767 | 136.2431
[11 empty] | Piping geometry factor | 15 | Final_F_P | 0.9988 | 0.99092 | 0.95333 | 0.90638
[11 empty] | Presssure drop ratio factor w/reducers | 22 | Final_x_TP | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Expansion factor | 12 | Final_Y_W_Reducers | 0.82572 | 0.82788 | 0.83326 | 0.82888
[11 empty] | Flow Non choked w/ reducers | 7 | Final_Flow_NonCh_W_Reducers | 2700 | 7200 | 14400 | 18000
[11 empty] | Flow Choked w/ reducers | 7 | Final_Flow_Ch_W_Reducers | 3016.3097 | 8072.653 | 16297.8282 | 20216.0752
[11 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 | Final_CH_x_W_Reducers | 0.63756 | 0.62515 | 0.56607 | 0.48699
[11 empty] | Select flow Non choked or flow choked |  | Calc_Flow_From_Final_ Calc_C | 2700 | 7200 | 14400 | 18000

## Installed Flow
[13 empty] | Intermediate Calculations |  |  |  | 22.29
VALVE DATA | ` | [10 empty] | Scroll to the right to see the | DESCRIPTION OF VARIABLE | Eqn. | NAME OF VARIABLE | FORMULA
Data copied from Valve Travel tab, Table: | BALL_SEG | [10 empty] | intermediate calculations | CALCULATED IN COLUMN "P" |  | CALCULATED IN COLUMN "P"
Valve size, Inch, from Valve Travell tab | 3
Relative travel, h | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 |  |  | CALCULATE PARAMETERS FOR UPSTREAM AND DOWNSTREAM PROCESS PRESSURE MODEL
Cv from tables on Valve Travel tab | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 |  |  | Minimum design flow (From Col D) |  | W_min | 2700
xT | 0.64 | 0.64 | 0.63341 | 0.6231 | 0.60075 | 0.55873 | 0.50449 | 0.42327 | 0.34677 | 0.18243 |  |  | Maximum design flow (From Col F) |  | W_max | 18000
[13 empty] | Valve inlet pressure at minimum des. Flow |  | P_1_minW | 90
| 3 0.7: BALL_SEG |  | Scroll down for instructions for the Installed flow and gain graphs and | Valve inlet pressure at maximum des. flow |  | P_1_maxW | 80
| 3 0.7: 3 |  | the calculation of the fully open flow, Qf. The accuracy of the calculations | Pressure drop at minimum des. flow |  | DELTA_P_minW | 30
| 3 0.7: PV123 |  | on this and the Installed Gain tab depend on the accuracy of the process | Pressure drop at maximum des. flow |  | DELTA_P_maxW | 20
[12 empty] | data. | Valve outlet pressure at minimum des. Flow |  | P_2_minW | 60
[13 empty] | Valve outlet pressure at maximum des. flow |  | P_2_maxW | 60
[13 empty] | Upstream system drop |  | dp_up | 10
| 3 0.7: Fully open Flow, Wf |  | INSTALED FLOW AND GAIN ERRORS | Upstream system resistance factor |  | R_up | 3.1575e-08
| 3 0.7: Wf =; 3 0.8: 24942.0996 |  | If there are any error messages below, the graphs and Wf are not valid | Downstream system drop |  | dp_dn | 0
[13 empty] | Downstream system resistance factor |  | R_dn | 0 | Relative Travel, h | 0.1 |  |  | 0.2 |  |  | 0.3 |  |  | 0.4 |  |  | 0.5 |  |  | 0.6 |  |  | 0.7 |  |  | 0.8 |  |  | 0.9 |  |  | 1
[13 empty] | Upstream system press drop an min flow |  | dpup_minQ | 0.23018 | Min C_h - Ci | 0.013826 |  |  | 0.04885 |  |  | 0.041413 |  |  | 0.20047 |  |  | 0.05177 |  |  | 0.46225 |  |  | 0.76938 |  |  | 0.83759 |  |  | 2.2576 |  |  | 1.0995
[13 empty] | Downstream system press drop an min flow |  | dpdn_minQ | 0 | Flow at C_h | 898.6574 |  |  | 2200.4819 |  |  | 4285.9771 |  |  | 7190.5364 |  |  | 10494.7837 |  |  | 13866.6628 |  |  | 17089.1635 |  |  | 19839.9883 |  |  | 23263.9466 |  |  | 24942.0996
| 3 0.7: Wmax = maximum | [6 empty] | Values found on Line | 2523 |  |  | 1305 |  |  | 983 |  |  | 773 |  |  | 577 |  |  | 437 |  |  | 339 |  |  | 255 |  |  | 269 |  |  | 143
[8 empty] | design flow = | 18000
CALCULATE FLOW AT EACH INCREMENT OF h
[13 empty] | Valve C at travel h (Cv or Kv) |  | C_h | 4.73 |  |  | 11.6 |  |  | 23 |  |  | 39.4 |  |  | 61 |  |  | 88.2 |  |  | 121 |  |  | 165 |  |  | 246 |  |  | 420
Wmin = minimum
[8 empty] | design flow = | 2700
Caculation of flow conditions
[13 empty] | Piping geometry factor at relative travel, h | 15 | F_P_h | 0.99987 |  |  | 0.99921 |  |  | 0.99692 |  |  | 0.99104 |  |  | 0.97891 |  |  | 0.95737 |  |  | 0.92396 |  |  | 0.87084 |  |  | 0.7651 |  |  | 0.57123
| 3 0.8: Flow units are; 3 0.9: lbm/h |  |  | Reducer corrected pressure drop ratio factor at choked flow | 21 | x_TP_h | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
400 iterations
[13 empty] | First iteration flow rate |  | W_i | 27 | Abs Value of | Flow this | 898.6574 | Abs Value of | Flow this | 2200.4819 | Abs Value of | Flow this | 4285.9771 | Abs Value of | Flow this | 7190.5364 | Abs Value of | Flow this | 10494.7837 | Abs Value of | Flow this | 13866.6628 | Abs Value of | Flow this | 17089.1635 | Abs Value of | Flow this | 19839.9883 | Abs Value of | Flow this | 23263.9466 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  | P1_Wi | 90.2302 |  |  | 90.2047 |  |  | 90.0773 |  |  | 89.6502 |  |  | 88.5977 |  |  | 86.7525 |  |  | 84.1589 |  |  | 81.0091 |  |  | 77.8016 |  |  | 73.1416
Valve relative travel, h | 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1 |  | P2 at this iteration flow rate |  | P2_Wi | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
Relative Flow Q/Qf | 0 | 0.03603 | 0.088224 | 0.17184 | 0.28829 | 0.42077 | 0.55595 | 0.68515 | 0.79544 | 0.93272 | 1 |  | Density at this iteration |  | RHO_Wi | 0.43525 |  |  | 0.43512 |  |  | 0.43451 |  |  | 0.43245 |  |  | 0.42737 |  |  | 0.41847 |  |  | 0.40596 |  |  | 0.39077 |  |  | 0.3753 |  |  | 0.35282
Minimum Flow | 0.10825 | 0.10825 | 0.10825 | 0.10825 | 0.10825 | 0.10825 | 0.10825 | 0.10825 | 0.10825 | 0.10825 | 0.10825 |  | Delta P at this iteration flow rate |  | DELTA_P_Wi | 30.2302 |  |  | 30.2047 |  |  | 30.0773 |  |  | 29.6502 |  |  | 28.5977 |  |  | 26.7525 |  |  | 24.1589 |  |  | 21.0091 |  |  | 17.8016 |  |  | 13.1416
Maximum Flow | 0.72167 | 0.72167 | 0.72167 | 0.72167 | 0.72167 | 0.72167 | 0.72167 | 0.72167 | 0.72167 | 0.72167 | 0.72167 |  | Press drop ratio this iteration |  | x_Wi | 0.33503 |  |  | 0.33485 |  |  | 0.33391 |  |  | 0.33073 |  |  | 0.32278 |  |  | 0.30838 |  |  | 0.28706 |  |  | 0.25934 |  |  | 0.22881 |  |  | 0.17967
[13 empty] | Expansion factor | 12 | Y_C_h | 0.82551 |  |  | 0.82565 |  |  | 0.82448 |  |  | 0.8237 |  |  | 0.8226 |  |  | 0.82035 |  |  | 0.82008 |  |  | 0.81826 |  |  | 0.87085 |  |  | 0.84101
[13 empty] | C Non choked w/ reducers | 5 | C_N_Ch | 0.14246 |  |  | 4.7467 |  |  | 11.6991 |  |  | 23.1635 |  |  | 40.3511 |  |  | 63.0924 |  |  | 92.3159 |  |  | 132.2289 |  |  | 181.9948 |  |  | 355.278
INSTRUCTIONS FOR THE OPTIONAL INSTALLED FLOW AND GAIN GRAPHS AND FULLY OPEN FLOW CALCULATION The process pressure model is a curve fit based on the Flow, P1 and Delta P in Columns D and G on the Valve Sizing tab. The curve fit is based on the principle that piping pressure losses are approximately proportional to flow squared. The Density used in the installed flow calculation is the value entered in Column G on the Valve Sizing tab adjusted for pressure as determined by the process pressue model for each increment of valve relative travel. To calculate the fully open flow, Wf, the installed flow and the installed gain, on the Valve Sizing tab, enter the minimum design flow along with its associated values of P1 and Delta P in Column D and the maximum design flow along with its associated values of P1 and Delta P in Column G. The accuracy of these calculations depends on the accuracy of the process data that is used. Any process conditions entered in Columns E and F are not used in the calculation of the fully open flow, the installed flow and the installed gain. The process model, Wf, and the graphs are only valid if: 1. The flow in G2 on the Valve Sizing tab is greater than the flow in D2 2. P1 is either constant or decreasing with increasing flow 3. P2 is either constant or increasing with increasing flow NOTE: Extrapolating curve-fit data beyond the limits for which the curve fit was established can be uncertain. The farther beyond the limits, the greater is the potential for uncertainty. As such, the fully open flow, the Installed Flow and the Installed Gain should be treated as approximations. | [12 empty] | C Choked w/ reducers | 5 | C_Ch | 0.12757 |  |  | 4.2495 |  |  | 10.4937 |  |  | 20.8034 |  |  | 36.3039 |  |  | 56.9673 |  |  | 83.3888 |  |  | 119.7783 |  |  | 147.9061 |  |  | 309.3799
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 | CH_x_W_Reducers | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  | C_i | 0.14246 |  |  | 4.7467 |  |  | 11.6991 |  |  | 23.1635 |  |  | 40.3511 |  |  | 63.0924 |  |  | 92.3159 |  |  | 132.2289 |  |  | 181.9948 |  |  | 355.278
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5875 | 27 |  | 6.8533 | 898.6574 |  | 11.3009 | 2200.4819 |  | 16.2365 | 4285.9771 |  | 20.6489 | 7190.5364 |  | 25.1076 | 10494.7837 |  | 28.6841 | 13866.6628 |  | 32.7711 | 17089.1635 |  | 64.0052 | 19839.9883 |  | 64.722 | 23263.9466
[13 empty] | Next iteration flow rate |  |  | 27.54 | Abs Value of | Flow this | 907.644 | Abs Value of | Flow this | 2222.4867 | Abs Value of | Flow this | 4328.8369 | Abs Value of | Flow this | 7262.4417 | Abs Value of | Flow this | 10599.7315 | Abs Value of | Flow this | 14005.3295 | Abs Value of | Flow this | 17260.0552 | Abs Value of | Flow this | 20038.3882 | Abs Value of | Flow this | 23496.5861 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2302 |  |  | 90.2042 |  |  | 90.0742 |  |  | 89.6385 |  |  | 88.5648 |  |  | 86.6826 |  |  | 84.0368 |  |  | 80.8238 |  |  | 77.5518 |  |  | 72.7982
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43512 |  |  | 0.4345 |  |  | 0.43239 |  |  | 0.42721 |  |  | 0.41814 |  |  | 0.40537 |  |  | 0.38987 |  |  | 0.37409 |  |  | 0.35116
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2302 |  |  | 30.2042 |  |  | 30.0742 |  |  | 29.6385 |  |  | 28.5648 |  |  | 26.6826 |  |  | 24.0368 |  |  | 20.8238 |  |  | 17.5518 |  |  | 12.7982
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33484 |  |  | 0.33388 |  |  | 0.33064 |  |  | 0.32253 |  |  | 0.30782 |  |  | 0.28603 |  |  | 0.25764 |  |  | 0.22632 |  |  | 0.1758
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82565 |  |  | 0.8245 |  |  | 0.82375 |  |  | 0.82274 |  |  | 0.82067 |  |  | 0.82073 |  |  | 0.81945 |  |  | 0.87225 |  |  | 0.84443
[13 empty] | C Non choked w/ reducers | 5 |  | 0.14531 |  |  | 4.7942 |  |  | 11.8167 |  |  | 23.4 |  |  | 40.7787 |  |  | 63.8072 |  |  | 93.4694 |  |  | 134.1029 |  |  | 185.1181 |  |  | 362.9926
[13 empty] | C Choked w/ reducers | 5 |  | 0.13012 |  |  | 4.292 |  |  | 10.599 |  |  | 21.0142 |  |  | 36.6806 |  |  | 57.5833 |  |  | 84.345 |  |  | 121.2535 |  |  | 149.8663 |  |  | 313.9481
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.14531 |  |  | 4.7942 |  |  | 11.8167 |  |  | 23.4 |  |  | 40.7787 |  |  | 63.8072 |  |  | 93.4694 |  |  | 134.1029 |  |  | 185.1181 |  |  | 362.9926
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5847 | 27.54 |  | 6.8058 | 907.644 |  | 11.1833 | 2222.4867 |  | 16 | 4328.8369 |  | 20.2213 | 7262.4417 |  | 24.3928 | 10599.7315 |  | 27.5306 | 14005.3295 |  | 30.8971 | 17260.0552 |  | 60.8819 | 20038.3882 |  | 57.0074 | 23496.5861
[13 empty] | Next iteration flow rate |  |  | 28.0908 | Abs Value of | Flow this | 916.7204 | Abs Value of | Flow this | 2244.7116 | Abs Value of | Flow this | 4372.1253 | Abs Value of | Flow this | 7335.0661 | Abs Value of | Flow this | 10705.7288 | Abs Value of | Flow this | 14145.3828 | Abs Value of | Flow this | 17432.6557 | Abs Value of | Flow this | 20238.7721 | Abs Value of | Flow this | 23731.552 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2302 |  |  | 90.2036 |  |  | 90.0711 |  |  | 89.6266 |  |  | 88.5314 |  |  | 86.6113 |  |  | 83.9124 |  |  | 80.6347 |  |  | 77.297 |  |  | 72.4478
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43512 |  |  | 0.43448 |  |  | 0.43234 |  |  | 0.42705 |  |  | 0.41779 |  |  | 0.40477 |  |  | 0.38896 |  |  | 0.37286 |  |  | 0.34947
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2302 |  |  | 30.2036 |  |  | 30.0711 |  |  | 29.6266 |  |  | 28.5314 |  |  | 26.6113 |  |  | 23.9124 |  |  | 20.6347 |  |  | 17.297 |  |  | 12.4478
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33484 |  |  | 0.33386 |  |  | 0.33056 |  |  | 0.32227 |  |  | 0.30725 |  |  | 0.28497 |  |  | 0.2559 |  |  | 0.22377 |  |  | 0.17182
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82565 |  |  | 0.82451 |  |  | 0.82379 |  |  | 0.82288 |  |  | 0.82101 |  |  | 0.82139 |  |  | 0.82067 |  |  | 0.87369 |  |  | 0.84796
[13 empty] | C Non choked w/ reducers | 5 |  | 0.14822 |  |  | 4.8422 |  |  | 11.9356 |  |  | 23.6389 |  |  | 41.2114 |  |  | 64.532 |  |  | 94.6431 |  |  | 136.0199 |  |  | 188.3409 |  |  | 371.0943
[13 empty] | C Choked w/ reducers | 5 |  | 0.13272 |  |  | 4.3349 |  |  | 10.7054 |  |  | 21.2271 |  |  | 37.0614 |  |  | 58.2071 |  |  | 85.3148 |  |  | 122.7532 |  |  | 151.864 |  |  | 318.6211
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.14822 |  |  | 4.8422 |  |  | 11.9356 |  |  | 23.6389 |  |  | 41.2114 |  |  | 64.532 |  |  | 94.6431 |  |  | 136.0199 |  |  | 188.3409 |  |  | 371.0943
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5818 | 28.0908 |  | 6.7578 | 916.7204 |  | 11.0644 | 2244.7116 |  | 15.7611 | 4372.1253 |  | 19.7886 | 7335.0661 |  | 23.668 | 10705.7288 |  | 26.3569 | 14145.3828 |  | 28.9801 | 17432.6557 |  | 57.6591 | 20238.7721 |  | 48.9057 | 23731.552
xT for characteritics calculation
[13 empty] | Next iteration flow rate |  |  | 28.6526 | Abs Value of | Flow this | 925.8876 | Abs Value of | Flow this | 2267.1587 | Abs Value of | Flow this | 4415.8465 | Abs Value of | Flow this | 7408.4168 | Abs Value of | Flow this | 10812.7861 | Abs Value of | Flow this | 14286.8366 | Abs Value of | Flow this | 17606.9823 | Abs Value of | Flow this | 20441.1598 | Abs Value of | Flow this | 23968.8675 | Abs Value of | Flow this
Globe, cage | 0.74 | 0.73391 | 0.7245 | 0.72088 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | [6 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
Globe Parabolic | 0.61655 | 0.60846 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 |  |  | P1 at this iteration flow rate |  |  | 90.2302 |  |  | 90.2031 |  |  | 90.0679 |  |  | 89.6145 |  |  | 88.4972 |  |  | 86.5386 |  |  | 83.7854 |  |  | 80.4419 |  |  | 77.037 |  |  | 72.0903
Rotary plug | 0.62 | 0.62 | 0.62 | 0.62 | 0.60431 | 0.55623 | 0.45298 | 0.399 | 0.399 | 0.399 |  |  | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
Segment ball | 0.64 | 0.64 | 0.63341 | 0.6231 | 0.60075 | 0.55873 | 0.50449 | 0.42327 | 0.34677 | 0.18243 |  |  | Density at this iteration |  |  | 0.43525 |  |  | 0.43512 |  |  | 0.43446 |  |  | 0.43228 |  |  | 0.42689 |  |  | 0.41744 |  |  | 0.40416 |  |  | 0.38803 |  |  | 0.37161 |  |  | 0.34775
Butterfly | 0.693 | 0.693 | 0.69101 | 0.6622 | 0.62425 | 0.57647 | 0.51885 | 0.44156 | 0.37887 | 0.15395 |  |  | Delta P at this iteration flow rate |  |  | 30.2302 |  |  | 30.2031 |  |  | 30.0679 |  |  | 29.6145 |  |  | 28.4972 |  |  | 26.5386 |  |  | 23.7854 |  |  | 20.4419 |  |  | 17.037 |  |  | 12.0903
Full ball (Full and reduced port | 0.82 | 0.82 | 0.80951 | 0.75917 | 0.69747 | 0.62685 | 0.55156 | 0.46607 | 0.34881 | 0.21951 |  |  | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33483 |  |  | 0.33384 |  |  | 0.33047 |  |  | 0.32201 |  |  | 0.30667 |  |  | 0.28388 |  |  | 0.25412 |  |  | 0.22115 |  |  | 0.16771
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82566 |  |  | 0.82452 |  |  | 0.82384 |  |  | 0.82303 |  |  | 0.82135 |  |  | 0.82207 |  |  | 0.82192 |  |  | 0.87517 |  |  | 0.85159
[13 empty] | C Non choked w/ reducers | 5 |  | 0.15118 |  |  | 4.8907 |  |  | 12.0556 |  |  | 23.8804 |  |  | 41.6492 |  |  | 65.2671 |  |  | 95.8377 |  |  | 137.9819 |  |  | 191.6688 |  |  | 379.62
[13 empty] | C Choked w/ reducers | 5 |  | 0.13538 |  |  | 4.3783 |  |  | 10.8128 |  |  | 21.4423 |  |  | 37.4464 |  |  | 58.8385 |  |  | 86.2986 |  |  | 124.278 |  |  | 153.9002 |  |  | 323.4028
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.15118 |  |  | 4.8907 |  |  | 12.0556 |  |  | 23.8804 |  |  | 41.6492 |  |  | 65.2671 |  |  | 95.8377 |  |  | 137.9819 |  |  | 191.6688 |  |  | 379.62
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5788 | 28.6526 |  | 6.7093 | 925.8876 |  | 10.9444 | 2267.1587 |  | 15.5196 | 4415.8465 |  | 19.3508 | 7408.4168 |  | 22.9329 | 10812.7861 |  | 25.1623 | 14286.8366 |  | 27.0181 | 17606.9823 |  | 54.3312 | 20441.1598 |  | 40.38 | 23968.8675
[13 empty] | Next iteration flow rate |  |  | 29.2257 | Abs Value of | Flow this | 935.1465 | Abs Value of | Flow this | 2289.8303 | Abs Value of | Flow this | 4460.005 | Abs Value of | Flow this | 7482.501 | Abs Value of | Flow this | 10920.914 | Abs Value of | Flow this | 14429.705 | Abs Value of | Flow this | 17783.0521 | Abs Value of | Flow this | 20645.5714 | Abs Value of | Flow this | 24208.5562 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2302 |  |  | 90.2026 |  |  | 90.0646 |  |  | 89.6021 |  |  | 88.4624 |  |  | 86.4644 |  |  | 83.6558 |  |  | 80.2451 |  |  | 76.7718 |  |  | 71.7257
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43511 |  |  | 0.43445 |  |  | 0.43222 |  |  | 0.42672 |  |  | 0.41708 |  |  | 0.40353 |  |  | 0.38708 |  |  | 0.37033 |  |  | 0.34599
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2302 |  |  | 30.2026 |  |  | 30.0646 |  |  | 29.6021 |  |  | 28.4624 |  |  | 26.4644 |  |  | 23.6558 |  |  | 20.2451 |  |  | 16.7718 |  |  | 11.7257
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33483 |  |  | 0.33381 |  |  | 0.33037 |  |  | 0.32175 |  |  | 0.30607 |  |  | 0.28278 |  |  | 0.25229 |  |  | 0.21846 |  |  | 0.16348
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82566 |  |  | 0.82453 |  |  | 0.82389 |  |  | 0.82317 |  |  | 0.82169 |  |  | 0.82277 |  |  | 0.8232 |  |  | 0.87669 |  |  | 0.85534
[13 empty] | C Non choked w/ reducers | 5 |  | 0.15421 |  |  | 4.9396 |  |  | 12.1768 |  |  | 24.1245 |  |  | 42.0922 |  |  | 66.0125 |  |  | 97.0538 |  |  | 139.9905 |  |  | 195.1081 |  |  | 388.6116
[13 empty] | C Choked w/ reducers | 5 |  | 0.13809 |  |  | 4.4221 |  |  | 10.9213 |  |  | 21.6597 |  |  | 37.8358 |  |  | 59.4779 |  |  | 87.2965 |  |  | 125.8285 |  |  | 155.9762 |  |  | 328.2973
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.15421 |  |  | 4.9396 |  |  | 12.1768 |  |  | 24.1245 |  |  | 42.0922 |  |  | 66.0125 |  |  | 97.0538 |  |  | 139.9905 |  |  | 195.1081 |  |  | 388.6116
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5758 | 29.2257 |  | 6.6604 | 935.1465 |  | 10.8232 | 2289.8303 |  | 15.2755 | 4460.005 |  | 18.9078 | 7482.501 |  | 22.1875 | 10920.914 |  | 23.9462 | 14429.705 |  | 25.0095 | 17783.0521 |  | 50.8919 | 20645.5714 |  | 31.3884 | 24208.5562
[13 empty] | Next iteration flow rate |  |  | 29.8102 | Abs Value of | Flow this | 944.498 | Abs Value of | Flow this | 2312.7286 | Abs Value of | Flow this | 4504.605 | Abs Value of | Flow this | 7557.326 | Abs Value of | Flow this | 11030.1231 | Abs Value of | Flow this | 14574.002 | Abs Value of | Flow this | 17960.8826 | Abs Value of | Flow this | 20852.0271 | Abs Value of | Flow this | 24450.6417 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2302 |  |  | 90.202 |  |  | 90.0613 |  |  | 89.5895 |  |  | 88.4269 |  |  | 86.3887 |  |  | 83.5237 |  |  | 80.0444 |  |  | 76.5013 |  |  | 71.3538
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43511 |  |  | 0.43443 |  |  | 0.43216 |  |  | 0.42655 |  |  | 0.41672 |  |  | 0.4029 |  |  | 0.38611 |  |  | 0.36902 |  |  | 0.34419
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2302 |  |  | 30.202 |  |  | 30.0613 |  |  | 29.5895 |  |  | 28.4269 |  |  | 26.3887 |  |  | 23.5237 |  |  | 20.0444 |  |  | 16.5013 |  |  | 11.3538
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33483 |  |  | 0.33379 |  |  | 0.33028 |  |  | 0.32147 |  |  | 0.30546 |  |  | 0.28164 |  |  | 0.25042 |  |  | 0.2157 |  |  | 0.15912
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82566 |  |  | 0.82455 |  |  | 0.82394 |  |  | 0.82332 |  |  | 0.82205 |  |  | 0.82348 |  |  | 0.82452 |  |  | 0.87825 |  |  | 0.85919
[13 empty] | C Non choked w/ reducers | 5 |  | 0.15729 |  |  | 4.9891 |  |  | 12.2993 |  |  | 24.3712 |  |  | 42.5405 |  |  | 66.7687 |  |  | 98.2921 |  |  | 142.0478 |  |  | 198.6653 |  |  | 398.1171
[13 empty] | C Choked w/ reducers | 5 |  | 0.14085 |  |  | 4.4664 |  |  | 11.0309 |  |  | 21.8794 |  |  | 38.2295 |  |  | 60.1253 |  |  | 88.309 |  |  | 127.4054 |  |  | 158.093 |  |  | 333.3087
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.15729 |  |  | 4.9891 |  |  | 12.2993 |  |  | 24.3712 |  |  | 42.5405 |  |  | 66.7687 |  |  | 98.2921 |  |  | 142.0478 |  |  | 198.6653 |  |  | 398.1171
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5727 | 29.8102 |  | 6.6109 | 944.498 |  | 10.7007 | 2312.7286 |  | 15.0288 | 4504.605 |  | 18.4595 | 7557.326 |  | 21.4313 | 11030.1231 |  | 22.7079 | 14574.002 |  | 22.9522 | 17960.8826 |  | 47.3347 | 20852.0271 |  | 21.8829 | 24450.6417
[13 empty] | Next iteration flow rate |  |  | 30.4064 | Abs Value of | Flow this | 953.943 | Abs Value of | Flow this | 2335.8559 | Abs Value of | Flow this | 4549.6511 | Abs Value of | Flow this | 7632.8992 | Abs Value of | Flow this | 11140.4243 | Abs Value of | Flow this | 14719.742 | Abs Value of | Flow this | 18140.4914 | Abs Value of | Flow this | 21060.5474 | Abs Value of | Flow this | 24695.1481 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.2014 |  |  | 90.0579 |  |  | 89.5766 |  |  | 88.3906 |  |  | 86.3115 |  |  | 83.3889 |  |  | 79.8397 |  |  | 76.2254 |  |  | 70.9744
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43511 |  |  | 0.43442 |  |  | 0.4321 |  |  | 0.42637 |  |  | 0.41635 |  |  | 0.40225 |  |  | 0.38513 |  |  | 0.36769 |  |  | 0.34236
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.2014 |  |  | 30.0579 |  |  | 29.5766 |  |  | 28.3906 |  |  | 26.3115 |  |  | 23.3889 |  |  | 19.8397 |  |  | 16.2254 |  |  | 10.9744
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33482 |  |  | 0.33376 |  |  | 0.33018 |  |  | 0.32119 |  |  | 0.30484 |  |  | 0.28048 |  |  | 0.24849 |  |  | 0.21286 |  |  | 0.15462
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82566 |  |  | 0.82456 |  |  | 0.82399 |  |  | 0.82347 |  |  | 0.82241 |  |  | 0.82421 |  |  | 0.82586 |  |  | 0.87985 |  |  | 0.86317
[13 empty] | C Non choked w/ reducers | 5 |  | 0.16044 |  |  | 5.039 |  |  | 12.4231 |  |  | 24.6205 |  |  | 42.9942 |  |  | 67.5357 |  |  | 99.5531 |  |  | 144.1559 |  |  | 202.3477 |  |  | 408.1919
[13 empty] | C Choked w/ reducers | 5 |  | 0.14366 |  |  | 4.5111 |  |  | 11.1417 |  |  | 22.1014 |  |  | 38.6276 |  |  | 60.7809 |  |  | 89.3363 |  |  | 129.0095 |  |  | 160.252 |  |  | 338.4414
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.16044 |  |  | 5.039 |  |  | 12.4231 |  |  | 24.6205 |  |  | 42.9942 |  |  | 67.5357 |  |  | 99.5531 |  |  | 144.1559 |  |  | 202.3477 |  |  | 408.1919
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5696 | 30.4064 |  | 6.561 | 953.943 |  | 10.5769 | 2335.8559 |  | 14.7795 | 4549.6511 |  | 18.0058 | 7632.8992 |  | 20.6643 | 11140.4243 |  | 21.4469 | 14719.742 |  | 20.8441 | 18140.4914 |  | 43.6523 | 21060.5474 |  | 11.8081 | 24695.1481
[13 empty] | Next iteration flow rate |  |  | 31.0145 | Abs Value of | Flow this | 963.4824 | Abs Value of | Flow this | 2359.2145 | Abs Value of | Flow this | 4595.1476 | Abs Value of | Flow this | 7709.2282 | Abs Value of | Flow this | 11251.8286 | Abs Value of | Flow this | 14866.9395 | Abs Value of | Flow this | 18321.8964 | Abs Value of | Flow this | 21271.1529 | Abs Value of | Flow this | 24942.0996 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.2009 |  |  | 90.0544 |  |  | 89.5635 |  |  | 88.3536 |  |  | 86.2327 |  |  | 83.2514 |  |  | 79.6308 |  |  | 75.9439 |  |  | 70.5873
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43511 |  |  | 0.4344 |  |  | 0.43203 |  |  | 0.4262 |  |  | 0.41597 |  |  | 0.40158 |  |  | 0.38412 |  |  | 0.36633 |  |  | 0.3405
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.2009 |  |  | 30.0544 |  |  | 29.5635 |  |  | 28.3536 |  |  | 26.2327 |  |  | 23.2514 |  |  | 19.6308 |  |  | 15.9439 |  |  | 10.5873
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33482 |  |  | 0.33374 |  |  | 0.33008 |  |  | 0.32091 |  |  | 0.30421 |  |  | 0.27929 |  |  | 0.24652 |  |  | 0.20994 |  |  | 0.14999
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82566 |  |  | 0.82457 |  |  | 0.82405 |  |  | 0.82363 |  |  | 0.82278 |  |  | 0.82495 |  |  | 0.82724 |  |  | 0.8815 |  |  | 0.86727
[13 empty] | C Non choked w/ reducers | 5 |  | 0.16365 |  |  | 5.0894 |  |  | 12.548 |  |  | 24.8724 |  |  | 43.4533 |  |  | 68.3139 |  |  | 100.8377 |  |  | 146.3171 |  |  | 206.1633 |  |  | 418.9005
[13 empty] | C Choked w/ reducers | 5 |  | 0.14654 |  |  | 4.5562 |  |  | 11.2535 |  |  | 22.3256 |  |  | 39.0302 |  |  | 61.4448 |  |  | 90.3787 |  |  | 130.6413 |  |  | 162.4544 |  |  | 343.7001
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.16365 |  |  | 5.0894 |  |  | 12.548 |  |  | 24.8724 |  |  | 43.4533 |  |  | 68.3139 |  |  | 100.8377 |  |  | 146.3171 |  |  | 206.1633 |  |  | 418.9005
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5664 | 31.0145 |  | 6.5106 | 963.4824 |  | 10.452 | 2359.2145 |  | 14.5276 | 4595.1476 |  | 17.5467 | 7709.2282 |  | 19.8861 | 11251.8286 |  | 20.1623 | 14866.9395 |  | 18.6829 | 18321.8964 |  | 39.8367 | 21271.1529 |  | 1.0995 | 24942.0996
[13 empty] | Next iteration flow rate |  |  | 31.6348 | Abs Value of | Flow this | 973.1172 | Abs Value of | Flow this | 2382.8066 | Abs Value of | Flow this | 4641.0991 | Abs Value of | Flow this | 7786.3205 | Abs Value of | Flow this | 11364.3469 | Abs Value of | Flow this | 15015.6088 | Abs Value of | Flow this | 18505.1153 | Abs Value of | Flow this | 21483.8644 | Abs Value of | Flow this | 25191.5206 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.2003 |  |  | 90.0509 |  |  | 89.5501 |  |  | 88.3159 |  |  | 86.1524 |  |  | 83.1111 |  |  | 79.4178 |  |  | 75.6567 |  |  | 70.1925
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.4351 |  |  | 0.43438 |  |  | 0.43197 |  |  | 0.42601 |  |  | 0.41558 |  |  | 0.40091 |  |  | 0.38309 |  |  | 0.36495 |  |  | 0.33859
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.2003 |  |  | 30.0509 |  |  | 29.5501 |  |  | 28.3159 |  |  | 26.1524 |  |  | 23.1111 |  |  | 19.4178 |  |  | 15.6567 |  |  | 10.1925
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33481 |  |  | 0.33371 |  |  | 0.32998 |  |  | 0.32062 |  |  | 0.30356 |  |  | 0.27807 |  |  | 0.2445 |  |  | 0.20694 |  |  | 0.14521
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82567 |  |  | 0.82459 |  |  | 0.8241 |  |  | 0.82379 |  |  | 0.82316 |  |  | 0.82571 |  |  | 0.82866 |  |  | 0.88319 |  |  | 0.87151
[13 empty] | C Non choked w/ reducers | 5 |  | 0.16692 |  |  | 5.1404 |  |  | 12.6743 |  |  | 25.1271 |  |  | 43.9179 |  |  | 69.1034 |  |  | 102.1464 |  |  | 148.5336 |  |  | 210.1207 |  |  | 430.3179
[13 empty] | C Choked w/ reducers | 5 |  | 0.14947 |  |  | 4.6018 |  |  | 11.3665 |  |  | 22.5523 |  |  | 39.4374 |  |  | 62.1171 |  |  | 91.4365 |  |  | 132.3017 |  |  | 164.7017 |  |  | 349.0896
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.16692 |  |  | 5.1404 |  |  | 12.6743 |  |  | 25.1271 |  |  | 43.9179 |  |  | 69.1034 |  |  | 102.1464 |  |  | 148.5336 |  |  | 210.1207 |  |  | 430.3179
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5631 | 31.6348 |  | 6.4596 | 973.1172 |  | 10.3257 | 2382.8066 |  | 14.2729 | 4641.0991 |  | 17.0821 | 7786.3205 |  | 19.0966 | 11364.3469 |  | 18.8536 | 15015.6088 |  | 16.4664 | 18505.1153 |  | 35.8793 | 21483.8644 |  | 10.3179 | 25191.5206
[13 empty] | Next iteration flow rate |  |  | 32.2675 | Abs Value of | Flow this | 982.8484 | Abs Value of | Flow this | 2406.6347 | Abs Value of | Flow this | 4687.5101 | Abs Value of | Flow this | 7864.1837 | Abs Value of | Flow this | 11477.9903 | Abs Value of | Flow this | 15165.7649 | Abs Value of | Flow this | 18690.1665 | Abs Value of | Flow this | 21698.703 | Abs Value of | Flow this | 25443.4358 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1997 |  |  | 90.0473 |  |  | 89.5364 |  |  | 88.2774 |  |  | 86.0704 |  |  | 82.968 |  |  | 79.2005 |  |  | 75.3638 |  |  | 69.7898
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.4351 |  |  | 0.43437 |  |  | 0.4319 |  |  | 0.42583 |  |  | 0.41518 |  |  | 0.40022 |  |  | 0.38204 |  |  | 0.36354 |  |  | 0.33665
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1997 |  |  | 30.0473 |  |  | 29.5364 |  |  | 28.2774 |  |  | 26.0704 |  |  | 22.968 |  |  | 19.2005 |  |  | 15.3638 |  |  | 9.7898
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33481 |  |  | 0.33368 |  |  | 0.32988 |  |  | 0.32032 |  |  | 0.3029 |  |  | 0.27683 |  |  | 0.24243 |  |  | 0.20386 |  |  | 0.14028
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82567 |  |  | 0.8246 |  |  | 0.82415 |  |  | 0.82395 |  |  | 0.82354 |  |  | 0.82649 |  |  | 0.83011 |  |  | 0.88493 |  |  | 0.87587
[13 empty] | C Non choked w/ reducers | 5 |  | 0.17026 |  |  | 5.1919 |  |  | 12.8019 |  |  | 25.3845 |  |  | 44.3882 |  |  | 69.9045 |  |  | 103.4802 |  |  | 150.808 |  |  | 214.2293 |  |  | 442.5325
[13 empty] | C Choked w/ reducers | 5 |  | 0.15246 |  |  | 4.6478 |  |  | 11.4806 |  |  | 22.7813 |  |  | 39.8491 |  |  | 62.7981 |  |  | 92.5101 |  |  | 133.9914 |  |  | 166.9953 |  |  | 354.6153
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.17026 |  |  | 5.1919 |  |  | 12.8019 |  |  | 25.3845 |  |  | 44.3882 |  |  | 69.9045 |  |  | 103.4802 |  |  | 150.808 |  |  | 214.2293 |  |  | 442.5325
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5597 | 32.2675 |  | 6.4081 | 982.8484 |  | 10.1981 | 2406.6347 |  | 14.0155 | 4687.5101 |  | 16.6118 | 7864.1837 |  | 18.2955 | 11477.9903 |  | 17.5198 | 15165.7649 |  | 14.192 | 18690.1665 |  | 31.7707 | 21698.703 |  | 22.5325 | 25443.4358
[13 empty] | Next iteration flow rate |  |  | 32.9128 | Abs Value of | Flow this | 992.6769 | Abs Value of | Flow this | 2430.701 | Abs Value of | Flow this | 4734.3852 | Abs Value of | Flow this | 7942.8256 | Abs Value of | Flow this | 11592.7702 | Abs Value of | Flow this | 15317.4226 | Abs Value of | Flow this | 18877.0681 | Abs Value of | Flow this | 21915.6901 | Abs Value of | Flow this | 25697.8702 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1991 |  |  | 90.0436 |  |  | 89.5225 |  |  | 88.2382 |  |  | 85.9868 |  |  | 82.822 |  |  | 78.9788 |  |  | 75.065 |  |  | 69.3789
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.4351 |  |  | 0.43435 |  |  | 0.43183 |  |  | 0.42564 |  |  | 0.41478 |  |  | 0.39951 |  |  | 0.38097 |  |  | 0.36209 |  |  | 0.33467
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1991 |  |  | 30.0436 |  |  | 29.5225 |  |  | 28.2382 |  |  | 25.9868 |  |  | 22.822 |  |  | 18.9788 |  |  | 15.065 |  |  | 9.3789
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.3348 |  |  | 0.33366 |  |  | 0.32978 |  |  | 0.32002 |  |  | 0.30222 |  |  | 0.27556 |  |  | 0.2403 |  |  | 0.20069 |  |  | 0.13518
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82567 |  |  | 0.82461 |  |  | 0.82421 |  |  | 0.82412 |  |  | 0.82394 |  |  | 0.82729 |  |  | 0.8316 |  |  | 0.88672 |  |  | 0.88038
[13 empty] | C Non choked w/ reducers | 5 |  | 0.17366 |  |  | 5.2438 |  |  | 12.9307 |  |  | 25.6447 |  |  | 44.8641 |  |  | 70.7175 |  |  | 104.8397 |  |  | 153.1431 |  |  | 218.4997 |  |  | 455.649
[13 empty] | C Choked w/ reducers | 5 |  | 0.15551 |  |  | 4.6943 |  |  | 11.5959 |  |  | 23.0127 |  |  | 40.2655 |  |  | 63.4877 |  |  | 93.5999 |  |  | 135.7111 |  |  | 169.3367 |  |  | 360.2824
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.17366 |  |  | 5.2438 |  |  | 12.9307 |  |  | 25.6447 |  |  | 44.8641 |  |  | 70.7175 |  |  | 104.8397 |  |  | 153.1431 |  |  | 218.4997 |  |  | 455.649
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5563 | 32.9128 |  | 6.3562 | 992.6769 |  | 10.0693 | 2430.701 |  | 13.7553 | 4734.3852 |  | 16.1359 | 7942.8256 |  | 17.4825 | 11592.7702 |  | 16.1603 | 15317.4226 |  | 11.8569 | 18877.0681 |  | 27.5003 | 21915.6901 |  | 35.649 | 25697.8702
[13 empty] | Next iteration flow rate |  |  | 33.5711 | Abs Value of | Flow this | 1002.6036 | Abs Value of | Flow this | 2455.008 | Abs Value of | Flow this | 4781.729 | Abs Value of | Flow this | 8022.2538 | Abs Value of | Flow this | 11708.6979 | Abs Value of | Flow this | 15470.5968 | Abs Value of | Flow this | 19065.8388 | Abs Value of | Flow this | 22134.847 | Abs Value of | Flow this | 25954.8489 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1984 |  |  | 90.0399 |  |  | 89.5082 |  |  | 88.1981 |  |  | 85.9015 |  |  | 82.6731 |  |  | 78.7526 |  |  | 74.7601 |  |  | 68.9598
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43509 |  |  | 0.43433 |  |  | 0.43177 |  |  | 0.42545 |  |  | 0.41437 |  |  | 0.39879 |  |  | 0.37988 |  |  | 0.36062 |  |  | 0.33264
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1984 |  |  | 30.0399 |  |  | 29.5082 |  |  | 28.1981 |  |  | 25.9015 |  |  | 22.6731 |  |  | 18.7526 |  |  | 14.7601 |  |  | 8.9598
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.3348 |  |  | 0.33363 |  |  | 0.32967 |  |  | 0.31971 |  |  | 0.30153 |  |  | 0.27425 |  |  | 0.23812 |  |  | 0.19743 |  |  | 0.12993
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82567 |  |  | 0.82463 |  |  | 0.82427 |  |  | 0.82429 |  |  | 0.82434 |  |  | 0.82811 |  |  | 0.83313 |  |  | 0.88856 |  |  | 0.88503
[13 empty] | C Non choked w/ reducers | 5 |  | 0.17714 |  |  | 5.2963 |  |  | 13.0609 |  |  | 25.9076 |  |  | 45.3459 |  |  | 71.5426 |  |  | 106.2259 |  |  | 155.5417 |  |  | 222.9434 |  |  | 469.7927
[13 empty] | C Choked w/ reducers | 5 |  | 0.15862 |  |  | 4.7413 |  |  | 11.7124 |  |  | 23.2465 |  |  | 40.6866 |  |  | 64.1863 |  |  | 94.7062 |  |  | 137.4619 |  |  | 171.7274 |  |  | 366.0968
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.17714 |  |  | 5.2963 |  |  | 13.0609 |  |  | 25.9076 |  |  | 45.3459 |  |  | 71.5426 |  |  | 106.2259 |  |  | 155.5417 |  |  | 222.9434 |  |  | 469.7927
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5529 | 33.5711 |  | 6.3037 | 1002.6036 |  | 9.9391 | 2455.008 |  | 13.4924 | 4781.729 |  | 15.6541 | 8022.2538 |  | 16.6574 | 11708.6979 |  | 14.7741 | 15470.5968 |  | 9.4583 | 19065.8388 |  | 23.0566 | 22134.847 |  | 49.7927 | 25954.8489
[13 empty] | Next iteration flow rate |  |  | 34.2425 | Abs Value of | Flow this | 1012.6297 | Abs Value of | Flow this | 2479.5581 | Abs Value of | Flow this | 4829.5463 | Abs Value of | Flow this | 8102.4763 | Abs Value of | Flow this | 11825.7849 | Abs Value of | Flow this | 15625.3028 | Abs Value of | Flow this | 19256.4972 | Abs Value of | Flow this | 22356.1955 | Abs Value of | Flow this | 26214.3974 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1978 |  |  | 90.0361 |  |  | 89.4937 |  |  | 88.1573 |  |  | 85.8145 |  |  | 82.5212 |  |  | 78.5219 |  |  | 74.4492 |  |  | 68.5323
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43509 |  |  | 0.43431 |  |  | 0.4317 |  |  | 0.42525 |  |  | 0.41395 |  |  | 0.39806 |  |  | 0.37877 |  |  | 0.35912 |  |  | 0.33058
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1978 |  |  | 30.0361 |  |  | 29.4937 |  |  | 28.1573 |  |  | 25.8145 |  |  | 22.5212 |  |  | 18.5219 |  |  | 14.4492 |  |  | 8.5323
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.3348 |  |  | 0.3336 |  |  | 0.32956 |  |  | 0.3194 |  |  | 0.30082 |  |  | 0.27291 |  |  | 0.23588 |  |  | 0.19408 |  |  | 0.1245
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82568 |  |  | 0.82464 |  |  | 0.82432 |  |  | 0.82446 |  |  | 0.82475 |  |  | 0.82895 |  |  | 0.8347 |  |  | 0.89045 |  |  | 0.88983
[13 empty] | C Non choked w/ reducers | 5 |  | 0.18068 |  |  | 5.3493 |  |  | 13.1924 |  |  | 26.1734 |  |  | 45.8335 |  |  | 72.3802 |  |  | 107.6395 |  |  | 158.007 |  |  | 227.573 |  |  | 485.1147
[13 empty] | C Choked w/ reducers | 5 |  | 0.16179 |  |  | 4.7888 |  |  | 11.83 |  |  | 23.4828 |  |  | 41.1125 |  |  | 64.8938 |  |  | 95.8293 |  |  | 139.2444 |  |  | 174.1691 |  |  | 372.0645
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.18068 |  |  | 5.3493 |  |  | 13.1924 |  |  | 26.1734 |  |  | 45.8335 |  |  | 72.3802 |  |  | 107.6395 |  |  | 158.007 |  |  | 227.573 |  |  | 485.1147
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5493 | 34.2425 |  | 6.2507 | 1012.6297 |  | 9.8076 | 2479.5581 |  | 13.2266 | 4829.5463 |  | 15.1665 | 8102.4763 |  | 15.8198 | 11825.7849 |  | 13.3605 | 15625.3028 |  | 6.993 | 19256.4972 |  | 18.427 | 22356.1955 |  | 65.1147 | 26214.3974
[13 empty] | Next iteration flow rate |  |  | 34.9274 | Abs Value of | Flow this | 1022.756 | Abs Value of | Flow this | 2504.3537 | Abs Value of | Flow this | 4877.8418 | Abs Value of | Flow this | 8183.5011 | Abs Value of | Flow this | 11944.0428 | Abs Value of | Flow this | 15781.5558 | Abs Value of | Flow this | 19449.0622 | Abs Value of | Flow this | 22579.7574 | Abs Value of | Flow this | 26476.5413 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1972 |  |  | 90.0321 |  |  | 89.4789 |  |  | 88.1156 |  |  | 85.7257 |  |  | 82.3663 |  |  | 78.2866 |  |  | 74.132 |  |  | 68.0961
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43509 |  |  | 0.43429 |  |  | 0.43162 |  |  | 0.42505 |  |  | 0.41352 |  |  | 0.39731 |  |  | 0.37763 |  |  | 0.35759 |  |  | 0.32848
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1972 |  |  | 30.0321 |  |  | 29.4789 |  |  | 28.1156 |  |  | 25.7257 |  |  | 22.3663 |  |  | 18.2866 |  |  | 14.132 |  |  | 8.0961
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33479 |  |  | 0.33357 |  |  | 0.32945 |  |  | 0.31908 |  |  | 0.30009 |  |  | 0.27155 |  |  | 0.23359 |  |  | 0.19063 |  |  | 0.11889
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82568 |  |  | 0.82466 |  |  | 0.82438 |  |  | 0.82464 |  |  | 0.82518 |  |  | 0.8298 |  |  | 0.83631 |  |  | 0.8924 |  |  | 0.89479
[13 empty] | C Non choked w/ reducers | 5 |  | 0.18429 |  |  | 5.4029 |  |  | 13.3252 |  |  | 26.4421 |  |  | 46.3272 |  |  | 73.2305 |  |  | 109.0816 |  |  | 160.5423 |  |  | 232.4026 |  |  | 501.7997
[13 empty] | C Choked w/ reducers | 5 |  | 0.16502 |  |  | 4.8367 |  |  | 11.9488 |  |  | 23.7215 |  |  | 41.5433 |  |  | 65.6106 |  |  | 96.9697 |  |  | 141.0596 |  |  | 176.6635 |  |  | 378.1919
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.18429 |  |  | 5.4029 |  |  | 13.3252 |  |  | 26.4421 |  |  | 46.3272 |  |  | 73.2305 |  |  | 109.0816 |  |  | 160.5423 |  |  | 232.4026 |  |  | 501.7997
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5457 | 34.9274 |  | 6.1971 | 1022.756 |  | 9.6748 | 2504.3537 |  | 12.9579 | 4877.8418 |  | 14.6728 | 8183.5011 |  | 14.9695 | 11944.0428 |  | 11.9184 | 15781.5558 |  | 4.4577 | 19449.0622 |  | 13.5974 | 22579.7574 |  | 81.7997 | 26476.5413
[13 empty] | Next iteration flow rate |  |  | 35.6259 | Abs Value of | Flow this | 1032.9835 | Abs Value of | Flow this | 2529.3972 | Abs Value of | Flow this | 4926.6202 | Abs Value of | Flow this | 8265.3361 | Abs Value of | Flow this | 12063.4832 | Abs Value of | Flow this | 15939.3714 | Abs Value of | Flow this | 19643.5528 | Abs Value of | Flow this | 22805.555 | Abs Value of | Flow this | 26741.3068 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1965 |  |  | 90.0282 |  |  | 89.4638 |  |  | 88.0731 |  |  | 85.6352 |  |  | 82.2082 |  |  | 78.0465 |  |  | 73.8084 |  |  | 67.6512
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43509 |  |  | 0.43427 |  |  | 0.43155 |  |  | 0.42484 |  |  | 0.41308 |  |  | 0.39655 |  |  | 0.37648 |  |  | 0.35603 |  |  | 0.32633
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1965 |  |  | 30.0282 |  |  | 29.4638 |  |  | 28.0731 |  |  | 25.6352 |  |  | 22.2082 |  |  | 18.0465 |  |  | 13.8084 |  |  | 7.6512
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33479 |  |  | 0.33354 |  |  | 0.32934 |  |  | 0.31875 |  |  | 0.29935 |  |  | 0.27015 |  |  | 0.23123 |  |  | 0.18708 |  |  | 0.1131
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82568 |  |  | 0.82467 |  |  | 0.82444 |  |  | 0.82482 |  |  | 0.82561 |  |  | 0.83068 |  |  | 0.83796 |  |  | 0.8944 |  |  | 0.89992
[13 empty] | C Non choked w/ reducers | 5 |  | 0.18798 |  |  | 5.457 |  |  | 13.4594 |  |  | 26.7137 |  |  | 46.8269 |  |  | 74.0937 |  |  | 110.5531 |  |  | 163.1512 |  |  | 237.4479 |  |  | 520.0756
[13 empty] | C Choked w/ reducers | 5 |  | 0.16833 |  |  | 4.8851 |  |  | 12.0688 |  |  | 23.9628 |  |  | 41.979 |  |  | 66.3368 |  |  | 98.1277 |  |  | 142.9084 |  |  | 179.2123 |  |  | 384.4858
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.18798 |  |  | 5.457 |  |  | 13.4594 |  |  | 26.7137 |  |  | 46.8269 |  |  | 74.0937 |  |  | 110.5531 |  |  | 163.1512 |  |  | 237.4479 |  |  | 520.0756
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.542 | 35.6259 |  | 6.143 | 1032.9835 |  | 9.5406 | 2529.3972 |  | 12.6863 | 4926.6202 |  | 14.1731 | 8265.3361 |  | 14.1063 | 12063.4832 |  | 10.4469 | 15939.3714 |  | 1.8488 | 19643.5528 |  | 8.5521 | 22805.555 |  | 100.0756 | 26741.3068
[13 empty] | Next iteration flow rate |  |  | 36.3384 | Abs Value of | Flow this | 1043.3134 | Abs Value of | Flow this | 2554.6912 | Abs Value of | Flow this | 4975.8864 | Abs Value of | Flow this | 8347.9895 | Abs Value of | Flow this | 12184.118 | Abs Value of | Flow this | 16098.7651 | Abs Value of | Flow this | 19839.9883 | Abs Value of | Flow this | 23033.6105 | Abs Value of | Flow this | 27008.7198 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1958 |  |  | 90.0241 |  |  | 89.4484 |  |  | 88.0298 |  |  | 85.5428 |  |  | 82.047 |  |  | 77.8016 |  |  | 73.4783 |  |  | 67.1974
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43508 |  |  | 0.43425 |  |  | 0.43148 |  |  | 0.42463 |  |  | 0.41264 |  |  | 0.39577 |  |  | 0.3753 |  |  | 0.35444 |  |  | 0.32414
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1958 |  |  | 30.0241 |  |  | 29.4484 |  |  | 28.0298 |  |  | 25.5428 |  |  | 22.047 |  |  | 17.8016 |  |  | 13.4783 |  |  | 7.1974
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33478 |  |  | 0.33351 |  |  | 0.32922 |  |  | 0.31841 |  |  | 0.2986 |  |  | 0.26871 |  |  | 0.22881 |  |  | 0.18343 |  |  | 0.10711
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82568 |  |  | 0.82469 |  |  | 0.82451 |  |  | 0.825 |  |  | 0.82605 |  |  | 0.83158 |  |  | 0.83966 |  |  | 0.89646 |  |  | 0.90522
[13 empty] | C Non choked w/ reducers | 5 |  | 0.19174 |  |  | 5.5116 |  |  | 13.5949 |  |  | 26.9882 |  |  | 47.3328 |  |  | 74.9703 |  |  | 112.055 |  |  | 165.8376 |  |  | 242.7264 |  |  | 540.2279
[13 empty] | C Choked w/ reducers | 5 |  | 0.17169 |  |  | 4.934 |  |  | 12.1901 |  |  | 24.2066 |  |  | 42.4196 |  |  | 67.0725 |  |  | 99.3038 |  |  | 144.7918 |  |  | 181.8176 |  |  | 390.9533
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.19174 |  |  | 5.5116 |  |  | 13.5949 |  |  | 26.9882 |  |  | 47.3328 |  |  | 74.9703 |  |  | 112.055 |  |  | 165.8376 |  |  | 242.7264 |  |  | 540.2279
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5383 | 36.3384 |  | 6.0884 | 1043.3134 |  | 9.4051 | 2554.6912 |  | 12.4118 | 4975.8864 |  | 13.6672 | 8347.9895 |  | 13.2297 | 12184.118 |  | 8.945 | 16098.7651 |  | 0.83759 | 19839.9883 |  | 3.2736 | 23033.6105 |  | 120.2279 | 27008.7198
[13 empty] | Next iteration flow rate |  |  | 37.0652 | Abs Value of | Flow this | 1053.7465 | Abs Value of | Flow this | 2580.2381 | Abs Value of | Flow this | 5025.6453 | Abs Value of | Flow this | 8431.4694 | Abs Value of | Flow this | 12305.9592 | Abs Value of | Flow this | 16259.7527 | Abs Value of | Flow this | 20038.3882 | Abs Value of | Flow this | 23263.9466 | Abs Value of | Flow this | 27278.807 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1951 |  |  | 90.02 |  |  | 89.4327 |  |  | 87.9855 |  |  | 85.4486 |  |  | 81.8825 |  |  | 77.5518 |  |  | 73.1416 |  |  | 66.7344
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43508 |  |  | 0.43423 |  |  | 0.4314 |  |  | 0.42442 |  |  | 0.41218 |  |  | 0.39498 |  |  | 0.37409 |  |  | 0.35282 |  |  | 0.32191
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1951 |  |  | 30.02 |  |  | 29.4327 |  |  | 27.9855 |  |  | 25.4486 |  |  | 21.8825 |  |  | 17.5518 |  |  | 13.1416 |  |  | 6.7344
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33478 |  |  | 0.33348 |  |  | 0.3291 |  |  | 0.31807 |  |  | 0.29782 |  |  | 0.26724 |  |  | 0.22632 |  |  | 0.17967 |  |  | 0.10091
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82569 |  |  | 0.82471 |  |  | 0.82457 |  |  | 0.82519 |  |  | 0.8265 |  |  | 0.8325 |  |  | 0.8414 |  |  | 0.89858 |  |  | 0.9107
[13 empty] | C Non choked w/ reducers | 5 |  | 0.19557 |  |  | 5.5668 |  |  | 13.7319 |  |  | 27.2656 |  |  | 47.845 |  |  | 75.8604 |  |  | 113.5883 |  |  | 168.6056 |  |  | 248.2576 |  |  | 562.6195
[13 empty] | C Choked w/ reducers | 5 |  | 0.17513 |  |  | 4.9834 |  |  | 12.3125 |  |  | 24.4529 |  |  | 42.8654 |  |  | 67.8179 |  |  | 100.4983 |  |  | 146.7108 |  |  | 184.4811 |  |  | 397.6021
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.19557 |  |  | 5.5668 |  |  | 13.7319 |  |  | 27.2656 |  |  | 47.845 |  |  | 75.8604 |  |  | 113.5883 |  |  | 168.6056 |  |  | 248.2576 |  |  | 562.6195
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5344 | 37.0652 |  | 6.0332 | 1053.7465 |  | 9.2681 | 2580.2381 |  | 12.1344 | 5025.6453 |  | 13.155 | 8431.4694 |  | 12.3396 | 12305.9592 |  | 7.4117 | 16259.7527 |  | 3.6056 | 20038.3882 |  | 2.2576 | 23263.9466 |  | 142.6195 | 27278.807
[13 empty] | Next iteration flow rate |  |  | 37.8065 | Abs Value of | Flow this | 1064.284 | Abs Value of | Flow this | 2606.0405 | Abs Value of | Flow this | 5075.9017 | Abs Value of | Flow this | 8515.7841 | Abs Value of | Flow this | 12429.0188 | Abs Value of | Flow this | 16422.3503 | Abs Value of | Flow this | 20238.7721 | Abs Value of | Flow this | 23496.5861 | Abs Value of | Flow this | 27551.5951 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1944 |  |  | 90.0157 |  |  | 89.4167 |  |  | 87.9404 |  |  | 85.3525 |  |  | 81.7147 |  |  | 77.297 |  |  | 72.7982 |  |  | 66.2622
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43508 |  |  | 0.43421 |  |  | 0.43132 |  |  | 0.4242 |  |  | 0.41172 |  |  | 0.39417 |  |  | 0.37286 |  |  | 0.35116 |  |  | 0.31963
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1944 |  |  | 30.0157 |  |  | 29.4167 |  |  | 27.9404 |  |  | 25.3525 |  |  | 21.7147 |  |  | 17.297 |  |  | 12.7982 |  |  | 6.2622
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33477 |  |  | 0.33345 |  |  | 0.32898 |  |  | 0.31772 |  |  | 0.29703 |  |  | 0.26574 |  |  | 0.22377 |  |  | 0.1758 |  |  | 0.094506
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82569 |  |  | 0.82472 |  |  | 0.82463 |  |  | 0.82538 |  |  | 0.82696 |  |  | 0.83345 |  |  | 0.84319 |  |  | 0.90077 |  |  | 0.91637
[13 empty] | C Non choked w/ reducers | 5 |  | 0.19948 |  |  | 5.6226 |  |  | 13.8702 |  |  | 27.5461 |  |  | 48.3636 |  |  | 76.7646 |  |  | 115.1543 |  |  | 171.4598 |  |  | 254.0637 |  |  | 587.7203
[13 empty] | C Choked w/ reducers | 5 |  | 0.17863 |  |  | 5.0332 |  |  | 12.4362 |  |  | 24.7019 |  |  | 43.3162 |  |  | 68.5732 |  |  | 101.7117 |  |  | 148.6665 |  |  | 187.205 |  |  | 404.4403
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.19948 |  |  | 5.6226 |  |  | 13.8702 |  |  | 27.5461 |  |  | 48.3636 |  |  | 76.7646 |  |  | 115.1543 |  |  | 171.4598 |  |  | 254.0637 |  |  | 587.7203
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5305 | 37.8065 |  | 5.9774 | 1064.284 |  | 9.1298 | 2606.0405 |  | 11.8539 | 5075.9017 |  | 12.6364 | 8515.7841 |  | 11.4354 | 12429.0188 |  | 5.8457 | 16422.3503 |  | 6.4598 | 20238.7721 |  | 8.0637 | 23496.5861 |  | 167.7203 | 27551.5951
[13 empty] | Next iteration flow rate |  |  | 38.5626 | Abs Value of | Flow this | 1074.9268 | Abs Value of | Flow this | 2632.1009 | Abs Value of | Flow this | 5126.6607 | Abs Value of | Flow this | 8600.9419 | Abs Value of | Flow this | 12553.309 | Abs Value of | Flow this | 16586.5738 | Abs Value of | Flow this | 20441.1598 | Abs Value of | Flow this | 23731.552 | Abs Value of | Flow this | 27827.111 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1937 |  |  | 90.0114 |  |  | 89.4003 |  |  | 87.8944 |  |  | 85.2545 |  |  | 81.5435 |  |  | 77.037 |  |  | 72.4478 |  |  | 65.7804
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43507 |  |  | 0.43419 |  |  | 0.43124 |  |  | 0.42398 |  |  | 0.41125 |  |  | 0.39335 |  |  | 0.37161 |  |  | 0.34947 |  |  | 0.31731
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1937 |  |  | 30.0114 |  |  | 29.4003 |  |  | 27.8944 |  |  | 25.2545 |  |  | 21.5435 |  |  | 17.037 |  |  | 12.4478 |  |  | 5.7804
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33477 |  |  | 0.33342 |  |  | 0.32886 |  |  | 0.31736 |  |  | 0.29622 |  |  | 0.2642 |  |  | 0.22115 |  |  | 0.17182 |  |  | 0.087875
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82569 |  |  | 0.82474 |  |  | 0.8247 |  |  | 0.82558 |  |  | 0.82743 |  |  | 0.83441 |  |  | 0.84502 |  |  | 0.90302 |  |  | 0.92224
[13 empty] | C Non choked w/ reducers | 5 |  | 0.20347 |  |  | 5.6788 |  |  | 14.01 |  |  | 27.8297 |  |  | 48.8886 |  |  | 77.683 |  |  | 116.7542 |  |  | 174.4051 |  |  | 260.1693 |  |  | 616.1512
[13 empty] | C Choked w/ reducers | 5 |  | 0.1822 |  |  | 5.0836 |  |  | 12.5612 |  |  | 24.9535 |  |  | 43.7723 |  |  | 69.3386 |  |  | 102.9444 |  |  | 150.6598 |  |  | 189.9915 |  |  | 411.4763
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.20347 |  |  | 5.6788 |  |  | 14.01 |  |  | 27.8297 |  |  | 48.8886 |  |  | 77.683 |  |  | 116.7542 |  |  | 174.4051 |  |  | 260.1693 |  |  | 616.1512
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5265 | 38.5626 |  | 5.9212 | 1074.9268 |  | 8.99 | 2632.1009 |  | 11.5703 | 5126.6607 |  | 12.1114 | 8600.9419 |  | 10.517 | 12553.309 |  | 4.2458 | 16586.5738 |  | 9.4051 | 20441.1598 |  | 14.1693 | 23731.552 |  | 196.1512 | 27827.111
[13 empty] | Next iteration flow rate |  |  | 39.3339 | Abs Value of | Flow this | 1085.6761 | Abs Value of | Flow this | 2658.4219 | Abs Value of | Flow this | 5177.9273 | Abs Value of | Flow this | 8686.9513 | Abs Value of | Flow this | 12678.8421 | Abs Value of | Flow this | 16752.4395 | Abs Value of | Flow this | 20645.5714 | Abs Value of | Flow this | 23968.8675 | Abs Value of | Flow this | 28105.3822 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.193 |  |  | 90.007 |  |  | 89.3836 |  |  | 87.8475 |  |  | 85.1545 |  |  | 81.3689 |  |  | 76.7718 |  |  | 72.0903 |  |  | 65.289
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43507 |  |  | 0.43417 |  |  | 0.43116 |  |  | 0.42375 |  |  | 0.41076 |  |  | 0.3925 |  |  | 0.37033 |  |  | 0.34775 |  |  | 0.31494
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.193 |  |  | 30.007 |  |  | 29.3836 |  |  | 27.8475 |  |  | 25.1545 |  |  | 21.3689 |  |  | 16.7718 |  |  | 12.0903 |  |  | 5.289
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33476 |  |  | 0.33339 |  |  | 0.32874 |  |  | 0.317 |  |  | 0.2954 |  |  | 0.26262 |  |  | 0.21846 |  |  | 0.16771 |  |  | 0.081009
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82569 |  |  | 0.82476 |  |  | 0.82476 |  |  | 0.82578 |  |  | 0.82791 |  |  | 0.8354 |  |  | 0.84691 |  |  | 0.90533 |  |  | 0.92832
[13 empty] | C Non choked w/ reducers | 5 |  | 0.20754 |  |  | 5.7357 |  |  | 14.1512 |  |  | 28.1163 |  |  | 49.4203 |  |  | 78.616 |  |  | 118.389 |  |  | 177.4467 |  |  | 266.6027 |  |  | 648.7526
[13 empty] | C Choked w/ reducers | 5 |  | 0.18584 |  |  | 5.1345 |  |  | 12.6874 |  |  | 25.2077 |  |  | 44.2337 |  |  | 70.1143 |  |  | 104.197 |  |  | 152.692 |  |  | 192.8429 |  |  | 418.7193
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.20754 |  |  | 5.7357 |  |  | 14.1512 |  |  | 28.1163 |  |  | 49.4203 |  |  | 78.616 |  |  | 118.389 |  |  | 177.4467 |  |  | 266.6027 |  |  | 648.7526
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5225 | 39.3339 |  | 5.8643 | 1085.6761 |  | 8.8488 | 2658.4219 |  | 11.2837 | 5177.9273 |  | 11.5797 | 8686.9513 |  | 9.584 | 12678.8421 |  | 2.611 | 16752.4395 |  | 12.4467 | 20645.5714 |  | 20.6027 | 23968.8675 |  | 228.7526 | 28105.3822
[13 empty] | Next iteration flow rate |  |  | 40.1206 | Abs Value of | Flow this | 1096.5328 | Abs Value of | Flow this | 2685.0061 | Abs Value of | Flow this | 5229.7066 | Abs Value of | Flow this | 8773.8208 | Abs Value of | Flow this | 12805.6305 | Abs Value of | Flow this | 16919.9639 | Abs Value of | Flow this | 20852.0271 | Abs Value of | Flow this | 24208.5562 | Abs Value of | Flow this | 28386.436 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1922 |  |  | 90.0025 |  |  | 89.3666 |  |  | 87.7996 |  |  | 85.0524 |  |  | 81.1908 |  |  | 76.5013 |  |  | 71.7257 |  |  | 64.7877
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43506 |  |  | 0.43415 |  |  | 0.43108 |  |  | 0.42352 |  |  | 0.41027 |  |  | 0.39164 |  |  | 0.36902 |  |  | 0.34599 |  |  | 0.31252
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1922 |  |  | 30.0025 |  |  | 29.3666 |  |  | 27.7996 |  |  | 25.0524 |  |  | 21.1908 |  |  | 16.5013 |  |  | 11.7257 |  |  | 4.7877
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33475 |  |  | 0.33335 |  |  | 0.32861 |  |  | 0.31663 |  |  | 0.29455 |  |  | 0.261 |  |  | 0.2157 |  |  | 0.16348 |  |  | 0.073898
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.8257 |  |  | 0.82477 |  |  | 0.82483 |  |  | 0.82599 |  |  | 0.8284 |  |  | 0.83641 |  |  | 0.84884 |  |  | 0.90772 |  |  | 0.93461
[13 empty] | C Non choked w/ reducers | 5 |  | 0.21169 |  |  | 5.7931 |  |  | 14.2938 |  |  | 28.406 |  |  | 49.9587 |  |  | 79.5641 |  |  | 120.0603 |  |  | 180.5905 |  |  | 273.396 |  |  | 686.6961
[13 empty] | C Choked w/ reducers | 5 |  | 0.18956 |  |  | 5.1859 |  |  | 12.8149 |  |  | 25.4646 |  |  | 44.7004 |  |  | 70.9003 |  |  | 105.4698 |  |  | 154.7643 |  |  | 195.7614 |  |  | 426.1789
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.21169 |  |  | 5.7931 |  |  | 14.2938 |  |  | 28.406 |  |  | 49.9587 |  |  | 79.5641 |  |  | 120.0603 |  |  | 180.5905 |  |  | 273.396 |  |  | 686.6961
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5183 | 40.1206 |  | 5.8069 | 1096.5328 |  | 8.7062 | 2685.0061 |  | 10.994 | 5229.7066 |  | 11.0413 | 8773.8208 |  | 8.6359 | 12805.6305 |  | 0.9397 | 16919.9639 |  | 15.5905 | 20852.0271 |  | 27.396 | 24208.5562 |  | 266.6961 | 28386.436
[13 empty] | Next iteration flow rate |  |  | 40.923 | Abs Value of | Flow this | 1107.4982 | Abs Value of | Flow this | 2711.8562 | Abs Value of | Flow this | 5282.0037 | Abs Value of | Flow this | 8861.5591 | Abs Value of | Flow this | 12933.6868 | Abs Value of | Flow this | 17089.1635 | Abs Value of | Flow this | 21060.5474 | Abs Value of | Flow this | 24450.6417 | Abs Value of | Flow this | 28670.3003 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1915 |  |  | 89.998 |  |  | 89.3493 |  |  | 87.7507 |  |  | 84.9484 |  |  | 81.0091 |  |  | 76.2254 |  |  | 71.3538 |  |  | 64.2763
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43506 |  |  | 0.43413 |  |  | 0.431 |  |  | 0.42329 |  |  | 0.40977 |  |  | 0.39077 |  |  | 0.36769 |  |  | 0.34419 |  |  | 0.31005
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1915 |  |  | 29.998 |  |  | 29.3493 |  |  | 27.7507 |  |  | 24.9484 |  |  | 21.0091 |  |  | 16.2254 |  |  | 11.3538 |  |  | 4.2763
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33475 |  |  | 0.33332 |  |  | 0.32848 |  |  | 0.31624 |  |  | 0.29369 |  |  | 0.25934 |  |  | 0.21286 |  |  | 0.15912 |  |  | 0.06653
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.8257 |  |  | 0.82479 |  |  | 0.8249 |  |  | 0.8262 |  |  | 0.82891 |  |  | 0.83745 |  |  | 0.85083 |  |  | 0.91018 |  |  | 0.94113
[13 empty] | C Non choked w/ reducers | 5 |  | 0.21593 |  |  | 5.8512 |  |  | 14.4379 |  |  | 28.6989 |  |  | 50.504 |  |  | 80.5275 |  |  | 121.7694 |  |  | 183.8426 |  |  | 280.586 |  |  | 731.6725
[13 empty] | C Choked w/ reducers | 5 |  | 0.19335 |  |  | 5.2378 |  |  | 12.9438 |  |  | 25.7243 |  |  | 45.1725 |  |  | 71.6971 |  |  | 106.7634 |  |  | 156.8778 |  |  | 198.7496 |  |  | 433.8653
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.21593 |  |  | 5.8512 |  |  | 14.4379 |  |  | 28.6989 |  |  | 50.504 |  |  | 80.5275 |  |  | 121.7694 |  |  | 183.8426 |  |  | 280.586 |  |  | 731.6725
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5141 | 40.923 |  | 5.7488 | 1107.4982 |  | 8.5621 | 2711.8562 |  | 10.7011 | 5282.0037 |  | 10.496 | 8861.5591 |  | 7.6725 | 12933.6868 |  | 0.76938 | 17089.1635 |  | 18.8426 | 21060.5474 |  | 34.586 | 24450.6417 |  | 311.6725 | 28670.3003
[13 empty] | Next iteration flow rate |  |  | 41.7415 | Abs Value of | Flow this | 1118.5731 | Abs Value of | Flow this | 2738.9748 | Abs Value of | Flow this | 5334.8237 | Abs Value of | Flow this | 8950.1746 | Abs Value of | Flow this | 13063.0237 | Abs Value of | Flow this | 17260.0552 | Abs Value of | Flow this | 21271.1529 | Abs Value of | Flow this | 24695.1481 | Abs Value of | Flow this | 28957.0033 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1907 |  |  | 89.9933 |  |  | 89.3316 |  |  | 87.7009 |  |  | 84.8422 |  |  | 80.8238 |  |  | 75.9439 |  |  | 70.9744 |  |  | 63.7546
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43506 |  |  | 0.43411 |  |  | 0.43091 |  |  | 0.42305 |  |  | 0.40926 |  |  | 0.38987 |  |  | 0.36633 |  |  | 0.34236 |  |  | 0.30754
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1907 |  |  | 29.9933 |  |  | 29.3316 |  |  | 27.7009 |  |  | 24.8422 |  |  | 20.8238 |  |  | 15.9439 |  |  | 10.9744 |  |  | 3.7546
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33474 |  |  | 0.33328 |  |  | 0.32834 |  |  | 0.31586 |  |  | 0.2928 |  |  | 0.25764 |  |  | 0.20994 |  |  | 0.15462 |  |  | 0.058891
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.8257 |  |  | 0.82481 |  |  | 0.82497 |  |  | 0.82641 |  |  | 0.82942 |  |  | 0.83852 |  |  | 0.85288 |  |  | 0.91272 |  |  | 0.94789
[13 empty] | C Non choked w/ reducers | 5 |  | 0.22025 |  |  | 5.9097 |  |  | 14.5835 |  |  | 28.9951 |  |  | 51.0562 |  |  | 81.5067 |  |  | 123.5177 |  |  | 187.2099 |  |  | 288.2151 |  |  | 786.232
[13 empty] | C Choked w/ reducers | 5 |  | 0.19722 |  |  | 5.2902 |  |  | 13.0739 |  |  | 25.9867 |  |  | 45.6502 |  |  | 72.5047 |  |  | 108.0783 |  |  | 159.0339 |  |  | 201.8102 |  |  | 441.7896
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.22025 |  |  | 5.9097 |  |  | 14.5835 |  |  | 28.9951 |  |  | 51.0562 |  |  | 81.5067 |  |  | 123.5177 |  |  | 187.2099 |  |  | 288.2151 |  |  | 786.232
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5098 | 41.7415 |  | 5.6903 | 1118.5731 |  | 8.4165 | 2738.9748 |  | 10.4049 | 5334.8237 |  | 9.9438 | 8950.1746 |  | 6.6933 | 13063.0237 |  | 2.5177 | 17260.0552 |  | 22.2099 | 21271.1529 |  | 42.2151 | 24695.1481 |  | 366.232 | 28957.0033
[13 empty] | Next iteration flow rate |  |  | 42.5763 | Abs Value of | Flow this | 1129.7589 | Abs Value of | Flow this | 2766.3645 | Abs Value of | Flow this | 5388.172 | Abs Value of | Flow this | 9039.6764 | Abs Value of | Flow this | 13193.6539 | Abs Value of | Flow this | 17432.6557 | Abs Value of | Flow this | 21483.8644 | Abs Value of | Flow this | 24942.0996 | Abs Value of | Flow this | 29246.5734 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1899 |  |  | 89.9885 |  |  | 89.3135 |  |  | 87.65 |  |  | 84.7339 |  |  | 80.6347 |  |  | 75.6567 |  |  | 70.5873 |  |  | 63.2224
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43505 |  |  | 0.43408 |  |  | 0.43083 |  |  | 0.4228 |  |  | 0.40874 |  |  | 0.38896 |  |  | 0.36495 |  |  | 0.3405 |  |  | 0.30497
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1899 |  |  | 29.9885 |  |  | 29.3135 |  |  | 27.65 |  |  | 24.7339 |  |  | 20.6347 |  |  | 15.6567 |  |  | 10.5873 |  |  | 3.2224
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33474 |  |  | 0.33325 |  |  | 0.32821 |  |  | 0.31546 |  |  | 0.2919 |  |  | 0.2559 |  |  | 0.20694 |  |  | 0.14999 |  |  | 0.05097
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82571 |  |  | 0.82483 |  |  | 0.82505 |  |  | 0.82663 |  |  | 0.82995 |  |  | 0.83961 |  |  | 0.85498 |  |  | 0.91534 |  |  | 0.9549
[13 empty] | C Non choked w/ reducers | 5 |  | 0.22465 |  |  | 5.9689 |  |  | 14.7305 |  |  | 29.2944 |  |  | 51.6155 |  |  | 82.5022 |  |  | 125.3069 |  |  | 190.7 |  |  | 296.3322 |  |  | 854.4403
[13 empty] | C Choked w/ reducers | 5 |  | 0.20116 |  |  | 5.3431 |  |  | 13.2053 |  |  | 26.2518 |  |  | 46.1334 |  |  | 73.3233 |  |  | 109.4151 |  |  | 161.2339 |  |  | 204.946 |  |  | 449.9634
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.22465 |  |  | 5.9689 |  |  | 14.7305 |  |  | 29.2944 |  |  | 51.6155 |  |  | 82.5022 |  |  | 125.3069 |  |  | 190.7 |  |  | 296.3322 |  |  | 854.4403
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5053 | 42.5763 |  | 5.6311 | 1129.7589 |  | 8.2695 | 2766.3645 |  | 10.1056 | 5388.172 |  | 9.3845 | 9039.6764 |  | 5.6978 | 13193.6539 |  | 4.3069 | 17432.6557 |  | 25.7 | 21483.8644 |  | 50.3322 | 24942.0996 |  | 434.4403 | 29246.5734
[13 empty] | Next iteration flow rate |  |  | 43.4278 | Abs Value of | Flow this | 1141.0565 | Abs Value of | Flow this | 2794.0281 | Abs Value of | Flow this | 5442.0537 | Abs Value of | Flow this | 9130.0732 | Abs Value of | Flow this | 13325.5904 | Abs Value of | Flow this | 17606.9823 | Abs Value of | Flow this | 21698.703 | Abs Value of | Flow this | 25191.5206 | Abs Value of | Flow this | 29539.0391 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1891 |  |  | 89.9837 |  |  | 89.2951 |  |  | 87.5982 |  |  | 84.6234 |  |  | 80.4419 |  |  | 75.3638 |  |  | 70.1925 |  |  | 62.6796
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43505 |  |  | 0.43406 |  |  | 0.43074 |  |  | 0.42255 |  |  | 0.4082 |  |  | 0.38803 |  |  | 0.36354 |  |  | 0.33859 |  |  | 0.30235
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1891 |  |  | 29.9837 |  |  | 29.2951 |  |  | 27.5982 |  |  | 24.6234 |  |  | 20.4419 |  |  | 15.3638 |  |  | 10.1925 |  |  | 2.6796
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33473 |  |  | 0.33321 |  |  | 0.32807 |  |  | 0.31505 |  |  | 0.29098 |  |  | 0.25412 |  |  | 0.20386 |  |  | 0.14521 |  |  | 0.042751
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82571 |  |  | 0.82485 |  |  | 0.82512 |  |  | 0.82685 |  |  | 0.83049 |  |  | 0.84073 |  |  | 0.85714 |  |  | 0.91804 |  |  | 0.96217
[13 empty] | C Non choked w/ reducers | 5 |  | 0.22914 |  |  | 6.0287 |  |  | 14.8791 |  |  | 29.5971 |  |  | 52.182 |  |  | 83.5142 |  |  | 127.1387 |  |  | 194.321 |  |  | 304.9947 |  |  | 943.2763
[13 empty] | C Choked w/ reducers | 5 |  | 0.20519 |  |  | 5.3966 |  |  | 13.3381 |  |  | 26.5198 |  |  | 46.6223 |  |  | 74.1532 |  |  | 110.7742 |  |  | 163.4792 |  |  | 208.1597 |  |  | 458.399
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.22914 |  |  | 6.0287 |  |  | 14.8791 |  |  | 29.5971 |  |  | 52.182 |  |  | 83.5142 |  |  | 127.1387 |  |  | 194.321 |  |  | 304.9947 |  |  | 943.2763
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5009 | 43.4278 |  | 5.5713 | 1141.0565 |  | 8.1209 | 2794.0281 |  | 9.8029 | 5442.0537 |  | 8.818 | 9130.0732 |  | 4.6858 | 13325.5904 |  | 6.1387 | 17606.9823 |  | 29.321 | 21698.703 |  | 58.9947 | 25191.5206 |  | 523.2763 | 29539.0391
[13 empty] | Next iteration flow rate |  |  | 44.2964 | Abs Value of | Flow this | 1152.467 | Abs Value of | Flow this | 2821.9684 | Abs Value of | Flow this | 5496.4742 | Abs Value of | Flow this | 9221.3739 | Abs Value of | Flow this | 13458.8463 | Abs Value of | Flow this | 17783.0521 | Abs Value of | Flow this | 21915.6901 | Abs Value of | Flow this | 25443.4358 | Abs Value of | Flow this | 29834.4295 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1882 |  |  | 89.9787 |  |  | 89.2763 |  |  | 87.5453 |  |  | 84.5107 |  |  | 80.2451 |  |  | 75.065 |  |  | 69.7898 |  |  | 62.1258
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43505 |  |  | 0.43403 |  |  | 0.43065 |  |  | 0.4223 |  |  | 0.40766 |  |  | 0.38708 |  |  | 0.36209 |  |  | 0.33665 |  |  | 0.29968
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1882 |  |  | 29.9787 |  |  | 29.2763 |  |  | 27.5453 |  |  | 24.5107 |  |  | 20.2451 |  |  | 15.065 |  |  | 9.7898 |  |  | 2.1258
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33472 |  |  | 0.33318 |  |  | 0.32793 |  |  | 0.31464 |  |  | 0.29003 |  |  | 0.25229 |  |  | 0.20069 |  |  | 0.14028 |  |  | 0.034218
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82571 |  |  | 0.82487 |  |  | 0.8252 |  |  | 0.82708 |  |  | 0.83104 |  |  | 0.84187 |  |  | 0.85936 |  |  | 0.92082 |  |  | 0.96972
[13 empty] | C Non choked w/ reducers | 5 |  | 0.23373 |  |  | 6.0891 |  |  | 15.0292 |  |  | 29.903 |  |  | 52.7558 |  |  | 84.5433 |  |  | 129.0147 |  |  | 198.082 |  |  | 314.2699 |  |  | 1066.0148
[13 empty] | C Choked w/ reducers | 5 |  | 0.20929 |  |  | 5.4506 |  |  | 13.4722 |  |  | 26.7907 |  |  | 47.117 |  |  | 74.9946 |  |  | 112.1562 |  |  | 165.7712 |  |  | 211.4546 |  |  | 467.1099
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.23373 |  |  | 6.0891 |  |  | 15.0292 |  |  | 29.903 |  |  | 52.7558 |  |  | 84.5433 |  |  | 129.0147 |  |  | 198.082 |  |  | 314.2699 |  |  | 1066.0148
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4963 | 44.2964 |  | 5.5109 | 1152.467 |  | 7.9708 | 2821.9684 |  | 9.497 | 5496.4742 |  | 8.2442 | 9221.3739 |  | 3.6567 | 13458.8463 |  | 8.0147 | 17783.0521 |  | 33.082 | 21915.6901 |  | 68.2699 | 25443.4358 |  | 646.0148 | 29834.4295
[13 empty] | Next iteration flow rate |  |  | 45.1823 | Abs Value of | Flow this | 1163.9917 | Abs Value of | Flow this | 2850.1881 | Abs Value of | Flow this | 5551.439 | Abs Value of | Flow this | 9313.5876 | Abs Value of | Flow this | 13593.4348 | Abs Value of | Flow this | 17960.8826 | Abs Value of | Flow this | 22134.847 | Abs Value of | Flow this | 25697.8702 | Abs Value of | Flow this | 30132.7738 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1874 |  |  | 89.9737 |  |  | 89.2571 |  |  | 87.4913 |  |  | 84.3958 |  |  | 80.0444 |  |  | 74.7601 |  |  | 69.3789 |  |  | 61.5609
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43504 |  |  | 0.43401 |  |  | 0.43055 |  |  | 0.42204 |  |  | 0.4071 |  |  | 0.38611 |  |  | 0.36062 |  |  | 0.33467 |  |  | 0.29695
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1874 |  |  | 29.9737 |  |  | 29.2571 |  |  | 27.4913 |  |  | 24.3958 |  |  | 20.0444 |  |  | 14.7601 |  |  | 9.3789 |  |  | 1.5609
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33472 |  |  | 0.33314 |  |  | 0.32778 |  |  | 0.31422 |  |  | 0.28906 |  |  | 0.25042 |  |  | 0.19743 |  |  | 0.13518 |  |  | 0.025356
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82572 |  |  | 0.82489 |  |  | 0.82527 |  |  | 0.82731 |  |  | 0.8316 |  |  | 0.84305 |  |  | 0.86164 |  |  | 0.92369 |  |  | 0.97756
[13 empty] | C Non choked w/ reducers | 5 |  | 0.2384 |  |  | 6.1501 |  |  | 15.1808 |  |  | 30.2124 |  |  | 53.3371 |  |  | 85.59 |  |  | 130.9369 |  |  | 201.9929 |  |  | 324.2372 |  |  | 1252.1106
[13 empty] | C Choked w/ reducers | 5 |  | 0.21348 |  |  | 5.5052 |  |  | 13.6077 |  |  | 27.0644 |  |  | 47.6175 |  |  | 75.8477 |  |  | 113.5618 |  |  | 168.1116 |  |  | 214.8339 |  |  | 476.1101
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.2384 |  |  | 6.1501 |  |  | 15.1808 |  |  | 30.2124 |  |  | 53.3371 |  |  | 85.59 |  |  | 130.9369 |  |  | 201.9929 |  |  | 324.2372 |  |  | 1252.1106
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4916 | 45.1823 |  | 5.4499 | 1163.9917 |  | 7.8192 | 2850.1881 |  | 9.1876 | 5551.439 |  | 7.6629 | 9313.5876 |  | 2.61 | 13593.4348 |  | 9.9369 | 17960.8826 |  | 36.9929 | 22134.847 |  | 78.2372 | 25697.8702 |  | 832.1106 | 30132.7738
[13 empty] | Next iteration flow rate |  |  | 46.0859 | Abs Value of | Flow this | 1175.6316 | Abs Value of | Flow this | 2878.69 | Abs Value of | Flow this | 5606.9533 | Abs Value of | Flow this | 9406.7235 | Abs Value of | Flow this | 13729.3692 | Abs Value of | Flow this | 18140.4914 | Abs Value of | Flow this | 22356.1955 | Abs Value of | Flow this | 25954.8489 | Abs Value of | Flow this | 30434.1015 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1865 |  |  | 89.9685 |  |  | 89.2375 |  |  | 87.4363 |  |  | 84.2785 |  |  | 79.8397 |  |  | 74.4492 |  |  | 68.9598 |  |  | 60.9847
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43504 |  |  | 0.43399 |  |  | 0.43046 |  |  | 0.42177 |  |  | 0.40654 |  |  | 0.38513 |  |  | 0.35912 |  |  | 0.33264 |  |  | 0.29417
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1865 |  |  | 29.9685 |  |  | 29.2375 |  |  | 27.4363 |  |  | 24.2785 |  |  | 19.8397 |  |  | 14.4492 |  |  | 8.9598 |  |  | 0.98467
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33471 |  |  | 0.3331 |  |  | 0.32764 |  |  | 0.31379 |  |  | 0.28807 |  |  | 0.24849 |  |  | 0.19408 |  |  | 0.12993 |  |  | 0.016146
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82572 |  |  | 0.82491 |  |  | 0.82535 |  |  | 0.82755 |  |  | 0.83218 |  |  | 0.84425 |  |  | 0.86399 |  |  | 0.92666 |  |  | 0.98571
[13 empty] | C Non choked w/ reducers | 5 |  | 0.24317 |  |  | 6.2116 |  |  | 15.334 |  |  | 30.5252 |  |  | 53.926 |  |  | 86.6546 |  |  | 132.9073 |  |  | 206.0647 |  |  | 334.992 |  |  | 1586.5218
[13 empty] | C Choked w/ reducers | 5 |  | 0.21775 |  |  | 5.5603 |  |  | 13.7446 |  |  | 27.341 |  |  | 48.124 |  |  | 76.7128 |  |  | 114.9916 |  |  | 170.5019 |  |  | 218.301 |  |  | 485.415
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.24317 |  |  | 6.2116 |  |  | 15.334 |  |  | 30.5252 |  |  | 53.926 |  |  | 86.6546 |  |  | 132.9073 |  |  | 206.0647 |  |  | 334.992 |  |  | 1586.5218
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4868 | 46.0859 |  | 5.3884 | 1175.6316 |  | 7.666 | 2878.69 |  | 8.8748 | 5606.9533 |  | 7.074 | 9406.7235 |  | 1.5454 | 13729.3692 |  | 11.9073 | 18140.4914 |  | 41.0647 | 22356.1955 |  | 88.992 | 25954.8489 |  | 1166.5218 | 30434.1015
[13 empty] | Next iteration flow rate |  |  | 47.0077 | Abs Value of | Flow this | 1187.3879 | Abs Value of | Flow this | 2907.4769 | Abs Value of | Flow this | 5663.0229 | Abs Value of | Flow this | 9500.7907 | Abs Value of | Flow this | 13866.6628 | Abs Value of | Flow this | 18321.8964 | Abs Value of | Flow this | 22579.7574 | Abs Value of | Flow this | 26214.3974 | Abs Value of | Flow this | 30738.4425 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1857 |  |  | 89.9633 |  |  | 89.2176 |  |  | 87.3801 |  |  | 84.1589 |  |  | 79.6308 |  |  | 74.132 |  |  | 68.5323 |  |  | 60.3968
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43503 |  |  | 0.43396 |  |  | 0.43036 |  |  | 0.4215 |  |  | 0.40596 |  |  | 0.38412 |  |  | 0.35759 |  |  | 0.33058 |  |  | 0.29134
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1857 |  |  | 29.9633 |  |  | 29.2176 |  |  | 27.3801 |  |  | 24.1589 |  |  | 19.6308 |  |  | 14.132 |  |  | 8.5323 |  |  | 0.39683
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33471 |  |  | 0.33306 |  |  | 0.32749 |  |  | 0.31334 |  |  | 0.28706 |  |  | 0.24652 |  |  | 0.19063 |  |  | 0.1245 |  |  | 0.0065705
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82572 |  |  | 0.82493 |  |  | 0.82543 |  |  | 0.82779 |  |  | 0.83277 |  |  | 0.84549 |  |  | 0.86641 |  |  | 0.92973 |  |  | 0.99419
[13 empty] | C Non choked w/ reducers | 5 |  | 0.24803 |  |  | 6.2739 |  |  | 15.4888 |  |  | 30.8414 |  |  | 54.5227 |  |  | 87.7377 |  |  | 134.9279 |  |  | 210.3096 |  |  | 346.6488 |  |  | 2514.7435
[13 empty] | C Choked w/ reducers | 5 |  | 0.2221 |  |  | 5.616 |  |  | 13.8828 |  |  | 27.6206 |  |  | 48.6365 |  |  | 77.5901 |  |  | 116.4461 |  |  | 172.9437 |  |  | 221.8595 |  |  | 495.0409
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.24803 |  |  | 6.2739 |  |  | 15.4888 |  |  | 30.8414 |  |  | 54.5227 |  |  | 87.7377 |  |  | 134.9279 |  |  | 210.3096 |  |  | 346.6488 |  |  | 2514.7435
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.482 | 47.0077 |  | 5.3261 | 1187.3879 |  | 7.5112 | 2907.4769 |  | 8.5586 | 5663.0229 |  | 6.4773 | 9500.7907 |  | 0.46225 | 13866.6628 |  | 13.9279 | 18321.8964 |  | 45.3096 | 22579.7574 |  | 100.6488 | 26214.3974 |  | 2094.7435 | 30738.4425
[13 empty] | Next iteration flow rate |  |  | 47.9478 | Abs Value of | Flow this | 1199.2618 | Abs Value of | Flow this | 2936.5517 | Abs Value of | Flow this | 5719.6531 | Abs Value of | Flow this | 9595.7986 | Abs Value of | Flow this | 14005.3295 | Abs Value of | Flow this | 18505.1153 | Abs Value of | Flow this | 22805.555 | Abs Value of | Flow this | 26476.5413 | Abs Value of | Flow this | 31045.827 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1848 |  |  | 89.9579 |  |  | 89.1972 |  |  | 87.3228 |  |  | 84.0368 |  |  | 79.4178 |  |  | 73.8084 |  |  | 68.0961 |  |  | 59.7972
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43503 |  |  | 0.43393 |  |  | 0.43027 |  |  | 0.42122 |  |  | 0.40537 |  |  | 0.38309 |  |  | 0.35603 |  |  | 0.32848 |  |  | 0.28845
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1848 |  |  | 29.9579 |  |  | 29.1972 |  |  | 27.3228 |  |  | 24.0368 |  |  | 19.4178 |  |  | 13.8084 |  |  | 8.0961 |  |  | -0.20282
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.3347 |  |  | 0.33302 |  |  | 0.32733 |  |  | 0.31289 |  |  | 0.28603 |  |  | 0.2445 |  |  | 0.18708 |  |  | 0.11889 |  |  | -0.0033917
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82573 |  |  | 0.82495 |  |  | 0.82551 |  |  | 0.82804 |  |  | 0.83337 |  |  | 0.84676 |  |  | 0.8689 |  |  | 0.93289 |  |  | 1.003
[13 empty] | C Non choked w/ reducers | 5 |  | 0.25299 |  |  | 6.3367 |  |  | 15.6452 |  |  | 31.1611 |  |  | 55.1272 |  |  | 88.8399 |  |  | 137.0012 |  |  | 214.7413 |  |  | 359.3475 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.22654 |  |  | 5.6722 |  |  | 14.0225 |  |  | 27.9032 |  |  | 49.155 |  |  | 78.4798 |  |  | 117.926 |  |  | 175.4389 |  |  | 225.5132 |  |  | 505.0053
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.25299 |  |  | 6.3367 |  |  | 15.6452 |  |  | 31.1611 |  |  | 55.1272 |  |  | 88.8399 |  |  | 137.0012 |  |  | 214.7413 |  |  | 359.3475 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.477 | 47.9478 |  | 5.2633 | 1199.2618 |  | 7.3548 | 2936.5517 |  | 8.2389 | 5719.6531 |  | 5.8728 | 9595.7986 |  | 0.63993 | 14005.3295 |  | 16.0012 | 18505.1153 |  | 49.7413 | 22805.555 |  | 113.3475 | 26476.5413 |  | 18000 | 31045.827
[13 empty] | Next iteration flow rate |  |  | 48.9068 | Abs Value of | Flow this | 1211.2544 | Abs Value of | Flow this | 2965.9172 | Abs Value of | Flow this | 5776.8496 | Abs Value of | Flow this | 9691.7566 | Abs Value of | Flow this | 14145.3828 | Abs Value of | Flow this | 18690.1665 | Abs Value of | Flow this | 23033.6105 | Abs Value of | Flow this | 26741.3068 | Abs Value of | Flow this | 31356.2852 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1839 |  |  | 89.9524 |  |  | 89.1765 |  |  | 87.2644 |  |  | 83.9124 |  |  | 79.2005 |  |  | 73.4783 |  |  | 67.6512 |  |  | 59.1855
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43502 |  |  | 0.43391 |  |  | 0.43017 |  |  | 0.42094 |  |  | 0.40477 |  |  | 0.38204 |  |  | 0.35444 |  |  | 0.32633 |  |  | 0.2855
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1839 |  |  | 29.9524 |  |  | 29.1765 |  |  | 27.2644 |  |  | 23.9124 |  |  | 19.2005 |  |  | 13.4783 |  |  | 7.6512 |  |  | -0.81452
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33469 |  |  | 0.33298 |  |  | 0.32718 |  |  | 0.31243 |  |  | 0.28497 |  |  | 0.24243 |  |  | 0.18343 |  |  | 0.1131 |  |  | -0.013762
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82573 |  |  | 0.82497 |  |  | 0.8256 |  |  | 0.82829 |  |  | 0.83399 |  |  | 0.84805 |  |  | 0.87146 |  |  | 0.93616 |  |  | 1.0122
[13 empty] | C Non choked w/ reducers | 5 |  | 0.25805 |  |  | 6.4002 |  |  | 15.8031 |  |  | 31.4844 |  |  | 55.7397 |  |  | 89.9617 |  |  | 139.1294 |  |  | 219.3748 |  |  | 373.2608 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.23107 |  |  | 5.729 |  |  | 14.1636 |  |  | 28.1888 |  |  | 49.6798 |  |  | 79.3822 |  |  | 119.4321 |  |  | 177.9893 |  |  | 229.2662 |  |  | 515.3269
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.25805 |  |  | 6.4002 |  |  | 15.8031 |  |  | 31.4844 |  |  | 55.7397 |  |  | 89.9617 |  |  | 139.1294 |  |  | 219.3748 |  |  | 373.2608 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4719 | 48.9068 |  | 5.1998 | 1211.2544 |  | 7.1969 | 2965.9172 |  | 7.9156 | 5776.8496 |  | 5.2603 | 9691.7566 |  | 1.7617 | 14145.3828 |  | 18.1294 | 18690.1665 |  | 54.3748 | 23033.6105 |  | 127.2608 | 26741.3068 |  | 18000 | 31356.2852
[13 empty] | Next iteration flow rate |  |  | 49.8849 | Abs Value of | Flow this | 1223.367 | Abs Value of | Flow this | 2995.5764 | Abs Value of | Flow this | 5834.6181 | Abs Value of | Flow this | 9788.6742 | Abs Value of | Flow this | 14286.8366 | Abs Value of | Flow this | 18877.0681 | Abs Value of | Flow this | 23263.9466 | Abs Value of | Flow this | 27008.7198 | Abs Value of | Flow this | 31669.8481 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1829 |  |  | 89.9468 |  |  | 89.1553 |  |  | 87.2048 |  |  | 83.7854 |  |  | 78.9788 |  |  | 73.1416 |  |  | 67.1974 |  |  | 58.5615
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43502 |  |  | 0.43388 |  |  | 0.43006 |  |  | 0.42065 |  |  | 0.40416 |  |  | 0.38097 |  |  | 0.35282 |  |  | 0.32414 |  |  | 0.28249
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1829 |  |  | 29.9468 |  |  | 29.1553 |  |  | 27.2048 |  |  | 23.7854 |  |  | 18.9788 |  |  | 13.1416 |  |  | 7.1974 |  |  | -1.4385
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33469 |  |  | 0.33294 |  |  | 0.32702 |  |  | 0.31196 |  |  | 0.28388 |  |  | 0.2403 |  |  | 0.17967 |  |  | 0.10711 |  |  | -0.024564
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82573 |  |  | 0.82499 |  |  | 0.82568 |  |  | 0.82855 |  |  | 0.83462 |  |  | 0.84939 |  |  | 0.87409 |  |  | 0.93954 |  |  | 1.0217
[13 empty] | C Non choked w/ reducers | 5 |  | 0.26322 |  |  | 6.4643 |  |  | 15.9627 |  |  | 31.8113 |  |  | 56.3605 |  |  | 91.1036 |  |  | 141.3151 |  |  | 224.2272 |  |  | 388.6044 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.2357 |  |  | 5.7863 |  |  | 14.3061 |  |  | 28.4774 |  |  | 50.2109 |  |  | 80.2975 |  |  | 120.9651 |  |  | 180.5968 |  |  | 233.1228 |  |  | 526.0261
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.26322 |  |  | 6.4643 |  |  | 15.9627 |  |  | 31.8113 |  |  | 56.3605 |  |  | 91.1036 |  |  | 141.3151 |  |  | 224.2272 |  |  | 388.6044 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4668 | 49.8849 |  | 5.1357 | 1223.367 |  | 7.0373 | 2995.5764 |  | 7.5887 | 5834.6181 |  | 4.6395 | 9788.6742 |  | 2.9036 | 14286.8366 |  | 20.3151 | 18877.0681 |  | 59.2272 | 23263.9466 |  | 142.6044 | 27008.7198 |  | 18000 | 31669.8481
[13 empty] | Next iteration flow rate |  |  | 50.8826 | Abs Value of | Flow this | 1235.6006 | Abs Value of | Flow this | 3025.5321 | Abs Value of | Flow this | 5892.9643 | Abs Value of | Flow this | 9886.5609 | Abs Value of | Flow this | 14429.705 | Abs Value of | Flow this | 19065.8388 | Abs Value of | Flow this | 23496.5861 | Abs Value of | Flow this | 27278.807 | Abs Value of | Flow this | 31986.5466 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.182 |  |  | 89.9411 |  |  | 89.1337 |  |  | 87.1439 |  |  | 83.6558 |  |  | 78.7526 |  |  | 72.7982 |  |  | 66.7344 |  |  | 57.9249
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43502 |  |  | 0.43385 |  |  | 0.42996 |  |  | 0.42036 |  |  | 0.40353 |  |  | 0.37988 |  |  | 0.35116 |  |  | 0.32191 |  |  | 0.27942
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.182 |  |  | 29.9411 |  |  | 29.1337 |  |  | 27.1439 |  |  | 23.6558 |  |  | 18.7526 |  |  | 12.7982 |  |  | 6.7344 |  |  | -2.0751
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33468 |  |  | 0.3329 |  |  | 0.32685 |  |  | 0.31148 |  |  | 0.28278 |  |  | 0.23812 |  |  | 0.1758 |  |  | 0.10091 |  |  | -0.035823
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82574 |  |  | 0.82501 |  |  | 0.82577 |  |  | 0.82881 |  |  | 0.83526 |  |  | 0.85075 |  |  | 0.8768 |  |  | 0.94304 |  |  | 1.0317
[13 empty] | C Non choked w/ reducers | 5 |  | 0.26848 |  |  | 6.529 |  |  | 16.124 |  |  | 32.1418 |  |  | 56.9895 |  |  | 92.2662 |  |  | 143.5613 |  |  | 229.3175 |  |  | 405.6525 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.24041 |  |  | 5.8442 |  |  | 14.4501 |  |  | 28.7692 |  |  | 50.7484 |  |  | 81.2261 |  |  | 122.5256 |  |  | 183.2634 |  |  | 237.0874 |  |  | 537.1247
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.26848 |  |  | 6.529 |  |  | 16.124 |  |  | 32.1418 |  |  | 56.9895 |  |  | 92.2662 |  |  | 143.5613 |  |  | 229.3175 |  |  | 405.6525 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4615 | 50.8826 |  | 5.071 | 1235.6006 |  | 6.876 | 3025.5321 |  | 7.2582 | 5892.9643 |  | 4.0105 | 9886.5609 |  | 4.0662 | 14429.705 |  | 22.5613 | 19065.8388 |  | 64.3175 | 23496.5861 |  | 159.6525 | 27278.807 |  | 18000 | 31986.5466
[13 empty] | Next iteration flow rate |  |  | 51.9002 | Abs Value of | Flow this | 1247.9567 | Abs Value of | Flow this | 3055.7874 | Abs Value of | Flow this | 5951.894 | Abs Value of | Flow this | 9985.4265 | Abs Value of | Flow this | 14574.002 | Abs Value of | Flow this | 19256.4972 | Abs Value of | Flow this | 23731.552 | Abs Value of | Flow this | 27551.5951 | Abs Value of | Flow this | 32306.412 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.181 |  |  | 89.9353 |  |  | 89.1116 |  |  | 87.0819 |  |  | 83.5237 |  |  | 78.5219 |  |  | 72.4478 |  |  | 66.2622 |  |  | 57.2756
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43501 |  |  | 0.43383 |  |  | 0.42985 |  |  | 0.42006 |  |  | 0.4029 |  |  | 0.37877 |  |  | 0.34947 |  |  | 0.31963 |  |  | 0.27628
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.181 |  |  | 29.9353 |  |  | 29.1116 |  |  | 27.0819 |  |  | 23.5237 |  |  | 18.5219 |  |  | 12.4478 |  |  | 6.2622 |  |  | -2.7244
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33467 |  |  | 0.33285 |  |  | 0.32669 |  |  | 0.31099 |  |  | 0.28164 |  |  | 0.23588 |  |  | 0.17182 |  |  | 0.094506 |  |  | -0.047566
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82574 |  |  | 0.82504 |  |  | 0.82586 |  |  | 0.82908 |  |  | 0.83593 |  |  | 0.85216 |  |  | 0.8796 |  |  | 0.94666 |  |  | 1.0421
[13 empty] | C Non choked w/ reducers | 5 |  | 0.27385 |  |  | 6.5944 |  |  | 16.2868 |  |  | 32.4761 |  |  | 57.6271 |  |  | 93.4502 |  |  | 145.8707 |  |  | 234.6674 |  |  | 424.7596 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.24522 |  |  | 5.9027 |  |  | 14.5955 |  |  | 29.064 |  |  | 51.2924 |  |  | 82.1681 |  |  | 124.1144 |  |  | 185.9912 |  |  | 241.1649 |  |  | 548.6463
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.27385 |  |  | 6.5944 |  |  | 16.2868 |  |  | 32.4761 |  |  | 57.6271 |  |  | 93.4502 |  |  | 145.8707 |  |  | 234.6674 |  |  | 424.7596 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4562 | 51.9002 |  | 5.0056 | 1247.9567 |  | 6.7132 | 3055.7874 |  | 6.9239 | 5951.894 |  | 3.3729 | 9985.4265 |  | 5.2502 | 14574.002 |  | 24.8707 | 19256.4972 |  | 69.6674 | 23731.552 |  | 178.7596 | 27551.5951 |  | 18000 | 32306.412
[13 empty] | Next iteration flow rate |  |  | 52.9383 | Abs Value of | Flow this | 1260.4362 | Abs Value of | Flow this | 3086.3453 | Abs Value of | Flow this | 6011.4129 | Abs Value of | Flow this | 10085.2808 | Abs Value of | Flow this | 14719.742 | Abs Value of | Flow this | 19449.0622 | Abs Value of | Flow this | 23968.8675 | Abs Value of | Flow this | 27827.111 | Abs Value of | Flow this | 32629.4762 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.18 |  |  | 89.9294 |  |  | 89.0892 |  |  | 87.0186 |  |  | 83.3889 |  |  | 78.2866 |  |  | 72.0903 |  |  | 65.7804 |  |  | 56.6132
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43501 |  |  | 0.4338 |  |  | 0.42974 |  |  | 0.41976 |  |  | 0.40225 |  |  | 0.37763 |  |  | 0.34775 |  |  | 0.31731 |  |  | 0.27309
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.18 |  |  | 29.9294 |  |  | 29.0892 |  |  | 27.0186 |  |  | 23.3889 |  |  | 18.2866 |  |  | 12.0903 |  |  | 5.7804 |  |  | -3.3868
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33466 |  |  | 0.33281 |  |  | 0.32652 |  |  | 0.31049 |  |  | 0.28048 |  |  | 0.23359 |  |  | 0.16771 |  |  | 0.087875 |  |  | -0.059823
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82574 |  |  | 0.82506 |  |  | 0.82595 |  |  | 0.82936 |  |  | 0.8366 |  |  | 0.8536 |  |  | 0.88247 |  |  | 0.9504 |  |  | 1.0529
[13 empty] | C Non choked w/ reducers | 5 |  | 0.27933 |  |  | 6.6605 |  |  | 16.4514 |  |  | 32.814 |  |  | 58.2733 |  |  | 94.6561 |  |  | 148.2466 |  |  | 240.3013 |  |  | 446.3938 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.25012 |  |  | 5.9618 |  |  | 14.7424 |  |  | 29.3621 |  |  | 51.843 |  |  | 83.124 |  |  | 125.7324 |  |  | 188.7825 |  |  | 245.3605 |  |  | 560.6162
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.27933 |  |  | 6.6605 |  |  | 16.4514 |  |  | 32.814 |  |  | 58.2733 |  |  | 94.6561 |  |  | 148.2466 |  |  | 240.3013 |  |  | 446.3938 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4507 | 52.9383 |  | 4.9395 | 1260.4362 |  | 6.5486 | 3086.3453 |  | 6.586 | 6011.4129 |  | 2.7267 | 10085.2808 |  | 6.4561 | 14719.742 |  | 27.2466 | 19449.0622 |  | 75.3013 | 23968.8675 |  | 200.3938 | 27827.111 |  | 18000 | 32629.4762
[13 empty] | Next iteration flow rate |  |  | 53.997 | Abs Value of | Flow this | 1273.0406 | Abs Value of | Flow this | 3117.2088 | Abs Value of | Flow this | 6071.527 | Abs Value of | Flow this | 10186.1336 | Abs Value of | Flow this | 14866.9395 | Abs Value of | Flow this | 19643.5528 | Abs Value of | Flow this | 24208.5562 | Abs Value of | Flow this | 28105.3822 | Abs Value of | Flow this | 32955.7709 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.179 |  |  | 89.9234 |  |  | 89.0662 |  |  | 86.9541 |  |  | 83.2514 |  |  | 78.0465 |  |  | 71.7257 |  |  | 65.289 |  |  | 55.9375
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.435 |  |  | 0.43377 |  |  | 0.42963 |  |  | 0.41944 |  |  | 0.40158 |  |  | 0.37648 |  |  | 0.34599 |  |  | 0.31494 |  |  | 0.26983
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.179 |  |  | 29.9234 |  |  | 29.0662 |  |  | 26.9541 |  |  | 23.2514 |  |  | 18.0465 |  |  | 11.7257 |  |  | 5.289 |  |  | -4.0625
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33466 |  |  | 0.33277 |  |  | 0.32634 |  |  | 0.30998 |  |  | 0.27929 |  |  | 0.23123 |  |  | 0.16348 |  |  | 0.081009 |  |  | -0.072625
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82575 |  |  | 0.82508 |  |  | 0.82604 |  |  | 0.82964 |  |  | 0.83729 |  |  | 0.85508 |  |  | 0.88544 |  |  | 0.95427 |  |  | 1.0643
[13 empty] | C Non choked w/ reducers | 5 |  | 0.28491 |  |  | 6.7272 |  |  | 16.6177 |  |  | 33.1558 |  |  | 58.9283 |  |  | 95.8848 |  |  | 150.6925 |  |  | 246.2471 |  |  | 471.1881 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.25513 |  |  | 6.0215 |  |  | 14.8909 |  |  | 29.6634 |  |  | 52.4003 |  |  | 84.0939 |  |  | 127.3803 |  |  | 191.6396 |  |  | 249.6794 |  |  | 573.0621
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.28491 |  |  | 6.7272 |  |  | 16.6177 |  |  | 33.1558 |  |  | 58.9283 |  |  | 95.8848 |  |  | 150.6925 |  |  | 246.2471 |  |  | 471.1881 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4451 | 53.997 |  | 4.8728 | 1273.0406 |  | 6.3823 | 3117.2088 |  | 6.2442 | 6071.527 |  | 2.0717 | 10186.1336 |  | 7.6848 | 14866.9395 |  | 29.6925 | 19643.5528 |  | 81.2471 | 24208.5562 |  | 225.1881 | 28105.3822 |  | 18000 | 32955.7709
[13 empty] | Next iteration flow rate |  |  | 55.077 | Abs Value of | Flow this | 1285.771 | Abs Value of | Flow this | 3148.3809 | Abs Value of | Flow this | 6132.2423 | Abs Value of | Flow this | 10287.995 | Abs Value of | Flow this | 15015.6088 | Abs Value of | Flow this | 19839.9883 | Abs Value of | Flow this | 24450.6417 | Abs Value of | Flow this | 28386.436 | Abs Value of | Flow this | 33285.3286 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.178 |  |  | 89.9172 |  |  | 89.0428 |  |  | 86.8882 |  |  | 83.1111 |  |  | 77.8016 |  |  | 71.3538 |  |  | 64.7877 |  |  | 55.2482
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.435 |  |  | 0.43374 |  |  | 0.42952 |  |  | 0.41913 |  |  | 0.40091 |  |  | 0.3753 |  |  | 0.34419 |  |  | 0.31252 |  |  | 0.2665
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.178 |  |  | 29.9172 |  |  | 29.0428 |  |  | 26.8882 |  |  | 23.1111 |  |  | 17.8016 |  |  | 11.3538 |  |  | 4.7877 |  |  | -4.7518
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33465 |  |  | 0.33272 |  |  | 0.32617 |  |  | 0.30946 |  |  | 0.27807 |  |  | 0.22881 |  |  | 0.15912 |  |  | 0.073898 |  |  | -0.086008
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82575 |  |  | 0.82511 |  |  | 0.82613 |  |  | 0.82993 |  |  | 0.838 |  |  | 0.85659 |  |  | 0.88849 |  |  | 0.95829 |  |  | 1.0761
[13 empty] | C Non choked w/ reducers | 5 |  | 0.29061 |  |  | 6.7946 |  |  | 16.7857 |  |  | 33.5014 |  |  | 59.5924 |  |  | 97.1368 |  |  | 153.212 |  |  | 252.5369 |  |  | 500.024 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.26023 |  |  | 6.0818 |  |  | 15.0408 |  |  | 29.9679 |  |  | 52.9644 |  |  | 85.0782 |  |  | 129.0591 |  |  | 194.5649 |  |  | 254.1275 |  |  | 586.0138
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.29061 |  |  | 6.7946 |  |  | 16.7857 |  |  | 33.5014 |  |  | 59.5924 |  |  | 97.1368 |  |  | 153.212 |  |  | 252.5369 |  |  | 500.024 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4394 | 55.077 |  | 4.8054 | 1285.771 |  | 6.2143 | 3148.3809 |  | 5.8986 | 6132.2423 |  | 1.4076 | 10287.995 |  | 8.9368 | 15015.6088 |  | 32.212 | 19839.9883 |  | 87.5369 | 24450.6417 |  | 254.024 | 28386.436 |  | 18000 | 33285.3286
[13 empty] | Next iteration flow rate |  |  | 56.1785 | Abs Value of | Flow this | 1298.6287 | Abs Value of | Flow this | 3179.8647 | Abs Value of | Flow this | 6193.5647 | Abs Value of | Flow this | 10390.8749 | Abs Value of | Flow this | 15165.7649 | Abs Value of | Flow this | 20038.3882 | Abs Value of | Flow this | 24695.1481 | Abs Value of | Flow this | 28670.3003 | Abs Value of | Flow this | 33618.1819 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1769 |  |  | 89.9109 |  |  | 89.019 |  |  | 86.8211 |  |  | 82.968 |  |  | 77.5518 |  |  | 70.9744 |  |  | 64.2763 |  |  | 54.5451
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43499 |  |  | 0.43371 |  |  | 0.42941 |  |  | 0.4188 |  |  | 0.40022 |  |  | 0.37409 |  |  | 0.34236 |  |  | 0.31005 |  |  | 0.26311
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1769 |  |  | 29.9109 |  |  | 29.019 |  |  | 26.8211 |  |  | 22.968 |  |  | 17.5518 |  |  | 10.9744 |  |  | 4.2763 |  |  | -5.4549
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33464 |  |  | 0.33267 |  |  | 0.32599 |  |  | 0.30892 |  |  | 0.27683 |  |  | 0.22632 |  |  | 0.15462 |  |  | 0.06653 |  |  | -0.10001
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82576 |  |  | 0.82513 |  |  | 0.82623 |  |  | 0.83022 |  |  | 0.83873 |  |  | 0.85815 |  |  | 0.89164 |  |  | 0.96245 |  |  | 1.0885
[13 empty] | C Non choked w/ reducers | 5 |  | 0.29642 |  |  | 6.8627 |  |  | 16.9554 |  |  | 33.851 |  |  | 60.2656 |  |  | 98.413 |  |  | 155.809 |  |  | 259.2074 |  |  | 534.1725 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.26543 |  |  | 6.1427 |  |  | 15.1923 |  |  | 30.2757 |  |  | 53.5355 |  |  | 86.0771 |  |  | 130.7695 |  |  | 197.561 |  |  | 258.7109 |  |  | 599.5037
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.29642 |  |  | 6.8627 |  |  | 16.9554 |  |  | 33.851 |  |  | 60.2656 |  |  | 98.413 |  |  | 155.809 |  |  | 259.2074 |  |  | 534.1725 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4336 | 56.1785 |  | 4.7373 | 1298.6287 |  | 6.0446 | 3179.8647 |  | 5.549 | 6193.5647 |  | 0.73437 | 10390.8749 |  | 10.213 | 15165.7649 |  | 34.809 | 20038.3882 |  | 94.2074 | 24695.1481 |  | 288.1725 | 28670.3003 |  | 18000 | 33618.1819
[13 empty] | Next iteration flow rate |  |  | 57.3021 | Abs Value of | Flow this | 1311.615 | Abs Value of | Flow this | 3211.6633 | Abs Value of | Flow this | 6255.5004 | Abs Value of | Flow this | 10494.7837 | Abs Value of | Flow this | 15317.4226 | Abs Value of | Flow this | 20238.7721 | Abs Value of | Flow this | 24942.0996 | Abs Value of | Flow this | 28957.0033 | Abs Value of | Flow this | 33954.3637 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1759 |  |  | 89.9045 |  |  | 88.9946 |  |  | 86.7525 |  |  | 82.822 |  |  | 77.297 |  |  | 70.5873 |  |  | 63.7546 |  |  | 53.8278
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43499 |  |  | 0.43368 |  |  | 0.42929 |  |  | 0.41847 |  |  | 0.39951 |  |  | 0.37286 |  |  | 0.3405 |  |  | 0.30754 |  |  | 0.25965
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1759 |  |  | 29.9045 |  |  | 28.9946 |  |  | 26.7525 |  |  | 22.822 |  |  | 17.297 |  |  | 10.5873 |  |  | 3.7546 |  |  | -6.1722
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33463 |  |  | 0.33263 |  |  | 0.3258 |  |  | 0.30838 |  |  | 0.27556 |  |  | 0.22377 |  |  | 0.14999 |  |  | 0.058891 |  |  | -0.11467
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82576 |  |  | 0.82516 |  |  | 0.82633 |  |  | 0.83052 |  |  | 0.83947 |  |  | 0.85975 |  |  | 0.89489 |  |  | 0.96676 |  |  | 1.1015
[13 empty] | C Non choked w/ reducers | 5 |  | 0.30235 |  |  | 6.9314 |  |  | 17.1269 |  |  | 34.2044 |  |  | 60.9482 |  |  | 99.714 |  |  | 158.488 |  |  | 266.3014 |  |  | 575.5489 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.27074 |  |  | 6.2042 |  |  | 15.3453 |  |  | 30.5868 |  |  | 54.1135 |  |  | 87.0911 |  |  | 132.5127 |  |  | 200.6307 |  |  | 263.4361 |  |  | 613.5672
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.30235 |  |  | 6.9314 |  |  | 17.1269 |  |  | 34.2044 |  |  | 60.9482 |  |  | 99.714 |  |  | 158.488 |  |  | 266.3014 |  |  | 575.5489 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4276 | 57.3021 |  | 4.6686 | 1311.615 |  | 5.8731 | 3211.6633 |  | 5.1956 | 6255.5004 |  | 0.05177 | 10494.7837 |  | 11.514 | 15317.4226 |  | 37.488 | 20238.7721 |  | 101.3014 | 24942.0996 |  | 329.5489 | 28957.0033 |  | 18000 | 33954.3637
[13 empty] | Next iteration flow rate |  |  | 58.4481 | Abs Value of | Flow this | 1324.7311 | Abs Value of | Flow this | 3243.7799 | Abs Value of | Flow this | 6318.0554 | Abs Value of | Flow this | 10599.7315 | Abs Value of | Flow this | 15470.5968 | Abs Value of | Flow this | 20441.1598 | Abs Value of | Flow this | 25191.5206 | Abs Value of | Flow this | 29246.5734 | Abs Value of | Flow this | 34293.9074 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1748 |  |  | 89.8979 |  |  | 88.9698 |  |  | 86.6826 |  |  | 82.6731 |  |  | 77.037 |  |  | 70.1925 |  |  | 63.2224 |  |  | 53.0961
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43498 |  |  | 0.43365 |  |  | 0.42917 |  |  | 0.41814 |  |  | 0.39879 |  |  | 0.37161 |  |  | 0.33859 |  |  | 0.30497 |  |  | 0.25612
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1748 |  |  | 29.8979 |  |  | 28.9698 |  |  | 26.6826 |  |  | 22.6731 |  |  | 17.037 |  |  | 10.1925 |  |  | 3.2224 |  |  | -6.9039
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33463 |  |  | 0.33258 |  |  | 0.32561 |  |  | 0.30782 |  |  | 0.27425 |  |  | 0.22115 |  |  | 0.14521 |  |  | 0.05097 |  |  | -0.13003
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82576 |  |  | 0.82518 |  |  | 0.82643 |  |  | 0.83083 |  |  | 0.84023 |  |  | 0.86139 |  |  | 0.89824 |  |  | 0.97123 |  |  | 1.1151
[13 empty] | C Non choked w/ reducers | 5 |  | 0.3084 |  |  | 7.0009 |  |  | 17.3002 |  |  | 34.5619 |  |  | 61.6404 |  |  | 101.0408 |  |  | 161.2534 |  |  | 273.8688 |  |  | 627.2043 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.27616 |  |  | 6.2663 |  |  | 15.4999 |  |  | 30.9013 |  |  | 54.6987 |  |  | 88.1205 |  |  | 134.2894 |  |  | 203.7769 |  |  | 268.31 |  |  | 628.2427
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.3084 |  |  | 7.0009 |  |  | 17.3002 |  |  | 34.5619 |  |  | 61.6404 |  |  | 101.0408 |  |  | 161.2534 |  |  | 273.8688 |  |  | 627.2043 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4216 | 58.4481 |  | 4.5991 | 1324.7311 |  | 5.6998 | 3243.7799 |  | 4.8381 | 6318.0554 |  | 0.64039 | 10599.7315 |  | 12.8408 | 15470.5968 |  | 40.2534 | 20441.1598 |  | 108.8688 | 25191.5206 |  | 381.2043 | 29246.5734 |  | 18000 | 34293.9074
[13 empty] | Next iteration flow rate |  |  | 59.6171 | Abs Value of | Flow this | 1337.9784 | Abs Value of | Flow this | 3276.2177 | Abs Value of | Flow this | 6381.2359 | Abs Value of | Flow this | 10705.7288 | Abs Value of | Flow this | 15625.3028 | Abs Value of | Flow this | 20645.5714 | Abs Value of | Flow this | 25443.4358 | Abs Value of | Flow this | 29539.0391 | Abs Value of | Flow this | 34636.8464 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1737 |  |  | 89.8913 |  |  | 88.9445 |  |  | 86.6113 |  |  | 82.5212 |  |  | 76.7718 |  |  | 69.7898 |  |  | 62.6796 |  |  | 52.3497
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43498 |  |  | 0.43361 |  |  | 0.42905 |  |  | 0.41779 |  |  | 0.39806 |  |  | 0.37033 |  |  | 0.33665 |  |  | 0.30235 |  |  | 0.25252
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1737 |  |  | 29.8913 |  |  | 28.9445 |  |  | 26.6113 |  |  | 22.5212 |  |  | 16.7718 |  |  | 9.7898 |  |  | 2.6796 |  |  | -7.6503
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33462 |  |  | 0.33253 |  |  | 0.32542 |  |  | 0.30725 |  |  | 0.27291 |  |  | 0.21846 |  |  | 0.14028 |  |  | 0.042751 |  |  | -0.14614
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82577 |  |  | 0.82521 |  |  | 0.82653 |  |  | 0.83114 |  |  | 0.84101 |  |  | 0.86308 |  |  | 0.9017 |  |  | 0.97587 |  |  | 1.1293
[13 empty] | C Non choked w/ reducers | 5 |  | 0.31457 |  |  | 7.071 |  |  | 17.4752 |  |  | 34.9234 |  |  | 62.3423 |  |  | 102.3941 |  |  | 164.1105 |  |  | 281.9681 |  |  | 694.3718 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.28168 |  |  | 6.3291 |  |  | 15.656 |  |  | 31.2192 |  |  | 55.2912 |  |  | 89.1655 |  |  | 136.1008 |  |  | 207.0024 |  |  | 273.3401 |  |  | 643.572
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.31457 |  |  | 7.071 |  |  | 17.4752 |  |  | 34.9234 |  |  | 62.3423 |  |  | 102.3941 |  |  | 164.1105 |  |  | 281.9681 |  |  | 694.3718 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4154 | 59.6171 |  | 4.529 | 1337.9784 |  | 5.5248 | 3276.2177 |  | 4.4766 | 6381.2359 |  | 1.3423 | 10705.7288 |  | 14.1941 | 15625.3028 |  | 43.1105 | 20645.5714 |  | 116.9681 | 25443.4358 |  | 448.3718 | 29539.0391 |  | 18000 | 34636.8464
[13 empty] | Next iteration flow rate |  |  | 60.8094 | Abs Value of | Flow this | 1351.3582 | Abs Value of | Flow this | 3308.9799 | Abs Value of | Flow this | 6445.0483 | Abs Value of | Flow this | 10812.7861 | Abs Value of | Flow this | 15781.5558 | Abs Value of | Flow this | 20852.0271 | Abs Value of | Flow this | 25697.8702 | Abs Value of | Flow this | 29834.4295 | Abs Value of | Flow this | 34983.2149 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1725 |  |  | 89.8845 |  |  | 88.9186 |  |  | 86.5386 |  |  | 82.3663 |  |  | 76.5013 |  |  | 69.3789 |  |  | 62.1258 |  |  | 51.5884
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43497 |  |  | 0.43358 |  |  | 0.42892 |  |  | 0.41744 |  |  | 0.39731 |  |  | 0.36902 |  |  | 0.33467 |  |  | 0.29968 |  |  | 0.24885
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1725 |  |  | 29.8845 |  |  | 28.9186 |  |  | 26.5386 |  |  | 22.3663 |  |  | 16.5013 |  |  | 9.3789 |  |  | 2.1258 |  |  | -8.4116
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33461 |  |  | 0.33248 |  |  | 0.32523 |  |  | 0.30667 |  |  | 0.27155 |  |  | 0.2157 |  |  | 0.13518 |  |  | 0.034218 |  |  | -0.16305
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82577 |  |  | 0.82523 |  |  | 0.82664 |  |  | 0.83146 |  |  | 0.84181 |  |  | 0.86481 |  |  | 0.90527 |  |  | 0.98069 |  |  | 1.1443
[13 empty] | C Non choked w/ reducers | 5 |  | 0.32086 |  |  | 7.1419 |  |  | 17.6521 |  |  | 35.2891 |  |  | 63.0542 |  |  | 103.7749 |  |  | 167.0646 |  |  | 290.6688 |  |  | 786.9969 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.28731 |  |  | 6.3924 |  |  | 15.8138 |  |  | 31.5405 |  |  | 55.8911 |  |  | 90.2266 |  |  | 137.9479 |  |  | 210.3105 |  |  | 278.5344 |  |  | 659.6013
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.32086 |  |  | 7.1419 |  |  | 17.6521 |  |  | 35.2891 |  |  | 63.0542 |  |  | 103.7749 |  |  | 167.0646 |  |  | 290.6688 |  |  | 786.9969 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4091 | 60.8094 |  | 4.4581 | 1351.3582 |  | 5.3479 | 3308.9799 |  | 4.1109 | 6445.0483 |  | 2.0542 | 10812.7861 |  | 15.5749 | 15781.5558 |  | 46.0646 | 20852.0271 |  | 125.6688 | 25697.8702 |  | 540.9969 | 29834.4295 |  | 18000 | 34983.2149
[13 empty] | Next iteration flow rate |  |  | 62.0256 | Abs Value of | Flow this | 1364.8718 | Abs Value of | Flow this | 3342.0697 | Abs Value of | Flow this | 6509.4988 | Abs Value of | Flow this | 10920.914 | Abs Value of | Flow this | 15939.3714 | Abs Value of | Flow this | 21060.5474 | Abs Value of | Flow this | 25954.8489 | Abs Value of | Flow this | 30132.7738 | Abs Value of | Flow this | 35333.0471 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1714 |  |  | 89.8775 |  |  | 88.8922 |  |  | 86.4644 |  |  | 82.2082 |  |  | 76.2254 |  |  | 68.9598 |  |  | 61.5609 |  |  | 50.8117
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43496 |  |  | 0.43355 |  |  | 0.42879 |  |  | 0.41708 |  |  | 0.39655 |  |  | 0.36769 |  |  | 0.33264 |  |  | 0.29695 |  |  | 0.2451
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1714 |  |  | 29.8775 |  |  | 28.8922 |  |  | 26.4644 |  |  | 22.2082 |  |  | 16.2254 |  |  | 8.9598 |  |  | 1.5609 |  |  | -9.1883
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.3346 |  |  | 0.33242 |  |  | 0.32503 |  |  | 0.30607 |  |  | 0.27015 |  |  | 0.21286 |  |  | 0.12993 |  |  | 0.025356 |  |  | -0.18083
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82578 |  |  | 0.82526 |  |  | 0.82674 |  |  | 0.83179 |  |  | 0.84262 |  |  | 0.86659 |  |  | 0.90895 |  |  | 0.98569 |  |  | 1.16
[13 empty] | C Non choked w/ reducers | 5 |  | 0.32728 |  |  | 7.2134 |  |  | 17.8308 |  |  | 35.6589 |  |  | 63.7762 |  |  | 105.1841 |  |  | 170.1217 |  |  | 300.0538 |  |  | 927.1305 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.29306 |  |  | 6.4564 |  |  | 15.9732 |  |  | 31.8654 |  |  | 56.4984 |  |  | 91.3041 |  |  | 139.8318 |  |  | 213.7046 |  |  | 283.9012 |  |  | 676.3807
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.32728 |  |  | 7.2134 |  |  | 17.8308 |  |  | 35.6589 |  |  | 63.7762 |  |  | 105.1841 |  |  | 170.1217 |  |  | 300.0538 |  |  | 927.1305 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.4027 | 62.0256 |  | 4.3866 | 1364.8718 |  | 5.1692 | 3342.0697 |  | 3.7411 | 6509.4988 |  | 2.7762 | 10920.914 |  | 16.9841 | 15939.3714 |  | 49.1217 | 21060.5474 |  | 135.0538 | 25954.8489 |  | 681.1305 | 30132.7738 |  | 18000 | 35333.0471
[13 empty] | Next iteration flow rate |  |  | 63.2661 | Abs Value of | Flow this | 1378.5205 | Abs Value of | Flow this | 3375.4904 | Abs Value of | Flow this | 6574.5937 | Abs Value of | Flow this | 11030.1231 | Abs Value of | Flow this | 16098.7651 | Abs Value of | Flow this | 21271.1529 | Abs Value of | Flow this | 26214.3974 | Abs Value of | Flow this | 30434.1015 | Abs Value of | Flow this | 35686.3775 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2301 |  |  | 90.1702 |  |  | 89.8704 |  |  | 88.8654 |  |  | 86.3887 |  |  | 82.047 |  |  | 75.9439 |  |  | 68.5323 |  |  | 60.9847 |  |  | 50.0193
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43496 |  |  | 0.43351 |  |  | 0.42866 |  |  | 0.41672 |  |  | 0.39577 |  |  | 0.36633 |  |  | 0.33058 |  |  | 0.29417 |  |  | 0.24128
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2301 |  |  | 30.1702 |  |  | 29.8704 |  |  | 28.8654 |  |  | 26.3887 |  |  | 22.047 |  |  | 15.9439 |  |  | 8.5323 |  |  | 0.98467 |  |  | -9.9807
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33459 |  |  | 0.33237 |  |  | 0.32482 |  |  | 0.30546 |  |  | 0.26871 |  |  | 0.20994 |  |  | 0.1245 |  |  | 0.016146 |  |  | -0.19954
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82578 |  |  | 0.82529 |  |  | 0.82685 |  |  | 0.83212 |  |  | 0.84346 |  |  | 0.86842 |  |  | 0.91275 |  |  | 0.99089 |  |  | 1.1766
[13 empty] | C Non choked w/ reducers | 5 |  | 0.33382 |  |  | 7.2857 |  |  | 18.0113 |  |  | 36.033 |  |  | 64.5086 |  |  | 106.6227 |  |  | 173.2884 |  |  | 310.2232 |  |  | 1178.3258 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.29892 |  |  | 6.5211 |  |  | 16.1342 |  |  | 32.1938 |  |  | 57.1134 |  |  | 92.3983 |  |  | 141.7536 |  |  | 217.1881 |  |  | 289.4496 |  |  | 693.9656
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.33382 |  |  | 7.2857 |  |  | 18.0113 |  |  | 36.033 |  |  | 64.5086 |  |  | 106.6227 |  |  | 173.2884 |  |  | 310.2232 |  |  | 1178.3258 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3962 | 63.2661 |  | 4.3143 | 1378.5205 |  | 4.9887 | 3375.4904 |  | 3.367 | 6574.5937 |  | 3.5086 | 11030.1231 |  | 18.4227 | 16098.7651 |  | 52.2884 | 21271.1529 |  | 145.2232 | 26214.3974 |  | 932.3258 | 30434.1015 |  | 18000 | 35686.3775
[13 empty] | Next iteration flow rate |  |  | 64.5314 | Abs Value of | Flow this | 1392.3057 | Abs Value of | Flow this | 3409.2453 | Abs Value of | Flow this | 6640.3397 | Abs Value of | Flow this | 11140.4243 | Abs Value of | Flow this | 16259.7527 | Abs Value of | Flow this | 21483.8644 | Abs Value of | Flow this | 26476.5413 | Abs Value of | Flow this | 30738.4425 | Abs Value of | Flow this | 36043.2413 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.169 |  |  | 89.8632 |  |  | 88.8379 |  |  | 86.3115 |  |  | 81.8825 |  |  | 75.6567 |  |  | 68.0961 |  |  | 60.3968 |  |  | 49.2111
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43495 |  |  | 0.43348 |  |  | 0.42853 |  |  | 0.41635 |  |  | 0.39498 |  |  | 0.36495 |  |  | 0.32848 |  |  | 0.29134 |  |  | 0.23738
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.169 |  |  | 29.8632 |  |  | 28.8379 |  |  | 26.3115 |  |  | 21.8825 |  |  | 15.6567 |  |  | 8.0961 |  |  | 0.39683 |  |  | -10.7889
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33458 |  |  | 0.33232 |  |  | 0.32461 |  |  | 0.30484 |  |  | 0.26724 |  |  | 0.20694 |  |  | 0.11889 |  |  | 0.0065705 |  |  | -0.21924
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82579 |  |  | 0.82532 |  |  | 0.82696 |  |  | 0.83246 |  |  | 0.84431 |  |  | 0.8703 |  |  | 0.91668 |  |  | 0.99629 |  |  | 1.194
[13 empty] | C Non choked w/ reducers | 5 |  | 0.3405 |  |  | 7.3587 |  |  | 18.1938 |  |  | 36.4114 |  |  | 65.2516 |  |  | 108.0918 |  |  | 176.5717 |  |  | 321.2992 |  |  | 1873.5613 |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.3049 |  |  | 6.5864 |  |  | 16.2968 |  |  | 32.5257 |  |  | 57.7361 |  |  | 93.5098 |  |  | 143.7145 |  |  | 220.7649 |  |  | 295.1895 |  |  | 712.4168
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.3405 |  |  | 7.3587 |  |  | 18.1938 |  |  | 36.4114 |  |  | 65.2516 |  |  | 108.0918 |  |  | 176.5717 |  |  | 321.2992 |  |  | 1873.5613 |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3895 | 64.5314 |  | 4.2413 | 1392.3057 |  | 4.8062 | 3409.2453 |  | 2.9886 | 6640.3397 |  | 4.2516 | 11140.4243 |  | 19.8918 | 16259.7527 |  | 55.5717 | 21483.8644 |  | 156.2992 | 26476.5413 |  | 1627.5613 | 30738.4425 |  | 18000 | 36043.2413
[13 empty] | Next iteration flow rate |  |  | 65.8221 | Abs Value of | Flow this | 1406.2288 | Abs Value of | Flow this | 3443.3378 | Abs Value of | Flow this | 6706.7431 | Abs Value of | Flow this | 11251.8286 | Abs Value of | Flow this | 16422.3503 | Abs Value of | Flow this | 21698.703 | Abs Value of | Flow this | 26741.3068 | Abs Value of | Flow this | 31045.827 | Abs Value of | Flow this | 36403.6737 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1677 |  |  | 89.8558 |  |  | 88.8099 |  |  | 86.2327 |  |  | 81.7147 |  |  | 75.3638 |  |  | 67.6512 |  |  | 59.7972 |  |  | 48.3866
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43495 |  |  | 0.43344 |  |  | 0.4284 |  |  | 0.41597 |  |  | 0.39417 |  |  | 0.36354 |  |  | 0.32633 |  |  | 0.28845 |  |  | 0.2334
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1677 |  |  | 29.8558 |  |  | 28.8099 |  |  | 26.2327 |  |  | 21.7147 |  |  | 15.3638 |  |  | 7.6512 |  |  | -0.20282 |  |  | -11.6134
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33457 |  |  | 0.33226 |  |  | 0.3244 |  |  | 0.30421 |  |  | 0.26574 |  |  | 0.20386 |  |  | 0.1131 |  |  | -0.0033917 |  |  | -0.24001
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82579 |  |  | 0.82535 |  |  | 0.82708 |  |  | 0.83281 |  |  | 0.84519 |  |  | 0.87223 |  |  | 0.92074 |  |  | 1.0019 |  |  | 1.2124
[13 empty] | C Non choked w/ reducers | 5 |  | 0.34731 |  |  | 7.4325 |  |  | 18.3781 |  |  | 36.7941 |  |  | 66.0055 |  |  | 109.5923 |  |  | 179.9795 |  |  | 333.4324 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.311 |  |  | 6.6523 |  |  | 16.4611 |  |  | 32.8614 |  |  | 58.3668 |  |  | 94.6388 |  |  | 145.7158 |  |  | 224.4389 |  |  | 301.1311 |  |  | 731.8016
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.34731 |  |  | 7.4325 |  |  | 18.3781 |  |  | 36.7941 |  |  | 66.0055 |  |  | 109.5923 |  |  | 179.9795 |  |  | 333.4324 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3827 | 65.8221 |  | 4.1675 | 1406.2288 |  | 4.6219 | 3443.3378 |  | 2.6059 | 6706.7431 |  | 5.0055 | 11251.8286 |  | 21.3923 | 16422.3503 |  | 58.9795 | 21698.703 |  | 168.4324 | 26741.3068 |  | 18000 | 31045.827 |  | 18000 | 36403.6737
[13 empty] | Next iteration flow rate |  |  | 67.1385 | Abs Value of | Flow this | 1420.2911 | Abs Value of | Flow this | 3477.7712 | Abs Value of | Flow this | 6773.8105 | Abs Value of | Flow this | 11364.3469 | Abs Value of | Flow this | 16586.5738 | Abs Value of | Flow this | 21915.6901 | Abs Value of | Flow this | 27008.7198 | Abs Value of | Flow this | 31356.2852 | Abs Value of | Flow this | 36767.7105 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1665 |  |  | 89.8483 |  |  | 88.7814 |  |  | 86.1524 |  |  | 81.5435 |  |  | 75.065 |  |  | 67.1974 |  |  | 59.1855 |  |  | 47.5456
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43494 |  |  | 0.43341 |  |  | 0.42826 |  |  | 0.41558 |  |  | 0.39335 |  |  | 0.36209 |  |  | 0.32414 |  |  | 0.2855 |  |  | 0.22935
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1665 |  |  | 29.8483 |  |  | 28.7814 |  |  | 26.1524 |  |  | 21.5435 |  |  | 15.065 |  |  | 7.1974 |  |  | -0.81452 |  |  | -12.4544
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33456 |  |  | 0.33221 |  |  | 0.32418 |  |  | 0.30356 |  |  | 0.2642 |  |  | 0.20069 |  |  | 0.10711 |  |  | -0.013762 |  |  | -0.26195
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.8258 |  |  | 0.82538 |  |  | 0.82719 |  |  | 0.83317 |  |  | 0.84609 |  |  | 0.87421 |  |  | 0.92494 |  |  | 1.0078 |  |  | 1.2318
[13 empty] | C Non choked w/ reducers | 5 |  | 0.35425 |  |  | 7.507 |  |  | 18.5643 |  |  | 37.1812 |  |  | 66.7704 |  |  | 111.1256 |  |  | 183.5203 |  |  | 346.8114 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.31722 |  |  | 6.719 |  |  | 16.6271 |  |  | 33.2006 |  |  | 59.0054 |  |  | 95.7858 |  |  | 147.7589 |  |  | 228.2143 |  |  | 307.2859 |  |  | 752.1943
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.35425 |  |  | 7.507 |  |  | 18.5643 |  |  | 37.1812 |  |  | 66.7704 |  |  | 111.1256 |  |  | 183.5203 |  |  | 346.8114 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3757 | 67.1385 |  | 4.093 | 1420.2911 |  | 4.4357 | 3477.7712 |  | 2.2188 | 6773.8105 |  | 5.7704 | 11364.3469 |  | 22.9256 | 16586.5738 |  | 62.5203 | 21915.6901 |  | 181.8114 | 27008.7198 |  | 18000 | 31356.2852 |  | 18000 | 36767.7105
[13 empty] | Next iteration flow rate |  |  | 68.4813 | Abs Value of | Flow this | 1434.494 | Abs Value of | Flow this | 3512.5489 | Abs Value of | Flow this | 6841.5486 | Abs Value of | Flow this | 11477.9903 | Abs Value of | Flow this | 16752.4395 | Abs Value of | Flow this | 22134.847 | Abs Value of | Flow this | 27278.807 | Abs Value of | Flow this | 31669.8481 | Abs Value of | Flow this | 37135.3876 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1652 |  |  | 89.8406 |  |  | 88.7523 |  |  | 86.0704 |  |  | 81.3689 |  |  | 74.7601 |  |  | 66.7344 |  |  | 58.5615 |  |  | 46.6876
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43493 |  |  | 0.43337 |  |  | 0.42812 |  |  | 0.41518 |  |  | 0.3925 |  |  | 0.36062 |  |  | 0.32191 |  |  | 0.28249 |  |  | 0.22521
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1652 |  |  | 29.8406 |  |  | 28.7523 |  |  | 26.0704 |  |  | 21.3689 |  |  | 14.7601 |  |  | 6.7344 |  |  | -1.4385 |  |  | -13.3124
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33455 |  |  | 0.33215 |  |  | 0.32396 |  |  | 0.3029 |  |  | 0.26262 |  |  | 0.19743 |  |  | 0.10091 |  |  | -0.024564 |  |  | -0.28514
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.8258 |  |  | 0.82541 |  |  | 0.82731 |  |  | 0.83353 |  |  | 0.84701 |  |  | 0.87626 |  |  | 0.92928 |  |  | 1.0139 |  |  | 1.2523
[13 empty] | C Non choked w/ reducers | 5 |  | 0.36134 |  |  | 7.5822 |  |  | 18.7525 |  |  | 37.5728 |  |  | 67.5466 |  |  | 112.6928 |  |  | 187.2036 |  |  | 361.6759 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.32356 |  |  | 6.7862 |  |  | 16.7948 |  |  | 33.5437 |  |  | 59.6522 |  |  | 96.9513 |  |  | 149.8449 |  |  | 232.0954 |  |  | 313.6657 |  |  | 773.6772
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.36134 |  |  | 7.5822 |  |  | 18.7525 |  |  | 37.5728 |  |  | 67.5466 |  |  | 112.6928 |  |  | 187.2036 |  |  | 361.6759 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3687 | 68.4813 |  | 4.0178 | 1434.494 |  | 4.2475 | 3512.5489 |  | 1.8272 | 6841.5486 |  | 6.5466 | 11477.9903 |  | 24.4928 | 16752.4395 |  | 66.2036 | 22134.847 |  | 196.6759 | 27278.807 |  | 18000 | 31669.8481 |  | 18000 | 37135.3876
[13 empty] | Next iteration flow rate |  |  | 69.8509 | Abs Value of | Flow this | 1448.8389 | Abs Value of | Flow this | 3547.6744 | Abs Value of | Flow this | 6909.9641 | Abs Value of | Flow this | 11592.7702 | Abs Value of | Flow this | 16919.9639 | Abs Value of | Flow this | 22356.1955 | Abs Value of | Flow this | 27551.5951 | Abs Value of | Flow this | 31986.5466 | Abs Value of | Flow this | 37506.7414 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1639 |  |  | 89.8328 |  |  | 88.7226 |  |  | 85.9868 |  |  | 81.1908 |  |  | 74.4492 |  |  | 66.2622 |  |  | 57.9249 |  |  | 45.8124
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43493 |  |  | 0.43333 |  |  | 0.42798 |  |  | 0.41478 |  |  | 0.39164 |  |  | 0.35912 |  |  | 0.31963 |  |  | 0.27942 |  |  | 0.22099
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1639 |  |  | 29.8328 |  |  | 28.7226 |  |  | 25.9868 |  |  | 21.1908 |  |  | 14.4492 |  |  | 6.2622 |  |  | -2.0751 |  |  | -14.1876
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33455 |  |  | 0.33209 |  |  | 0.32373 |  |  | 0.30222 |  |  | 0.261 |  |  | 0.19408 |  |  | 0.094506 |  |  | -0.035823 |  |  | -0.30969
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82581 |  |  | 0.82544 |  |  | 0.82743 |  |  | 0.8339 |  |  | 0.84795 |  |  | 0.87836 |  |  | 0.93377 |  |  | 1.0202 |  |  | 1.274
[13 empty] | C Non choked w/ reducers | 5 |  | 0.36857 |  |  | 7.6582 |  |  | 18.9426 |  |  | 37.969 |  |  | 68.3344 |  |  | 114.2952 |  |  | 191.0399 |  |  | 378.336 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.33003 |  |  | 6.8542 |  |  | 16.9643 |  |  | 33.8904 |  |  | 60.3073 |  |  | 98.1356 |  |  | 151.9755 |  |  | 236.0871 |  |  | 320.2838 |  |  | 796.3423
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.36857 |  |  | 7.6582 |  |  | 18.9426 |  |  | 37.969 |  |  | 68.3344 |  |  | 114.2952 |  |  | 191.0399 |  |  | 378.336 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3614 | 69.8509 |  | 3.9418 | 1448.8389 |  | 4.0574 | 3547.6744 |  | 1.431 | 6909.9641 |  | 7.3344 | 11592.7702 |  | 26.0952 | 16919.9639 |  | 70.0399 | 22356.1955 |  | 213.336 | 27551.5951 |  | 18000 | 31986.5466 |  | 18000 | 37506.7414
[13 empty] | Next iteration flow rate |  |  | 71.2479 | Abs Value of | Flow this | 1463.3273 | Abs Value of | Flow this | 3583.1511 | Abs Value of | Flow this | 6979.0637 | Abs Value of | Flow this | 11708.6979 | Abs Value of | Flow this | 17089.1635 | Abs Value of | Flow this | 22579.7574 | Abs Value of | Flow this | 27827.111 | Abs Value of | Flow this | 32306.412 | Abs Value of | Flow this | 37881.8088 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1626 |  |  | 89.8248 |  |  | 88.6923 |  |  | 85.9015 |  |  | 81.0091 |  |  | 74.132 |  |  | 65.7804 |  |  | 57.2756 |  |  | 44.9196
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43492 |  |  | 0.43329 |  |  | 0.42783 |  |  | 0.41437 |  |  | 0.39077 |  |  | 0.35759 |  |  | 0.31731 |  |  | 0.27628 |  |  | 0.21668
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1626 |  |  | 29.8248 |  |  | 28.6923 |  |  | 25.9015 |  |  | 21.0091 |  |  | 14.132 |  |  | 5.7804 |  |  | -2.7244 |  |  | -15.0804
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33454 |  |  | 0.33203 |  |  | 0.3235 |  |  | 0.30153 |  |  | 0.25934 |  |  | 0.19063 |  |  | 0.087875 |  |  | -0.047566 |  |  | -0.33572
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82581 |  |  | 0.82547 |  |  | 0.82755 |  |  | 0.83428 |  |  | 0.84892 |  |  | 0.88052 |  |  | 0.93842 |  |  | 1.0268 |  |  | 1.2971
[13 empty] | C Non choked w/ reducers | 5 |  | 0.37594 |  |  | 7.735 |  |  | 19.1347 |  |  | 38.3698 |  |  | 69.1341 |  |  | 115.9342 |  |  | 195.0407 |  |  | 397.2011 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.33663 |  |  | 6.9228 |  |  | 17.1354 |  |  | 34.241 |  |  | 60.9709 |  |  | 99.3393 |  |  | 154.152 |  |  | 240.1943 |  |  | 327.154 |  |  | 820.2916
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.37594 |  |  | 7.735 |  |  | 19.1347 |  |  | 38.3698 |  |  | 69.1341 |  |  | 115.9342 |  |  | 195.0407 |  |  | 397.2011 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3541 | 71.2479 |  | 3.865 | 1463.3273 |  | 3.8653 | 3583.1511 |  | 1.0302 | 6979.0637 |  | 8.1341 | 11708.6979 |  | 27.7342 | 17089.1635 |  | 74.0407 | 22579.7574 |  | 232.2011 | 27827.111 |  | 18000 | 32306.412 |  | 18000 | 37881.8088
[13 empty] | Next iteration flow rate |  |  | 72.6729 | Abs Value of | Flow this | 1477.9606 | Abs Value of | Flow this | 3618.9826 | Abs Value of | Flow this | 7048.8544 | Abs Value of | Flow this | 11825.7849 | Abs Value of | Flow this | 17260.0552 | Abs Value of | Flow this | 22805.555 | Abs Value of | Flow this | 28105.3822 | Abs Value of | Flow this | 32629.4762 | Abs Value of | Flow this | 38260.6269 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1612 |  |  | 89.8166 |  |  | 88.6614 |  |  | 85.8145 |  |  | 80.8238 |  |  | 73.8084 |  |  | 65.289 |  |  | 56.6132 |  |  | 44.0089
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43492 |  |  | 0.43325 |  |  | 0.42768 |  |  | 0.41395 |  |  | 0.38987 |  |  | 0.35603 |  |  | 0.31494 |  |  | 0.27309 |  |  | 0.21229
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1612 |  |  | 29.8166 |  |  | 28.6614 |  |  | 25.8145 |  |  | 20.8238 |  |  | 13.8084 |  |  | 5.289 |  |  | -3.3868 |  |  | -15.9911
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33453 |  |  | 0.33197 |  |  | 0.32327 |  |  | 0.30082 |  |  | 0.25764 |  |  | 0.18708 |  |  | 0.081009 |  |  | -0.059823 |  |  | -0.36336
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82582 |  |  | 0.8255 |  |  | 0.82768 |  |  | 0.83467 |  |  | 0.8499 |  |  | 0.88274 |  |  | 0.94323 |  |  | 1.0338 |  |  | 1.3215
[13 empty] | C Non choked w/ reducers | 5 |  | 0.38346 |  |  | 7.8125 |  |  | 19.3289 |  |  | 38.7752 |  |  | 69.9458 |  |  | 117.6111 |  |  | 199.219 |  |  | 418.8253 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.34337 |  |  | 6.9922 |  |  | 17.3084 |  |  | 34.5955 |  |  | 61.643 |  |  | 100.5627 |  |  | 156.3761 |  |  | 244.4223 |  |  | 334.2916 |  |  | 845.6398
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.38346 |  |  | 7.8125 |  |  | 19.3289 |  |  | 38.7752 |  |  | 69.9458 |  |  | 117.6111 |  |  | 199.219 |  |  | 418.8253 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3465 | 72.6729 |  | 3.7875 | 1477.9606 |  | 3.6711 | 3618.9826 |  | 0.62476 | 7048.8544 |  | 8.9458 | 11825.7849 |  | 29.4111 | 17260.0552 |  | 78.219 | 22805.555 |  | 253.8253 | 28105.3822 |  | 18000 | 32629.4762 |  | 18000 | 38260.6269
[13 empty] | Next iteration flow rate |  |  | 74.1263 | Abs Value of | Flow this | 1492.7402 | Abs Value of | Flow this | 3655.1724 | Abs Value of | Flow this | 7119.3429 | Abs Value of | Flow this | 11944.0428 | Abs Value of | Flow this | 17432.6557 | Abs Value of | Flow this | 23033.6105 | Abs Value of | Flow this | 28386.436 | Abs Value of | Flow this | 32955.7709 | Abs Value of | Flow this | 38643.2332 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1598 |  |  | 89.8083 |  |  | 88.6298 |  |  | 85.7257 |  |  | 80.6347 |  |  | 73.4783 |  |  | 64.7877 |  |  | 55.9375 |  |  | 43.0798
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43491 |  |  | 0.43321 |  |  | 0.42753 |  |  | 0.41352 |  |  | 0.38896 |  |  | 0.35444 |  |  | 0.31252 |  |  | 0.26983 |  |  | 0.20781
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1598 |  |  | 29.8083 |  |  | 28.6298 |  |  | 25.7257 |  |  | 20.6347 |  |  | 13.4783 |  |  | 4.7877 |  |  | -4.0625 |  |  | -16.9202
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33452 |  |  | 0.33191 |  |  | 0.32303 |  |  | 0.30009 |  |  | 0.2559 |  |  | 0.18343 |  |  | 0.073898 |  |  | -0.072625 |  |  | -0.39276
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82582 |  |  | 0.82553 |  |  | 0.82781 |  |  | 0.83507 |  |  | 0.85092 |  |  | 0.88503 |  |  | 0.94821 |  |  | 1.041 |  |  | 1.3476
[13 empty] | C Non choked w/ reducers | 5 |  | 0.39112 |  |  | 7.8908 |  |  | 19.525 |  |  | 39.1854 |  |  | 70.7699 |  |  | 119.3277 |  |  | 203.5891 |  |  | 443.9805 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.35023 |  |  | 7.0622 |  |  | 17.4831 |  |  | 34.9539 |  |  | 62.3239 |  |  | 101.8065 |  |  | 158.6494 |  |  | 248.7768 |  |  | 341.713 |  |  | 872.5155
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.39112 |  |  | 7.8908 |  |  | 19.525 |  |  | 39.1854 |  |  | 70.7699 |  |  | 119.3277 |  |  | 203.5891 |  |  | 443.9805 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3389 | 74.1263 |  | 3.7092 | 1492.7402 |  | 3.475 | 3655.1724 |  | 0.21456 | 7119.3429 |  | 9.7699 | 11944.0428 |  | 31.1277 | 17432.6557 |  | 82.5891 | 23033.6105 |  | 278.9805 | 28386.436 |  | 18000 | 32955.7709 |  | 18000 | 38643.2332
[13 empty] | Next iteration flow rate |  |  | 75.6089 | Abs Value of | Flow this | 1507.6676 | Abs Value of | Flow this | 3691.7242 | Abs Value of | Flow this | 7190.5364 | Abs Value of | Flow this | 12063.4832 | Abs Value of | Flow this | 17606.9823 | Abs Value of | Flow this | 23263.9466 | Abs Value of | Flow this | 28670.3003 | Abs Value of | Flow this | 33285.3286 | Abs Value of | Flow this | 39029.6655 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1584 |  |  | 89.7999 |  |  | 88.5977 |  |  | 85.6352 |  |  | 80.4419 |  |  | 73.1416 |  |  | 64.2763 |  |  | 55.2482 |  |  | 42.1321
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.4349 |  |  | 0.43317 |  |  | 0.42737 |  |  | 0.41308 |  |  | 0.38803 |  |  | 0.35282 |  |  | 0.31005 |  |  | 0.2665 |  |  | 0.20323
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1584 |  |  | 29.7999 |  |  | 28.5977 |  |  | 25.6352 |  |  | 20.4419 |  |  | 13.1416 |  |  | 4.2763 |  |  | -4.7518 |  |  | -17.8679
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.3345 |  |  | 0.33185 |  |  | 0.32278 |  |  | 0.29935 |  |  | 0.25412 |  |  | 0.17967 |  |  | 0.06653 |  |  | -0.086008 |  |  | -0.42409
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82583 |  |  | 0.82557 |  |  | 0.82794 |  |  | 0.83548 |  |  | 0.85196 |  |  | 0.88739 |  |  | 0.95338 |  |  | 1.0485 |  |  | 1.3753
[13 empty] | C Non choked w/ reducers | 5 |  | 0.39895 |  |  | 7.9699 |  |  | 19.7232 |  |  | 39.6005 |  |  | 71.6067 |  |  | 121.0853 |  |  | 208.1672 |  |  | 473.7801 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.35724 |  |  | 7.1329 |  |  | 17.6596 |  |  | 35.3162 |  |  | 63.0137 |  |  | 103.0711 |  |  | 160.9735 |  |  | 253.2636 |  |  | 349.436 |  |  | 901.0633
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.39895 |  |  | 7.9699 |  |  | 19.7232 |  |  | 39.6005 |  |  | 71.6067 |  |  | 121.0853 |  |  | 208.1672 |  |  | 473.7801 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3311 | 75.6089 |  | 3.6301 | 1507.6676 |  | 3.2768 | 3691.7242 |  | 0.20047 | 7190.5364 |  | 10.6067 | 12063.4832 |  | 32.8853 | 17606.9823 |  | 87.1672 | 23263.9466 |  | 308.7801 | 28670.3003 |  | 18000 | 33285.3286 |  | 18000 | 39029.6655
[13 empty] | Next iteration flow rate |  |  | 77.121 | Abs Value of | Flow this | 1522.7443 | Abs Value of | Flow this | 3728.6414 | Abs Value of | Flow this | 7262.4417 | Abs Value of | Flow this | 12184.118 | Abs Value of | Flow this | 17783.0521 | Abs Value of | Flow this | 23496.5861 | Abs Value of | Flow this | 28957.0033 | Abs Value of | Flow this | 33618.1819 | Abs Value of | Flow this | 39419.9622 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.157 |  |  | 89.7912 |  |  | 88.5648 |  |  | 85.5428 |  |  | 80.2451 |  |  | 72.7982 |  |  | 63.7546 |  |  | 54.5451 |  |  | 41.1653
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43489 |  |  | 0.43313 |  |  | 0.42721 |  |  | 0.41264 |  |  | 0.38708 |  |  | 0.35116 |  |  | 0.30754 |  |  | 0.26311 |  |  | 0.19857
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.157 |  |  | 29.7912 |  |  | 28.5648 |  |  | 25.5428 |  |  | 20.2451 |  |  | 12.7982 |  |  | 3.7546 |  |  | -5.4549 |  |  | -18.8347
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33449 |  |  | 0.33178 |  |  | 0.32253 |  |  | 0.2986 |  |  | 0.25229 |  |  | 0.1758 |  |  | 0.058891 |  |  | -0.10001 |  |  | -0.45754
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82583 |  |  | 0.8256 |  |  | 0.82807 |  |  | 0.83589 |  |  | 0.85302 |  |  | 0.88981 |  |  | 0.95873 |  |  | 1.0564 |  |  | 1.4049
[13 empty] | C Non choked w/ reducers | 5 |  | 0.40693 |  |  | 8.0498 |  |  | 19.9235 |  |  | 40.0204 |  |  | 72.4565 |  |  | 122.8859 |  |  | 212.9714 |  |  | 509.9026 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.36438 |  |  | 7.2044 |  |  | 17.8379 |  |  | 35.6826 |  |  | 63.7126 |  |  | 104.3571 |  |  | 163.3504 |  |  | 257.8893 |  |  | 357.4799 |  |  | 931.4471
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.40693 |  |  | 8.0498 |  |  | 19.9235 |  |  | 40.0204 |  |  | 72.4565 |  |  | 122.8859 |  |  | 212.9714 |  |  | 509.9026 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3231 | 77.121 |  | 3.5502 | 1522.7443 |  | 3.0765 | 3728.6414 |  | 0.62039 | 7262.4417 |  | 11.4565 | 12184.118 |  | 34.6859 | 17783.0521 |  | 91.9714 | 23496.5861 |  | 344.9026 | 28957.0033 |  | 18000 | 33618.1819 |  | 18000 | 39419.9622
[13 empty] | Next iteration flow rate |  |  | 78.6635 | Abs Value of | Flow this | 1537.9717 | Abs Value of | Flow this | 3765.9278 | Abs Value of | Flow this | 7335.0661 | Abs Value of | Flow this | 12305.9592 | Abs Value of | Flow this | 17960.8826 | Abs Value of | Flow this | 23731.552 | Abs Value of | Flow this | 29246.5734 | Abs Value of | Flow this | 33954.3637 | Abs Value of | Flow this | 39814.1618 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1555 |  |  | 89.7824 |  |  | 88.5314 |  |  | 85.4486 |  |  | 80.0444 |  |  | 72.4478 |  |  | 63.2224 |  |  | 53.8278 |  |  | 40.1791
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43489 |  |  | 0.43309 |  |  | 0.42705 |  |  | 0.41218 |  |  | 0.38611 |  |  | 0.34947 |  |  | 0.30497 |  |  | 0.25965 |  |  | 0.19381
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1555 |  |  | 29.7824 |  |  | 28.5314 |  |  | 25.4486 |  |  | 20.0444 |  |  | 12.4478 |  |  | 3.2224 |  |  | -6.1722 |  |  | -19.8209
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33448 |  |  | 0.33172 |  |  | 0.32227 |  |  | 0.29782 |  |  | 0.25042 |  |  | 0.17182 |  |  | 0.05097 |  |  | -0.11467 |  |  | -0.49331
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82584 |  |  | 0.82563 |  |  | 0.82821 |  |  | 0.83632 |  |  | 0.85412 |  |  | 0.89231 |  |  | 0.96428 |  |  | 1.0647 |  |  | 1.4365
[13 empty] | C Non choked w/ reducers | 5 |  | 0.41506 |  |  | 8.1305 |  |  | 20.1258 |  |  | 40.4453 |  |  | 73.3195 |  |  | 124.7311 |  |  | 218.0221 |  |  | 555.0227 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.37167 |  |  | 7.2765 |  |  | 18.018 |  |  | 36.0531 |  |  | 64.4206 |  |  | 105.6649 |  |  | 165.7818 |  |  | 262.6607 |  |  | 365.8659 |  |  | 963.8528
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.41506 |  |  | 8.1305 |  |  | 20.1258 |  |  | 40.4453 |  |  | 73.3195 |  |  | 124.7311 |  |  | 218.0221 |  |  | 555.0227 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3149 | 78.6635 |  | 3.4695 | 1537.9717 |  | 2.8742 | 3765.9278 |  | 1.0453 | 7335.0661 |  | 12.3195 | 12305.9592 |  | 36.5311 | 17960.8826 |  | 97.0221 | 23731.552 |  | 390.0227 | 29246.5734 |  | 18000 | 33954.3637 |  | 18000 | 39814.1618
[13 empty] | Next iteration flow rate |  |  | 80.2367 | Abs Value of | Flow this | 1553.3514 | Abs Value of | Flow this | 3803.5871 | Abs Value of | Flow this | 7408.4168 | Abs Value of | Flow this | 12429.0188 | Abs Value of | Flow this | 18140.4914 | Abs Value of | Flow this | 23968.8675 | Abs Value of | Flow this | 29539.0391 | Abs Value of | Flow this | 34293.9074 | Abs Value of | Flow this | 40212.3034 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.154 |  |  | 89.7734 |  |  | 88.4972 |  |  | 85.3525 |  |  | 79.8397 |  |  | 72.0903 |  |  | 62.6796 |  |  | 53.0961 |  |  | 39.1731
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43488 |  |  | 0.43304 |  |  | 0.42689 |  |  | 0.41172 |  |  | 0.38513 |  |  | 0.34775 |  |  | 0.30235 |  |  | 0.25612 |  |  | 0.18896
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.154 |  |  | 29.7734 |  |  | 28.4972 |  |  | 25.3525 |  |  | 19.8397 |  |  | 12.0903 |  |  | 2.6796 |  |  | -6.9039 |  |  | -20.8269
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33447 |  |  | 0.33165 |  |  | 0.32201 |  |  | 0.29703 |  |  | 0.24849 |  |  | 0.16771 |  |  | 0.042751 |  |  | -0.13003 |  |  | -0.53166
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82584 |  |  | 0.82567 |  |  | 0.82835 |  |  | 0.83675 |  |  | 0.85524 |  |  | 0.89488 |  |  | 0.97004 |  |  | 1.0734 |  |  | 1.4705
[13 empty] | C Non choked w/ reducers | 5 |  | 0.42337 |  |  | 8.2121 |  |  | 20.3303 |  |  | 40.8752 |  |  | 74.1961 |  |  | 126.623 |  |  | 223.3426 |  |  | 613.7293 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.3791 |  |  | 7.3494 |  |  | 18.2 |  |  | 36.4277 |  |  | 65.1381 |  |  | 106.9952 |  |  | 168.2698 |  |  | 267.5849 |  |  | 374.6167 |  |  | 998.4921
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.42337 |  |  | 8.2121 |  |  | 20.3303 |  |  | 40.8752 |  |  | 74.1961 |  |  | 126.623 |  |  | 223.3426 |  |  | 613.7293 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3066 | 80.2367 |  | 3.3879 | 1553.3514 |  | 2.6697 | 3803.5871 |  | 1.4752 | 7408.4168 |  | 13.1961 | 12429.0188 |  | 38.423 | 18140.4914 |  | 102.3426 | 23968.8675 |  | 448.7293 | 29539.0391 |  | 18000 | 34293.9074 |  | 18000 | 40212.3034
[13 empty] | Next iteration flow rate |  |  | 81.8415 | Abs Value of | Flow this | 1568.885 | Abs Value of | Flow this | 3841.623 | Abs Value of | Flow this | 7482.501 | Abs Value of | Flow this | 12553.309 | Abs Value of | Flow this | 18321.8964 | Abs Value of | Flow this | 24208.5562 | Abs Value of | Flow this | 29834.4295 | Abs Value of | Flow this | 34636.8464 | Abs Value of | Flow this | 40614.4265 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1525 |  |  | 89.7642 |  |  | 88.4624 |  |  | 85.2545 |  |  | 79.6308 |  |  | 71.7257 |  |  | 62.1258 |  |  | 52.3497 |  |  | 38.1468
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43487 |  |  | 0.433 |  |  | 0.42672 |  |  | 0.41125 |  |  | 0.38412 |  |  | 0.34599 |  |  | 0.29968 |  |  | 0.25252 |  |  | 0.18401
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1525 |  |  | 29.7642 |  |  | 28.4624 |  |  | 25.2545 |  |  | 19.6308 |  |  | 11.7257 |  |  | 2.1258 |  |  | -7.6503 |  |  | -21.8532
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33446 |  |  | 0.33158 |  |  | 0.32175 |  |  | 0.29622 |  |  | 0.24652 |  |  | 0.16348 |  |  | 0.034218 |  |  | -0.14614 |  |  | -0.57287
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82585 |  |  | 0.8257 |  |  | 0.82849 |  |  | 0.8372 |  |  | 0.85638 |  |  | 0.89754 |  |  | 0.97602 |  |  | 1.0825 |  |  | 1.5069
[13 empty] | C Non choked w/ reducers | 5 |  | 0.43183 |  |  | 8.2944 |  |  | 20.5369 |  |  | 41.3102 |  |  | 75.0867 |  |  | 128.5636 |  |  | 228.9593 |  |  | 694.7478 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.38669 |  |  | 7.4231 |  |  | 18.3839 |  |  | 36.8064 |  |  | 65.8651 |  |  | 108.3486 |  |  | 170.8164 |  |  | 272.6697 |  |  | 383.7575 |  |  | 1035.6076
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.43183 |  |  | 8.2944 |  |  | 20.5369 |  |  | 41.3102 |  |  | 75.0867 |  |  | 128.5636 |  |  | 228.9593 |  |  | 694.7478 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2982 | 81.8415 |  | 3.3056 | 1568.885 |  | 2.4631 | 3841.623 |  | 1.9102 | 7482.501 |  | 14.0867 | 12553.309 |  | 40.3636 | 18321.8964 |  | 107.9593 | 24208.5562 |  | 529.7478 | 29834.4295 |  | 18000 | 34636.8464 |  | 18000 | 40614.4265
[13 empty] | Next iteration flow rate |  |  | 83.4783 | Abs Value of | Flow this | 1584.5738 | Abs Value of | Flow this | 3880.0392 | Abs Value of | Flow this | 7557.326 | Abs Value of | Flow this | 12678.8421 | Abs Value of | Flow this | 18505.1153 | Abs Value of | Flow this | 24450.6417 | Abs Value of | Flow this | 30132.7738 | Abs Value of | Flow this | 34983.2149 | Abs Value of | Flow this | 41020.5707 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1509 |  |  | 89.7548 |  |  | 88.4269 |  |  | 85.1545 |  |  | 79.4178 |  |  | 71.3538 |  |  | 61.5609 |  |  | 51.5884 |  |  | 37.1
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43487 |  |  | 0.43295 |  |  | 0.42655 |  |  | 0.41076 |  |  | 0.38309 |  |  | 0.34419 |  |  | 0.29695 |  |  | 0.24885 |  |  | 0.17896
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1509 |  |  | 29.7548 |  |  | 28.4269 |  |  | 25.1545 |  |  | 19.4178 |  |  | 11.3538 |  |  | 1.5609 |  |  | -8.4116 |  |  | -22.9
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33445 |  |  | 0.33151 |  |  | 0.32147 |  |  | 0.2954 |  |  | 0.2445 |  |  | 0.15912 |  |  | 0.025356 |  |  | -0.16305 |  |  | -0.61725
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82586 |  |  | 0.82574 |  |  | 0.82864 |  |  | 0.83765 |  |  | 0.85756 |  |  | 0.90027 |  |  | 0.98223 |  |  | 1.092 |  |  | 1.5462
[13 empty] | C Non choked w/ reducers | 5 |  | 0.44047 |  |  | 8.3776 |  |  | 20.7457 |  |  | 41.7505 |  |  | 75.9915 |  |  | 130.5552 |  |  | 234.9025 |  |  | 817.4289 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.39442 |  |  | 7.4974 |  |  | 18.5697 |  |  | 37.1894 |  |  | 66.6019 |  |  | 109.7257 |  |  | 173.4239 |  |  | 277.9235 |  |  | 393.3157 |  |  | 1075.4784
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.44047 |  |  | 8.3776 |  |  | 20.7457 |  |  | 41.7505 |  |  | 75.9915 |  |  | 130.5552 |  |  | 234.9025 |  |  | 817.4289 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2895 | 83.4783 |  | 3.2224 | 1584.5738 |  | 2.2543 | 3880.0392 |  | 2.3505 | 7557.326 |  | 14.9915 | 12678.8421 |  | 42.3552 | 18505.1153 |  | 113.9025 | 24450.6417 |  | 652.4289 | 30132.7738 |  | 18000 | 34983.2149 |  | 18000 | 41020.5707
[13 empty] | Next iteration flow rate |  |  | 85.1479 | Abs Value of | Flow this | 1600.4195 | Abs Value of | Flow this | 3918.8396 | Abs Value of | Flow this | 7632.8992 | Abs Value of | Flow this | 12805.6305 | Abs Value of | Flow this | 18690.1665 | Abs Value of | Flow this | 24695.1481 | Abs Value of | Flow this | 30434.1015 | Abs Value of | Flow this | 35333.0471 | Abs Value of | Flow this | 41430.7764 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.23 |  |  | 90.1493 |  |  | 89.7453 |  |  | 88.3906 |  |  | 85.0524 |  |  | 79.2005 |  |  | 70.9744 |  |  | 60.9847 |  |  | 50.8117 |  |  | 36.032
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43486 |  |  | 0.43291 |  |  | 0.42637 |  |  | 0.41027 |  |  | 0.38204 |  |  | 0.34236 |  |  | 0.29417 |  |  | 0.2451 |  |  | 0.17381
[13 empty] | Delta P at this iteration flow rate |  |  | 30.23 |  |  | 30.1493 |  |  | 29.7453 |  |  | 28.3906 |  |  | 25.0524 |  |  | 19.2005 |  |  | 10.9744 |  |  | 0.98467 |  |  | -9.1883 |  |  | -23.968
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33444 |  |  | 0.33144 |  |  | 0.32119 |  |  | 0.29455 |  |  | 0.24243 |  |  | 0.15462 |  |  | 0.016146 |  |  | -0.18083 |  |  | -0.66518
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82586 |  |  | 0.82578 |  |  | 0.82878 |  |  | 0.83812 |  |  | 0.85877 |  |  | 0.90309 |  |  | 0.98869 |  |  | 1.1021 |  |  | 1.5886
[13 empty] | C Non choked w/ reducers | 5 |  | 0.44928 |  |  | 8.4616 |  |  | 20.9567 |  |  | 42.196 |  |  | 76.911 |  |  | 132.5999 |  |  | 241.2072 |  |  | 1037.5635 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.40231 |  |  | 7.5725 |  |  | 18.7574 |  |  | 37.5767 |  |  | 67.3486 |  |  | 111.127 |  |  | 176.0945 |  |  | 283.3551 |  |  | 403.3211 |  |  | 1118.427
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.44928 |  |  | 8.4616 |  |  | 20.9567 |  |  | 42.196 |  |  | 76.911 |  |  | 132.5999 |  |  | 241.2072 |  |  | 1037.5635 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2807 | 85.1479 |  | 3.1384 | 1600.4195 |  | 2.0433 | 3918.8396 |  | 2.796 | 7632.8992 |  | 15.911 | 12805.6305 |  | 44.3999 | 18690.1665 |  | 120.2072 | 24695.1481 |  | 872.5635 | 30434.1015 |  | 18000 | 35333.0471 |  | 18000 | 41430.7764
[13 empty] | Next iteration flow rate |  |  | 86.8508 | Abs Value of | Flow this | 1616.4237 | Abs Value of | Flow this | 3958.028 | Abs Value of | Flow this | 7709.2282 | Abs Value of | Flow this | 12933.6868 | Abs Value of | Flow this | 18877.0681 | Abs Value of | Flow this | 24942.0996 | Abs Value of | Flow this | 30738.4425 | Abs Value of | Flow this | 35686.3775 | Abs Value of | Flow this | 41845.0842 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2299 |  |  | 90.1477 |  |  | 89.7355 |  |  | 88.3536 |  |  | 84.9484 |  |  | 78.9788 |  |  | 70.5873 |  |  | 60.3968 |  |  | 50.0193 |  |  | 34.9427
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43485 |  |  | 0.43286 |  |  | 0.4262 |  |  | 0.40977 |  |  | 0.38097 |  |  | 0.3405 |  |  | 0.29134 |  |  | 0.24128 |  |  | 0.16855
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2299 |  |  | 30.1477 |  |  | 29.7355 |  |  | 28.3536 |  |  | 24.9484 |  |  | 18.9788 |  |  | 10.5873 |  |  | 0.39683 |  |  | -9.9807 |  |  | -25.0573
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33443 |  |  | 0.33137 |  |  | 0.32091 |  |  | 0.29369 |  |  | 0.2403 |  |  | 0.14999 |  |  | 0.0065705 |  |  | -0.19954 |  |  | -0.7171
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82587 |  |  | 0.82582 |  |  | 0.82894 |  |  | 0.83859 |  |  | 0.86001 |  |  | 0.90599 |  |  | 0.9954 |  |  | 1.1126 |  |  | 1.6346
[13 empty] | C Non choked w/ reducers | 5 |  | 0.45827 |  |  | 8.5464 |  |  | 21.1699 |  |  | 42.6469 |  |  | 77.8456 |  |  | 134.7005 |  |  | 247.9138 |  |  | 1647.5631 |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.41035 |  |  | 7.6484 |  |  | 18.947 |  |  | 37.9684 |  |  | 68.1055 |  |  | 112.5533 |  |  | 178.8306 |  |  | 288.9741 |  |  | 413.8069 |  |  | 1164.8283
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.45827 |  |  | 8.5464 |  |  | 21.1699 |  |  | 42.6469 |  |  | 77.8456 |  |  | 134.7005 |  |  | 247.9138 |  |  | 1647.5631 |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2717 | 86.8508 |  | 3.0536 | 1616.4237 |  | 1.8301 | 3958.028 |  | 3.2469 | 7709.2282 |  | 16.8456 | 12933.6868 |  | 46.5005 | 18877.0681 |  | 126.9138 | 24942.0996 |  | 1482.5631 | 30738.4425 |  | 18000 | 35686.3775 |  | 18000 | 41845.0842
[13 empty] | Next iteration flow rate |  |  | 88.5878 | Abs Value of | Flow this | 1632.588 | Abs Value of | Flow this | 3997.6083 | Abs Value of | Flow this | 7786.3205 | Abs Value of | Flow this | 13063.0237 | Abs Value of | Flow this | 19065.8388 | Abs Value of | Flow this | 25191.5206 | Abs Value of | Flow this | 31045.827 | Abs Value of | Flow this | 36043.2413 | Abs Value of | Flow this | 42263.535 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2299 |  |  | 90.146 |  |  | 89.7256 |  |  | 88.3159 |  |  | 84.8422 |  |  | 78.7526 |  |  | 70.1925 |  |  | 59.7972 |  |  | 49.2111 |  |  | 33.8314
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43484 |  |  | 0.43281 |  |  | 0.42601 |  |  | 0.40926 |  |  | 0.37988 |  |  | 0.33859 |  |  | 0.28845 |  |  | 0.23738 |  |  | 0.16319
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2299 |  |  | 30.146 |  |  | 29.7256 |  |  | 28.3159 |  |  | 24.8422 |  |  | 18.7526 |  |  | 10.1925 |  |  | -0.20282 |  |  | -10.7889 |  |  | -26.1686
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33441 |  |  | 0.33129 |  |  | 0.32062 |  |  | 0.2928 |  |  | 0.23812 |  |  | 0.14521 |  |  | -0.0033917 |  |  | -0.21924 |  |  | -0.7735
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82587 |  |  | 0.82586 |  |  | 0.82909 |  |  | 0.83908 |  |  | 0.86128 |  |  | 0.90899 |  |  | 1.0024 |  |  | 1.1237 |  |  | 1.6845
[13 empty] | C Non choked w/ reducers | 5 |  | 0.46743 |  |  | 8.6322 |  |  | 21.3854 |  |  | 43.1032 |  |  | 78.7955 |  |  | 136.8595 |  |  | 255.0696 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.41856 |  |  | 7.725 |  |  | 19.1386 |  |  | 38.3644 |  |  | 68.8726 |  |  | 114.0053 |  |  | 181.6349 |  |  | 294.7907 |  |  | 424.8092 |  |  | 1215.121
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.46743 |  |  | 8.6322 |  |  | 21.3854 |  |  | 43.1032 |  |  | 78.7955 |  |  | 136.8595 |  |  | 255.0696 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2626 | 88.5878 |  | 2.9678 | 1632.588 |  | 1.6146 | 3997.6083 |  | 3.7032 | 7786.3205 |  | 17.7955 | 13063.0237 |  | 48.6595 | 19065.8388 |  | 134.0696 | 25191.5206 |  | 18000 | 31045.827 |  | 18000 | 36043.2413 |  | 18000 | 42263.535
[13 empty] | Next iteration flow rate |  |  | 90.3596 | Abs Value of | Flow this | 1648.9139 | Abs Value of | Flow this | 4037.5843 | Abs Value of | Flow this | 7864.1837 | Abs Value of | Flow this | 13193.6539 | Abs Value of | Flow this | 19256.4972 | Abs Value of | Flow this | 25443.4358 | Abs Value of | Flow this | 31356.2852 | Abs Value of | Flow this | 36403.6737 | Abs Value of | Flow this | 42686.1704 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2299 |  |  | 90.1443 |  |  | 89.7154 |  |  | 88.2774 |  |  | 84.7339 |  |  | 78.5219 |  |  | 69.7898 |  |  | 59.1855 |  |  | 48.3866 |  |  | 32.6978
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43483 |  |  | 0.43276 |  |  | 0.42583 |  |  | 0.40874 |  |  | 0.37877 |  |  | 0.33665 |  |  | 0.2855 |  |  | 0.2334 |  |  | 0.15773
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2299 |  |  | 30.1443 |  |  | 29.7154 |  |  | 28.2774 |  |  | 24.7339 |  |  | 18.5219 |  |  | 9.7898 |  |  | -0.81452 |  |  | -11.6134 |  |  | -27.3022
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.3344 |  |  | 0.33122 |  |  | 0.32032 |  |  | 0.2919 |  |  | 0.23588 |  |  | 0.14028 |  |  | -0.013762 |  |  | -0.24001 |  |  | -0.83499
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82588 |  |  | 0.8259 |  |  | 0.82925 |  |  | 0.83957 |  |  | 0.86258 |  |  | 0.91208 |  |  | 1.0096 |  |  | 1.1355 |  |  | 1.7389
[13 empty] | C Non choked w/ reducers | 5 |  | 0.47678 |  |  | 8.7187 |  |  | 21.6031 |  |  | 43.565 |  |  | 79.7612 |  |  | 139.0799 |  |  | 262.73 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.42693 |  |  | 7.8024 |  |  | 19.3322 |  |  | 38.765 |  |  | 69.6502 |  |  | 115.4837 |  |  | 184.5099 |  |  | 300.8159 |  |  | 436.3682 |  |  | 1269.8212
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.47678 |  |  | 8.7187 |  |  | 21.6031 |  |  | 43.565 |  |  | 79.7612 |  |  | 139.0799 |  |  | 262.73 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2532 | 90.3596 |  | 2.8813 | 1648.9139 |  | 1.3969 | 4037.5843 |  | 4.165 | 7864.1837 |  | 18.7612 | 13193.6539 |  | 50.8799 | 19256.4972 |  | 141.73 | 25443.4358 |  | 18000 | 31356.2852 |  | 18000 | 36403.6737 |  | 18000 | 42686.1704
[13 empty] | Next iteration flow rate |  |  | 92.1668 | Abs Value of | Flow this | 1665.403 | Abs Value of | Flow this | 4077.9602 | Abs Value of | Flow this | 7942.8256 | Abs Value of | Flow this | 13325.5904 | Abs Value of | Flow this | 19449.0622 | Abs Value of | Flow this | 25697.8702 | Abs Value of | Flow this | 31669.8481 | Abs Value of | Flow this | 36767.7105 | Abs Value of | Flow this | 43113.0321 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2299 |  |  | 90.1426 |  |  | 89.7051 |  |  | 88.2382 |  |  | 84.6234 |  |  | 78.2866 |  |  | 69.3789 |  |  | 58.5615 |  |  | 47.5456 |  |  | 31.5414
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43483 |  |  | 0.43271 |  |  | 0.42564 |  |  | 0.4082 |  |  | 0.37763 |  |  | 0.33467 |  |  | 0.28249 |  |  | 0.22935 |  |  | 0.15215
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2299 |  |  | 30.1426 |  |  | 29.7051 |  |  | 28.2382 |  |  | 24.6234 |  |  | 18.2866 |  |  | 9.3789 |  |  | -1.4385 |  |  | -12.4544 |  |  | -28.4586
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33439 |  |  | 0.33114 |  |  | 0.32002 |  |  | 0.29098 |  |  | 0.23359 |  |  | 0.13518 |  |  | -0.024564 |  |  | -0.26195 |  |  | -0.90226
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82589 |  |  | 0.82594 |  |  | 0.82941 |  |  | 0.84008 |  |  | 0.86392 |  |  | 0.91527 |  |  | 1.0172 |  |  | 1.1479 |  |  | 1.7984
[13 empty] | C Non choked w/ reducers | 5 |  | 0.48632 |  |  | 8.8062 |  |  | 21.8231 |  |  | 44.0325 |  |  | 80.7432 |  |  | 141.3647 |  |  | 270.9607 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.43547 |  |  | 7.8806 |  |  | 19.5277 |  |  | 39.17 |  |  | 70.4386 |  |  | 116.9891 |  |  | 187.4586 |  |  | 307.0614 |  |  | 448.5282 |  |  | 1329.5404
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.48632 |  |  | 8.8062 |  |  | 21.8231 |  |  | 44.0325 |  |  | 80.7432 |  |  | 141.3647 |  |  | 270.9607 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2437 | 92.1668 |  | 2.7938 | 1665.403 |  | 1.1769 | 4077.9602 |  | 4.6325 | 7942.8256 |  | 19.7432 | 13325.5904 |  | 53.1647 | 19449.0622 |  | 149.9607 | 25697.8702 |  | 18000 | 31669.8481 |  | 18000 | 36767.7105 |  | 18000 | 43113.0321
[13 empty] | Next iteration flow rate |  |  | 94.0101 | Abs Value of | Flow this | 1682.057 | Abs Value of | Flow this | 4118.7398 | Abs Value of | Flow this | 8022.2538 | Abs Value of | Flow this | 13458.8463 | Abs Value of | Flow this | 19643.5528 | Abs Value of | Flow this | 25954.8489 | Abs Value of | Flow this | 31986.5466 | Abs Value of | Flow this | 37135.3876 | Abs Value of | Flow this | 43544.1624 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2299 |  |  | 90.1408 |  |  | 89.6945 |  |  | 88.1981 |  |  | 84.5107 |  |  | 78.0465 |  |  | 68.9598 |  |  | 57.9249 |  |  | 46.6876 |  |  | 30.3617
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43482 |  |  | 0.43266 |  |  | 0.42545 |  |  | 0.40766 |  |  | 0.37648 |  |  | 0.33264 |  |  | 0.27942 |  |  | 0.22521 |  |  | 0.14646
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2299 |  |  | 30.1408 |  |  | 29.6945 |  |  | 28.1981 |  |  | 24.5107 |  |  | 18.0465 |  |  | 8.9598 |  |  | -2.0751 |  |  | -13.3124 |  |  | -29.6383
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33437 |  |  | 0.33106 |  |  | 0.31971 |  |  | 0.29003 |  |  | 0.23123 |  |  | 0.12993 |  |  | -0.035823 |  |  | -0.28514 |  |  | -0.97617
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82589 |  |  | 0.82598 |  |  | 0.82957 |  |  | 0.8406 |  |  | 0.86529 |  |  | 0.91857 |  |  | 1.0251 |  |  | 1.1609 |  |  | 1.8638
[13 empty] | C Non choked w/ reducers | 5 |  | 0.49604 |  |  | 8.8945 |  |  | 22.0454 |  |  | 44.5056 |  |  | 81.7418 |  |  | 143.7173 |  |  | 279.8402 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.44418 |  |  | 7.9595 |  |  | 19.7253 |  |  | 39.5797 |  |  | 71.2378 |  |  | 118.5225 |  |  | 190.4839 |  |  | 313.5401 |  |  | 461.3384 |  |  | 1395.0091
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.49604 |  |  | 8.8945 |  |  | 22.0454 |  |  | 44.5056 |  |  | 81.7418 |  |  | 143.7173 |  |  | 279.8402 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.234 | 94.0101 |  | 2.7055 | 1682.057 |  | 0.95455 | 4118.7398 |  | 5.1056 | 8022.2538 |  | 20.7418 | 13458.8463 |  | 55.5173 | 19643.5528 |  | 158.8402 | 25954.8489 |  | 18000 | 31986.5466 |  | 18000 | 37135.3876 |  | 18000 | 43544.1624
[13 empty] | Next iteration flow rate |  |  | 95.8903 | Abs Value of | Flow this | 1698.8776 | Abs Value of | Flow this | 4159.9272 | Abs Value of | Flow this | 8102.4763 | Abs Value of | Flow this | 13593.4348 | Abs Value of | Flow this | 19839.9883 | Abs Value of | Flow this | 26214.3974 | Abs Value of | Flow this | 32306.412 | Abs Value of | Flow this | 37506.7414 | Abs Value of | Flow this | 43979.604 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2299 |  |  | 90.139 |  |  | 89.6838 |  |  | 88.1573 |  |  | 84.3958 |  |  | 77.8016 |  |  | 68.5323 |  |  | 57.2756 |  |  | 45.8124 |  |  | 29.1584
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43481 |  |  | 0.43261 |  |  | 0.42525 |  |  | 0.4071 |  |  | 0.3753 |  |  | 0.33058 |  |  | 0.27628 |  |  | 0.22099 |  |  | 0.14065
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2299 |  |  | 30.139 |  |  | 29.6838 |  |  | 28.1573 |  |  | 24.3958 |  |  | 17.8016 |  |  | 8.5323 |  |  | -2.7244 |  |  | -14.1876 |  |  | -30.8416
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33436 |  |  | 0.33098 |  |  | 0.3194 |  |  | 0.28906 |  |  | 0.22881 |  |  | 0.1245 |  |  | -0.047566 |  |  | -0.30969 |  |  | -1.0577
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.8259 |  |  | 0.82602 |  |  | 0.82974 |  |  | 0.84113 |  |  | 0.8667 |  |  | 0.92197 |  |  | 1.0333 |  |  | 1.1748 |  |  | 1.936
[13 empty] | C Non choked w/ reducers | 5 |  | 0.50596 |  |  | 8.9838 |  |  | 22.2701 |  |  | 44.9846 |  |  | 82.7575 |  |  | 146.1412 |  |  | 289.4632 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.45306 |  |  | 8.0393 |  |  | 19.925 |  |  | 39.994 |  |  | 72.0482 |  |  | 120.0845 |  |  | 193.5889 |  |  | 320.2656 |  |  | 474.8534 |  |  | 1467.1065
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.50596 |  |  | 8.9838 |  |  | 22.2701 |  |  | 44.9846 |  |  | 82.7575 |  |  | 146.1412 |  |  | 289.4632 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.224 | 95.8903 |  | 2.6162 | 1698.8776 |  | 0.72986 | 4159.9272 |  | 5.5846 | 8102.4763 |  | 21.7575 | 13593.4348 |  | 57.9412 | 19839.9883 |  | 168.4632 | 26214.3974 |  | 18000 | 32306.412 |  | 18000 | 37506.7414 |  | 18000 | 43979.604
[13 empty] | Next iteration flow rate |  |  | 97.8081 | Abs Value of | Flow this | 1715.8664 | Abs Value of | Flow this | 4201.5265 | Abs Value of | Flow this | 8183.5011 | Abs Value of | Flow this | 13729.3692 | Abs Value of | Flow this | 20038.3882 | Abs Value of | Flow this | 26476.5413 | Abs Value of | Flow this | 32629.4762 | Abs Value of | Flow this | 37881.8088 | Abs Value of | Flow this | 44419.4001 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2299 |  |  | 90.1372 |  |  | 89.6728 |  |  | 88.1156 |  |  | 84.2785 |  |  | 77.5518 |  |  | 68.0961 |  |  | 56.6132 |  |  | 44.9196 |  |  | 27.9308
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.4348 |  |  | 0.43256 |  |  | 0.42505 |  |  | 0.40654 |  |  | 0.37409 |  |  | 0.32848 |  |  | 0.27309 |  |  | 0.21668 |  |  | 0.13473
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2299 |  |  | 30.1372 |  |  | 29.6728 |  |  | 28.1156 |  |  | 24.2785 |  |  | 17.5518 |  |  | 8.0961 |  |  | -3.3868 |  |  | -15.0804 |  |  | -32.0692
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33435 |  |  | 0.3309 |  |  | 0.31908 |  |  | 0.28807 |  |  | 0.22632 |  |  | 0.11889 |  |  | -0.059823 |  |  | -0.33572 |  |  | -1.1482
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82591 |  |  | 0.82606 |  |  | 0.82991 |  |  | 0.84168 |  |  | 0.86815 |  |  | 0.92548 |  |  | 1.0419 |  |  | 1.1895 |  |  | 2.016
[13 empty] | C Non choked w/ reducers | 5 |  | 0.51608 |  |  | 9.0739 |  |  | 22.4972 |  |  | 45.4694 |  |  | 83.7908 |  |  | 148.6404 |  |  | 299.9453 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.46212 |  |  | 8.1199 |  |  | 20.1267 |  |  | 40.413 |  |  | 72.8699 |  |  | 121.676 |  |  | 196.7771 |  |  | 327.2529 |  |  | 489.1342 |  |  | 1546.9008
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.51608 |  |  | 9.0739 |  |  | 22.4972 |  |  | 45.4694 |  |  | 83.7908 |  |  | 148.6404 |  |  | 299.9453 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2139 | 97.8081 |  | 2.5261 | 1715.8664 |  | 0.50279 | 4201.5265 |  | 6.0694 | 8183.5011 |  | 22.7908 | 13729.3692 |  | 60.4404 | 20038.3882 |  | 178.9453 | 26476.5413 |  | 18000 | 32629.4762 |  | 18000 | 37881.8088 |  | 18000 | 44419.4001
[13 empty] | Next iteration flow rate |  |  | 99.7643 | Abs Value of | Flow this | 1733.025 | Abs Value of | Flow this | 4243.5417 | Abs Value of | Flow this | 8265.3361 | Abs Value of | Flow this | 13866.6628 | Abs Value of | Flow this | 20238.7721 | Abs Value of | Flow this | 26741.3068 | Abs Value of | Flow this | 32955.7709 | Abs Value of | Flow this | 38260.6269 | Abs Value of | Flow this | 44863.5941 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2299 |  |  | 90.1353 |  |  | 89.6616 |  |  | 88.0731 |  |  | 84.1589 |  |  | 77.297 |  |  | 67.6512 |  |  | 55.9375 |  |  | 44.0089 |  |  | 26.6786
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43479 |  |  | 0.43251 |  |  | 0.42484 |  |  | 0.40596 |  |  | 0.37286 |  |  | 0.32633 |  |  | 0.26983 |  |  | 0.21229 |  |  | 0.12869
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2299 |  |  | 30.1353 |  |  | 29.6616 |  |  | 28.0731 |  |  | 24.1589 |  |  | 17.297 |  |  | 7.6512 |  |  | -4.0625 |  |  | -15.9911 |  |  | -33.3214
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33433 |  |  | 0.33082 |  |  | 0.31875 |  |  | 0.28706 |  |  | 0.22377 |  |  | 0.1131 |  |  | -0.072625 |  |  | -0.36336 |  |  | -1.249
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82592 |  |  | 0.82611 |  |  | 0.83009 |  |  | 0.84223 |  |  | 0.86964 |  |  | 0.92911 |  |  | 1.0509 |  |  | 1.2051 |  |  | 2.1052
[13 empty] | C Non choked w/ reducers | 5 |  | 0.5264 |  |  | 9.1649 |  |  | 22.7267 |  |  | 45.9603 |  |  | 84.8422 |  |  | 151.2189 |  |  | 311.4288 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.47137 |  |  | 8.2012 |  |  | 20.3305 |  |  | 40.8369 |  |  | 73.7033 |  |  | 123.298 |  |  | 200.0518 |  |  | 334.5181 |  |  | 504.2492 |  |  | 1635.703
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.5264 |  |  | 9.1649 |  |  | 22.7267 |  |  | 45.9603 |  |  | 84.8422 |  |  | 151.2189 |  |  | 311.4288 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2036 | 99.7643 |  | 2.4351 | 1733.025 |  | 0.27332 | 4243.5417 |  | 6.5603 | 8265.3361 |  | 23.8422 | 13866.6628 |  | 63.0189 | 20238.7721 |  | 190.4288 | 26741.3068 |  | 18000 | 32955.7709 |  | 18000 | 38260.6269 |  | 18000 | 44863.5941
[13 empty] | Next iteration flow rate |  |  | 101.7596 | Abs Value of | Flow this | 1750.3553 | Abs Value of | Flow this | 4285.9771 | Abs Value of | Flow this | 8347.9895 | Abs Value of | Flow this | 14005.3295 | Abs Value of | Flow this | 20441.1598 | Abs Value of | Flow this | 27008.7198 | Abs Value of | Flow this | 33285.3286 | Abs Value of | Flow this | 38643.2332 | Abs Value of | Flow this | 45312.23 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2299 |  |  | 90.1334 |  |  | 89.6502 |  |  | 88.0298 |  |  | 84.0368 |  |  | 77.037 |  |  | 67.1974 |  |  | 55.2482 |  |  | 43.0798 |  |  | 25.4012
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43478 |  |  | 0.43245 |  |  | 0.42463 |  |  | 0.40537 |  |  | 0.37161 |  |  | 0.32414 |  |  | 0.2665 |  |  | 0.20781 |  |  | 0.12253
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2299 |  |  | 30.1334 |  |  | 29.6502 |  |  | 28.0298 |  |  | 24.0368 |  |  | 17.037 |  |  | 7.1974 |  |  | -4.7518 |  |  | -16.9202 |  |  | -34.5988
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33432 |  |  | 0.33073 |  |  | 0.31841 |  |  | 0.28603 |  |  | 0.22115 |  |  | 0.10711 |  |  | -0.086008 |  |  | -0.39276 |  |  | -1.3621
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82592 |  |  | 0.82615 |  |  | 0.83027 |  |  | 0.8428 |  |  | 0.87116 |  |  | 0.93287 |  |  | 1.0603 |  |  | 1.2217 |  |  | 2.2053
[13 empty] | C Non choked w/ reducers | 5 |  | 0.53693 |  |  | 9.2569 |  |  | 22.9586 |  |  | 46.4572 |  |  | 85.9122 |  |  | 153.8813 |  |  | 324.0921 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.48079 |  |  | 8.2834 |  |  | 20.5364 |  |  | 41.2656 |  |  | 74.5484 |  |  | 124.9512 |  |  | 203.417 |  |  | 342.0785 |  |  | 520.2749 |  |  | 1735.1395
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.53693 |  |  | 9.2569 |  |  | 22.9586 |  |  | 46.4572 |  |  | 85.9122 |  |  | 153.8813 |  |  | 324.0921 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1931 | 101.7596 |  | 2.3431 | 1750.3553 |  | 0.041413 | 4285.9771 |  | 7.0572 | 8347.9895 |  | 24.9122 | 14005.3295 |  | 65.6813 | 20441.1598 |  | 203.0921 | 27008.7198 |  | 18000 | 33285.3286 |  | 18000 | 38643.2332 |  | 18000 | 45312.23
[13 empty] | Next iteration flow rate |  |  | 103.7948 | Abs Value of | Flow this | 1767.8588 | Abs Value of | Flow this | 4328.8369 | Abs Value of | Flow this | 8431.4694 | Abs Value of | Flow this | 14145.3828 | Abs Value of | Flow this | 20645.5714 | Abs Value of | Flow this | 27278.807 | Abs Value of | Flow this | 33618.1819 | Abs Value of | Flow this | 39029.6655 | Abs Value of | Flow this | 45765.3523 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2298 |  |  | 90.1315 |  |  | 89.6385 |  |  | 87.9855 |  |  | 83.9124 |  |  | 76.7718 |  |  | 66.7344 |  |  | 54.5451 |  |  | 42.1321 |  |  | 24.0982
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43477 |  |  | 0.43239 |  |  | 0.42442 |  |  | 0.40477 |  |  | 0.37033 |  |  | 0.32191 |  |  | 0.26311 |  |  | 0.20323 |  |  | 0.11624
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2298 |  |  | 30.1315 |  |  | 29.6385 |  |  | 27.9855 |  |  | 23.9124 |  |  | 16.7718 |  |  | 6.7344 |  |  | -5.4549 |  |  | -17.8679 |  |  | -35.9018
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33431 |  |  | 0.33064 |  |  | 0.31807 |  |  | 0.28497 |  |  | 0.21846 |  |  | 0.10091 |  |  | -0.10001 |  |  | -0.42409 |  |  | -1.4898
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82593 |  |  | 0.8262 |  |  | 0.83045 |  |  | 0.84338 |  |  | 0.87273 |  |  | 0.93675 |  |  | 1.0701 |  |  | 1.2394 |  |  | 2.3183
[13 empty] | C Non choked w/ reducers | 5 |  | 0.54767 |  |  | 9.3498 |  |  | 23.193 |  |  | 46.9603 |  |  | 87.0013 |  |  | 156.6325 |  |  | 338.1617 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.49041 |  |  | 8.3664 |  |  | 20.7445 |  |  | 41.6992 |  |  | 75.4056 |  |  | 126.6366 |  |  | 206.8764 |  |  | 349.953 |  |  | 537.2978 |  |  | 1847.2536
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.54767 |  |  | 9.3498 |  |  | 23.193 |  |  | 46.9603 |  |  | 87.0013 |  |  | 156.6325 |  |  | 338.1617 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1823 | 103.7948 |  | 2.2502 | 1767.8588 |  | 0.19296 | 4328.8369 |  | 7.5603 | 8431.4694 |  | 26.0013 | 14145.3828 |  | 68.4325 | 20645.5714 |  | 217.1617 | 27278.807 |  | 18000 | 33618.1819 |  | 18000 | 39029.6655 |  | 18000 | 45765.3523
[13 empty] | Next iteration flow rate |  |  | 105.8707 | Abs Value of | Flow this | 1785.5374 | Abs Value of | Flow this | 4372.1253 | Abs Value of | Flow this | 8515.7841 | Abs Value of | Flow this | 14286.8366 | Abs Value of | Flow this | 20852.0271 | Abs Value of | Flow this | 27551.5951 | Abs Value of | Flow this | 33954.3637 | Abs Value of | Flow this | 39419.9622 | Abs Value of | Flow this | 46223.0059 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2298 |  |  | 90.1295 |  |  | 89.6266 |  |  | 87.9404 |  |  | 83.7854 |  |  | 76.5013 |  |  | 66.2622 |  |  | 53.8278 |  |  | 41.1653 |  |  | 22.7689
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43476 |  |  | 0.43234 |  |  | 0.4242 |  |  | 0.40416 |  |  | 0.36902 |  |  | 0.31963 |  |  | 0.25965 |  |  | 0.19857 |  |  | 0.10983
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2298 |  |  | 30.1295 |  |  | 29.6266 |  |  | 27.9404 |  |  | 23.7854 |  |  | 16.5013 |  |  | 6.2622 |  |  | -6.1722 |  |  | -18.8347 |  |  | -37.2311
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33429 |  |  | 0.33056 |  |  | 0.31772 |  |  | 0.28388 |  |  | 0.2157 |  |  | 0.094506 |  |  | -0.11467 |  |  | -0.45754 |  |  | -1.6352
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82594 |  |  | 0.82624 |  |  | 0.83064 |  |  | 0.84398 |  |  | 0.87434 |  |  | 0.94077 |  |  | 1.0804 |  |  | 1.2583 |  |  | 2.447
[13 empty] | C Non choked w/ reducers | 5 |  | 0.55862 |  |  | 9.4436 |  |  | 23.4298 |  |  | 47.4697 |  |  | 88.1101 |  |  | 159.4778 |  |  | 353.9305 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.50022 |  |  | 8.4503 |  |  | 20.9547 |  |  | 42.1378 |  |  | 76.2751 |  |  | 128.3552 |  |  | 210.4344 |  |  | 358.1624 |  |  | 555.4155 |  |  | 1974.6476
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.55862 |  |  | 9.4436 |  |  | 23.4298 |  |  | 47.4697 |  |  | 88.1101 |  |  | 159.4778 |  |  | 353.9305 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1714 | 105.8707 |  | 2.1564 | 1785.5374 |  | 0.42982 | 4372.1253 |  | 8.0697 | 8515.7841 |  | 27.1101 | 14286.8366 |  | 71.2778 | 20852.0271 |  | 232.9305 | 27551.5951 |  | 18000 | 33954.3637 |  | 18000 | 39419.9622 |  | 18000 | 46223.0059
[13 empty] | Next iteration flow rate |  |  | 107.9881 | Abs Value of | Flow this | 1803.3928 | Abs Value of | Flow this | 4415.8465 | Abs Value of | Flow this | 8600.9419 | Abs Value of | Flow this | 14429.705 | Abs Value of | Flow this | 21060.5474 | Abs Value of | Flow this | 27827.111 | Abs Value of | Flow this | 34293.9074 | Abs Value of | Flow this | 39814.1618 | Abs Value of | Flow this | 46685.2359 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2298 |  |  | 90.1275 |  |  | 89.6145 |  |  | 87.8944 |  |  | 83.6558 |  |  | 76.2254 |  |  | 65.7804 |  |  | 53.0961 |  |  | 40.1791 |  |  | 21.4129
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43475 |  |  | 0.43228 |  |  | 0.42398 |  |  | 0.40353 |  |  | 0.36769 |  |  | 0.31731 |  |  | 0.25612 |  |  | 0.19381 |  |  | 0.10329
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2298 |  |  | 30.1275 |  |  | 29.6145 |  |  | 27.8944 |  |  | 23.6558 |  |  | 16.2254 |  |  | 5.7804 |  |  | -6.9039 |  |  | -19.8209 |  |  | -38.5871
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33428 |  |  | 0.33047 |  |  | 0.31736 |  |  | 0.28278 |  |  | 0.21286 |  |  | 0.087875 |  |  | -0.13003 |  |  | -0.49331 |  |  | -1.802
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82595 |  |  | 0.82629 |  |  | 0.83083 |  |  | 0.84459 |  |  | 0.87599 |  |  | 0.94492 |  |  | 1.0911 |  |  | 1.2785 |  |  | 2.5946
[13 empty] | C Non choked w/ reducers | 5 |  | 0.5698 |  |  | 9.5384 |  |  | 23.6692 |  |  | 47.9855 |  |  | 89.2391 |  |  | 162.423 |  |  | 371.7854 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.51022 |  |  | 8.535 |  |  | 21.1671 |  |  | 42.5814 |  |  | 77.1571 |  |  | 130.1081 |  |  | 214.0953 |  |  | 366.729 |  |  | 574.7387 |  |  | 2120.689
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.5698 |  |  | 9.5384 |  |  | 23.6692 |  |  | 47.9855 |  |  | 89.2391 |  |  | 162.423 |  |  | 371.7854 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1602 | 107.9881 |  | 2.0616 | 1803.3928 |  | 0.6692 | 4415.8465 |  | 8.5855 | 8600.9419 |  | 28.2391 | 14429.705 |  | 74.223 | 21060.5474 |  | 250.7854 | 27827.111 |  | 18000 | 34293.9074 |  | 18000 | 39814.1618 |  | 18000 | 46685.2359
[13 empty] | Next iteration flow rate |  |  | 110.1478 | Abs Value of | Flow this | 1821.4267 | Abs Value of | Flow this | 4460.005 | Abs Value of | Flow this | 8686.9513 | Abs Value of | Flow this | 14574.002 | Abs Value of | Flow this | 21271.1529 | Abs Value of | Flow this | 28105.3822 | Abs Value of | Flow this | 34636.8464 | Abs Value of | Flow this | 40212.3034 | Abs Value of | Flow this | 47152.0883 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2298 |  |  | 90.1254 |  |  | 89.6021 |  |  | 87.8475 |  |  | 83.5237 |  |  | 75.9439 |  |  | 65.289 |  |  | 52.3497 |  |  | 39.1731 |  |  | 20.0297
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43474 |  |  | 0.43222 |  |  | 0.42375 |  |  | 0.4029 |  |  | 0.36633 |  |  | 0.31494 |  |  | 0.25252 |  |  | 0.18896 |  |  | 0.096618
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2298 |  |  | 30.1254 |  |  | 29.6021 |  |  | 27.8475 |  |  | 23.5237 |  |  | 15.9439 |  |  | 5.289 |  |  | -7.6503 |  |  | -20.8269 |  |  | -39.9703
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33426 |  |  | 0.33037 |  |  | 0.317 |  |  | 0.28164 |  |  | 0.20994 |  |  | 0.081009 |  |  | -0.14614 |  |  | -0.53166 |  |  | -1.9956
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82595 |  |  | 0.82634 |  |  | 0.83102 |  |  | 0.84521 |  |  | 0.87769 |  |  | 0.94923 |  |  | 1.1024 |  |  | 1.3001 |  |  | 2.7659
[13 empty] | C Non choked w/ reducers | 5 |  | 0.58119 |  |  | 9.6341 |  |  | 23.9111 |  |  | 48.5078 |  |  | 90.3891 |  |  | 165.4744 |  |  | 392.2496 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.52043 |  |  | 8.6205 |  |  | 21.3818 |  |  | 43.0302 |  |  | 78.052 |  |  | 131.8963 |  |  | 217.8639 |  |  | 375.6774 |  |  | 595.3939 |  |  | 2289.8126
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.58119 |  |  | 9.6341 |  |  | 23.9111 |  |  | 48.5078 |  |  | 90.3891 |  |  | 165.4744 |  |  | 392.2496 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1488 | 110.1478 |  | 1.9659 | 1821.4267 |  | 0.91113 | 4460.005 |  | 9.1078 | 8686.9513 |  | 29.3891 | 14574.002 |  | 77.2744 | 21271.1529 |  | 271.2496 | 28105.3822 |  | 18000 | 34636.8464 |  | 18000 | 40212.3034 |  | 18000 | 47152.0883
[13 empty] | Next iteration flow rate |  |  | 112.3508 | Abs Value of | Flow this | 1839.641 | Abs Value of | Flow this | 4504.605 | Abs Value of | Flow this | 8773.8208 | Abs Value of | Flow this | 14719.742 | Abs Value of | Flow this | 21483.8644 | Abs Value of | Flow this | 28386.436 | Abs Value of | Flow this | 34983.2149 | Abs Value of | Flow this | 40614.4265 | Abs Value of | Flow this | 47623.6092 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2298 |  |  | 90.1233 |  |  | 89.5895 |  |  | 87.7996 |  |  | 83.3889 |  |  | 75.6567 |  |  | 64.7877 |  |  | 51.5884 |  |  | 38.1468 |  |  | 18.6187
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43473 |  |  | 0.43216 |  |  | 0.42352 |  |  | 0.40225 |  |  | 0.36495 |  |  | 0.31252 |  |  | 0.24885 |  |  | 0.18401 |  |  | 0.089812
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2298 |  |  | 30.1233 |  |  | 29.5895 |  |  | 27.7996 |  |  | 23.3889 |  |  | 15.6567 |  |  | 4.7877 |  |  | -8.4116 |  |  | -21.8532 |  |  | -41.3813
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33425 |  |  | 0.33028 |  |  | 0.31663 |  |  | 0.28048 |  |  | 0.20694 |  |  | 0.073898 |  |  | -0.16305 |  |  | -0.57287 |  |  | -2.2226
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82596 |  |  | 0.82639 |  |  | 0.83122 |  |  | 0.84585 |  |  | 0.87944 |  |  | 0.95368 |  |  | 1.1143 |  |  | 1.3234 |  |  | 2.9668
[13 empty] | C Non choked w/ reducers | 5 |  | 0.59282 |  |  | 9.7308 |  |  | 24.1556 |  |  | 49.0367 |  |  | 91.5605 |  |  | 168.6389 |  |  | 416.0518 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.53084 |  |  | 8.7069 |  |  | 21.5986 |  |  | 43.4842 |  |  | 78.9599 |  |  | 133.7208 |  |  | 221.7452 |  |  | 385.0343 |  |  | 617.5257 |  |  | 2487.9812
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.59282 |  |  | 9.7308 |  |  | 24.1556 |  |  | 49.0367 |  |  | 91.5605 |  |  | 168.6389 |  |  | 416.0518 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1372 | 112.3508 |  | 1.8692 | 1839.641 |  | 1.1556 | 4504.605 |  | 9.6367 | 8773.8208 |  | 30.5605 | 14719.742 |  | 80.4389 | 21483.8644 |  | 295.0518 | 28386.436 |  | 18000 | 34983.2149 |  | 18000 | 40614.4265 |  | 18000 | 47623.6092
[13 empty] | Next iteration flow rate |  |  | 114.5978 | Abs Value of | Flow this | 1858.0374 | Abs Value of | Flow this | 4549.6511 | Abs Value of | Flow this | 8861.5591 | Abs Value of | Flow this | 14866.9395 | Abs Value of | Flow this | 21698.703 | Abs Value of | Flow this | 28670.3003 | Abs Value of | Flow this | 35333.0471 | Abs Value of | Flow this | 41020.5707 | Abs Value of | Flow this | 48099.8452 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2298 |  |  | 90.1212 |  |  | 89.5766 |  |  | 87.7507 |  |  | 83.2514 |  |  | 75.3638 |  |  | 64.2763 |  |  | 50.8117 |  |  | 37.1 |  |  | 17.1793
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43472 |  |  | 0.4321 |  |  | 0.42329 |  |  | 0.40158 |  |  | 0.36354 |  |  | 0.31005 |  |  | 0.2451 |  |  | 0.17896 |  |  | 0.082869
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2298 |  |  | 30.1212 |  |  | 29.5766 |  |  | 27.7507 |  |  | 23.2514 |  |  | 15.3638 |  |  | 4.2763 |  |  | -9.1883 |  |  | -22.9 |  |  | -42.8207
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33423 |  |  | 0.33018 |  |  | 0.31624 |  |  | 0.27929 |  |  | 0.20386 |  |  | 0.06653 |  |  | -0.18083 |  |  | -0.61725 |  |  | -2.4926
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82597 |  |  | 0.82644 |  |  | 0.83142 |  |  | 0.8465 |  |  | 0.88124 |  |  | 0.9583 |  |  | 1.1267 |  |  | 1.3484 |  |  | 3.2057
[13 empty] | C Non choked w/ reducers | 5 |  | 0.60467 |  |  | 9.8285 |  |  | 24.4028 |  |  | 49.5723 |  |  | 92.7541 |  |  | 171.9241 |  |  | 444.2434 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.54145 |  |  | 8.7942 |  |  | 21.8177 |  |  | 43.9435 |  |  | 79.8812 |  |  | 135.583 |  |  | 225.7445 |  |  | 394.829 |  |  | 641.3003 |  |  | 2723.4049
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.60467 |  |  | 9.8285 |  |  | 24.4028 |  |  | 49.5723 |  |  | 92.7541 |  |  | 171.9241 |  |  | 444.2434 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1253 | 114.5978 |  | 1.7715 | 1858.0374 |  | 1.4028 | 4549.6511 |  | 10.1723 | 8861.5591 |  | 31.7541 | 14866.9395 |  | 83.7241 | 21698.703 |  | 323.2434 | 28670.3003 |  | 18000 | 35333.0471 |  | 18000 | 41020.5707 |  | 18000 | 48099.8452
[13 empty] | Next iteration flow rate |  |  | 116.8898 | Abs Value of | Flow this | 1876.6178 | Abs Value of | Flow this | 4595.1476 | Abs Value of | Flow this | 8950.1746 | Abs Value of | Flow this | 15015.6088 | Abs Value of | Flow this | 21915.6901 | Abs Value of | Flow this | 28957.0033 | Abs Value of | Flow this | 35686.3775 | Abs Value of | Flow this | 41430.7764 | Abs Value of | Flow this | 48580.8437 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2297 |  |  | 90.119 |  |  | 89.5635 |  |  | 87.7009 |  |  | 83.1111 |  |  | 75.065 |  |  | 63.7546 |  |  | 50.0193 |  |  | 36.032 |  |  | 15.711
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43471 |  |  | 0.43203 |  |  | 0.42305 |  |  | 0.40091 |  |  | 0.36209 |  |  | 0.30754 |  |  | 0.24128 |  |  | 0.17381 |  |  | 0.075786
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2297 |  |  | 30.119 |  |  | 29.5635 |  |  | 27.7009 |  |  | 23.1111 |  |  | 15.065 |  |  | 3.7546 |  |  | -9.9807 |  |  | -23.968 |  |  | -44.289
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33421 |  |  | 0.33008 |  |  | 0.31586 |  |  | 0.27807 |  |  | 0.20069 |  |  | 0.058891 |  |  | -0.19954 |  |  | -0.66518 |  |  | -2.819
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82598 |  |  | 0.82649 |  |  | 0.83163 |  |  | 0.84717 |  |  | 0.88308 |  |  | 0.96309 |  |  | 1.1398 |  |  | 1.3755 |  |  | 3.4945
[13 empty] | C Non choked w/ reducers | 5 |  | 0.61677 |  |  | 9.9271 |  |  | 24.6525 |  |  | 50.1148 |  |  | 93.9705 |  |  | 175.3384 |  |  | 478.4082 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.55228 |  |  | 8.8824 |  |  | 22.0391 |  |  | 44.4082 |  |  | 80.8162 |  |  | 137.484 |  |  | 229.8676 |  |  | 405.094 |  |  | 666.9102 |  |  | 3007.7097
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.61677 |  |  | 9.9271 |  |  | 24.6525 |  |  | 50.1148 |  |  | 93.9705 |  |  | 175.3384 |  |  | 478.4082 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1132 | 116.8898 |  | 1.6729 | 1876.6178 |  | 1.6525 | 4595.1476 |  | 10.7148 | 8950.1746 |  | 32.9705 | 15015.6088 |  | 87.1384 | 21915.6901 |  | 357.4082 | 28957.0033 |  | 18000 | 35686.3775 |  | 18000 | 41430.7764 |  | 18000 | 48580.8437
[13 empty] | Next iteration flow rate |  |  | 119.2276 | Abs Value of | Flow this | 1895.384 | Abs Value of | Flow this | 4641.0991 | Abs Value of | Flow this | 9039.6764 | Abs Value of | Flow this | 15165.7649 | Abs Value of | Flow this | 22134.847 | Abs Value of | Flow this | 29246.5734 | Abs Value of | Flow this | 36043.2413 | Abs Value of | Flow this | 41845.0842 | Abs Value of | Flow this | 49066.6521 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2297 |  |  | 90.1167 |  |  | 89.5501 |  |  | 87.65 |  |  | 82.968 |  |  | 74.7601 |  |  | 63.2224 |  |  | 49.2111 |  |  | 34.9427 |  |  | 14.2131
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.4347 |  |  | 0.43197 |  |  | 0.4228 |  |  | 0.40022 |  |  | 0.36062 |  |  | 0.30497 |  |  | 0.23738 |  |  | 0.16855 |  |  | 0.068561
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2297 |  |  | 30.1167 |  |  | 29.5501 |  |  | 27.65 |  |  | 22.968 |  |  | 14.7601 |  |  | 3.2224 |  |  | -10.7889 |  |  | -25.0573 |  |  | -45.7869
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.3342 |  |  | 0.32998 |  |  | 0.31546 |  |  | 0.27683 |  |  | 0.19743 |  |  | 0.05097 |  |  | -0.21924 |  |  | -0.7171 |  |  | -3.2215
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82599 |  |  | 0.82654 |  |  | 0.83184 |  |  | 0.84786 |  |  | 0.88498 |  |  | 0.96805 |  |  | 1.1536 |  |  | 1.4048 |  |  | 3.8507
[13 empty] | C Non choked w/ reducers | 5 |  | 0.6291 |  |  | 10.0268 |  |  | 24.905 |  |  | 50.6643 |  |  | 95.2106 |  |  | 178.8908 |  |  | 521.0704 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.56333 |  |  | 8.9714 |  |  | 22.2629 |  |  | 44.8783 |  |  | 81.7652 |  |  | 139.425 |  |  | 234.1205 |  |  | 415.8647 |  |  | 694.5791 |  |  | 3357.9211
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.6291 |  |  | 10.0268 |  |  | 24.905 |  |  | 50.6643 |  |  | 95.2106 |  |  | 178.8908 |  |  | 521.0704 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.1009 | 119.2276 |  | 1.5732 | 1895.384 |  | 1.905 | 4641.0991 |  | 11.2643 | 9039.6764 |  | 34.2106 | 15165.7649 |  | 90.6908 | 22134.847 |  | 400.0704 | 29246.5734 |  | 18000 | 36043.2413 |  | 18000 | 41845.0842 |  | 18000 | 49066.6521
[13 empty] | Next iteration flow rate |  |  | 121.6121 | Abs Value of | Flow this | 1914.3378 | Abs Value of | Flow this | 4687.5101 | Abs Value of | Flow this | 9130.0732 | Abs Value of | Flow this | 15317.4226 | Abs Value of | Flow this | 22356.1955 | Abs Value of | Flow this | 29539.0391 | Abs Value of | Flow this | 36403.6737 | Abs Value of | Flow this | 42263.535 | Abs Value of | Flow this | 49557.3187 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2297 |  |  | 90.1145 |  |  | 89.5364 |  |  | 87.5982 |  |  | 82.822 |  |  | 74.4492 |  |  | 62.6796 |  |  | 48.3866 |  |  | 33.8314 |  |  | 12.6852
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43469 |  |  | 0.4319 |  |  | 0.42255 |  |  | 0.39951 |  |  | 0.35912 |  |  | 0.30235 |  |  | 0.2334 |  |  | 0.16319 |  |  | 0.06119
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2297 |  |  | 30.1145 |  |  | 29.5364 |  |  | 27.5982 |  |  | 22.822 |  |  | 14.4492 |  |  | 2.6796 |  |  | -11.6134 |  |  | -26.1686 |  |  | -47.3148
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33418 |  |  | 0.32988 |  |  | 0.31505 |  |  | 0.27556 |  |  | 0.19408 |  |  | 0.042751 |  |  | -0.24001 |  |  | -0.7735 |  |  | -3.7299
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.826 |  |  | 0.8266 |  |  | 0.83206 |  |  | 0.84856 |  |  | 0.88693 |  |  | 0.97321 |  |  | 1.1682 |  |  | 1.4366 |  |  | 4.3006
[13 empty] | C Non choked w/ reducers | 5 |  | 0.64168 |  |  | 10.1275 |  |  | 25.1601 |  |  | 51.2208 |  |  | 96.475 |  |  | 182.5915 |  |  | 576.5593 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.5746 |  |  | 9.0614 |  |  | 22.4889 |  |  | 45.3539 |  |  | 82.7284 |  |  | 141.4074 |  |  | 238.5096 |  |  | 427.1803 |  |  | 724.5682 |  |  | 3800.0102
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.64168 |  |  | 10.1275 |  |  | 25.1601 |  |  | 51.2208 |  |  | 96.475 |  |  | 182.5915 |  |  | 576.5593 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0883 | 121.6121 |  | 1.4725 | 1914.3378 |  | 2.1601 | 4687.5101 |  | 11.8208 | 9130.0732 |  | 35.475 | 15317.4226 |  | 94.3915 | 22356.1955 |  | 455.5593 | 29539.0391 |  | 18000 | 36403.6737 |  | 18000 | 42263.535 |  | 18000 | 49557.3187
[13 empty] | Next iteration flow rate |  |  | 124.0444 | Abs Value of | Flow this | 1933.4812 | Abs Value of | Flow this | 4734.3852 | Abs Value of | Flow this | 9221.3739 | Abs Value of | Flow this | 15470.5968 | Abs Value of | Flow this | 22579.7574 | Abs Value of | Flow this | 29834.4295 | Abs Value of | Flow this | 36767.7105 | Abs Value of | Flow this | 42686.1704 | Abs Value of | Flow this | 50052.8918 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2297 |  |  | 90.1121 |  |  | 89.5225 |  |  | 87.5453 |  |  | 82.6731 |  |  | 74.132 |  |  | 62.1258 |  |  | 47.5456 |  |  | 32.6978 |  |  | 11.1265
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43468 |  |  | 0.43183 |  |  | 0.4223 |  |  | 0.39879 |  |  | 0.35759 |  |  | 0.29968 |  |  | 0.22935 |  |  | 0.15773 |  |  | 0.053672
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2297 |  |  | 30.1121 |  |  | 29.5225 |  |  | 27.5453 |  |  | 22.6731 |  |  | 14.132 |  |  | 2.1258 |  |  | -12.4544 |  |  | -27.3022 |  |  | -48.8735
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33416 |  |  | 0.32978 |  |  | 0.31464 |  |  | 0.27425 |  |  | 0.19063 |  |  | 0.034218 |  |  | -0.26195 |  |  | -0.83499 |  |  | -4.3925
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82601 |  |  | 0.82665 |  |  | 0.83228 |  |  | 0.84928 |  |  | 0.88894 |  |  | 0.97855 |  |  | 1.1836 |  |  | 1.4713 |  |  | 4.8869
[13 empty] | C Non choked w/ reducers | 5 |  | 0.65452 |  |  | 10.2292 |  |  | 25.418 |  |  | 51.7846 |  |  | 97.7646 |  |  | 186.4518 |  |  | 653.1051 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.58609 |  |  | 9.1522 |  |  | 22.7174 |  |  | 45.8351 |  |  | 83.7061 |  |  | 143.4325 |  |  | 243.042 |  |  | 439.0843 |  |  | 757.1856 |  |  | 4375.6566
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.65452 |  |  | 10.2292 |  |  | 25.418 |  |  | 51.7846 |  |  | 97.7646 |  |  | 186.4518 |  |  | 653.1051 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0755 | 124.0444 |  | 1.3708 | 1933.4812 |  | 2.418 | 4734.3852 |  | 12.3846 | 9221.3739 |  | 36.7646 | 15470.5968 |  | 98.2518 | 22579.7574 |  | 532.1051 | 29834.4295 |  | 18000 | 36767.7105 |  | 18000 | 42686.1704 |  | 18000 | 50052.8918
[13 empty] | Next iteration flow rate |  |  | 126.5252 | Abs Value of | Flow this | 1952.816 | Abs Value of | Flow this | 4781.729 | Abs Value of | Flow this | 9313.5876 | Abs Value of | Flow this | 15625.3028 | Abs Value of | Flow this | 22805.555 | Abs Value of | Flow this | 30132.7738 | Abs Value of | Flow this | 37135.3876 | Abs Value of | Flow this | 43113.0321 | Abs Value of | Flow this | 50553.4208 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2297 |  |  | 90.1098 |  |  | 89.5082 |  |  | 87.4913 |  |  | 82.5212 |  |  | 73.8084 |  |  | 61.5609 |  |  | 46.6876 |  |  | 31.5414 |  |  | 9.5365
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43467 |  |  | 0.43177 |  |  | 0.42204 |  |  | 0.39806 |  |  | 0.35603 |  |  | 0.29695 |  |  | 0.22521 |  |  | 0.15215 |  |  | 0.046002
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2297 |  |  | 30.1098 |  |  | 29.5082 |  |  | 27.4913 |  |  | 22.5212 |  |  | 13.8084 |  |  | 1.5609 |  |  | -13.3124 |  |  | -28.4586 |  |  | -50.4635
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33415 |  |  | 0.32967 |  |  | 0.31422 |  |  | 0.27291 |  |  | 0.18708 |  |  | 0.025356 |  |  | -0.28514 |  |  | -0.90226 |  |  | -5.2916
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82601 |  |  | 0.82671 |  |  | 0.8325 |  |  | 0.85001 |  |  | 0.89101 |  |  | 0.98411 |  |  | 1.1998 |  |  | 1.5093 |  |  | 5.6825
[13 empty] | C Non choked w/ reducers | 5 |  | 0.66761 |  |  | 10.3319 |  |  | 25.6787 |  |  | 52.3557 |  |  | 99.0801 |  |  | 190.4841 |  |  | 768.9576 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.59781 |  |  | 9.244 |  |  | 22.9482 |  |  | 46.322 |  |  | 84.6988 |  |  | 145.502 |  |  | 247.7249 |  |  | 451.6247 |  |  | 792.7957 |  |  | 5156.2419
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.66761 |  |  | 10.3319 |  |  | 25.6787 |  |  | 52.3557 |  |  | 99.0801 |  |  | 190.4841 |  |  | 768.9576 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0624 | 126.5252 |  | 1.2681 | 1952.816 |  | 2.6787 | 4781.729 |  | 12.9557 | 9313.5876 |  | 38.0801 | 15625.3028 |  | 102.2841 | 22805.555 |  | 647.9576 | 30132.7738 |  | 18000 | 37135.3876 |  | 18000 | 43113.0321 |  | 18000 | 50553.4208
[13 empty] | Next iteration flow rate |  |  | 129.0557 | Abs Value of | Flow this | 1972.3441 | Abs Value of | Flow this | 4829.5463 | Abs Value of | Flow this | 9406.7235 | Abs Value of | Flow this | 15781.5558 | Abs Value of | Flow this | 23033.6105 | Abs Value of | Flow this | 30434.1015 | Abs Value of | Flow this | 37506.7414 | Abs Value of | Flow this | 43544.1624 | Abs Value of | Flow this | 51058.955 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2297 |  |  | 90.1073 |  |  | 89.4937 |  |  | 87.4363 |  |  | 82.3663 |  |  | 73.4783 |  |  | 60.9847 |  |  | 45.8124 |  |  | 30.3617 |  |  | 7.9146
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43466 |  |  | 0.4317 |  |  | 0.42177 |  |  | 0.39731 |  |  | 0.35444 |  |  | 0.29417 |  |  | 0.22099 |  |  | 0.14646 |  |  | 0.038178
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2297 |  |  | 30.1073 |  |  | 29.4937 |  |  | 27.4363 |  |  | 22.3663 |  |  | 13.4783 |  |  | 0.98467 |  |  | -14.1876 |  |  | -29.6383 |  |  | -52.0854
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33413 |  |  | 0.32956 |  |  | 0.31379 |  |  | 0.27155 |  |  | 0.18343 |  |  | 0.016146 |  |  | -0.30969 |  |  | -0.97617 |  |  | -6.5809
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82602 |  |  | 0.82677 |  |  | 0.83273 |  |  | 0.85076 |  |  | 0.89314 |  |  | 0.98988 |  |  | 1.217 |  |  | 1.551 |  |  | 6.8235
[13 empty] | C Non choked w/ reducers | 5 |  | 0.68096 |  |  | 10.4356 |  |  | 25.9422 |  |  | 52.9343 |  |  | 100.4226 |  |  | 194.7025 |  |  | 976.723 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.60977 |  |  | 9.3367 |  |  | 23.1814 |  |  | 46.8147 |  |  | 85.7067 |  |  | 147.6171 |  |  | 252.5664 |  |  | 464.8551 |  |  | 831.8342 |  |  | 6275.0426
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.68096 |  |  | 10.4356 |  |  | 25.9422 |  |  | 52.9343 |  |  | 100.4226 |  |  | 194.7025 |  |  | 976.723 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.049 | 129.0557 |  | 1.1644 | 1972.3441 |  | 2.9422 | 4829.5463 |  | 13.5343 | 9406.7235 |  | 39.4226 | 15781.5558 |  | 106.5025 | 23033.6105 |  | 855.723 | 30434.1015 |  | 18000 | 37506.7414 |  | 18000 | 43544.1624 |  | 18000 | 51058.955
[13 empty] | Next iteration flow rate |  |  | 131.6369 | Abs Value of | Flow this | 1992.0676 | Abs Value of | Flow this | 4877.8418 | Abs Value of | Flow this | 9500.7907 | Abs Value of | Flow this | 15939.3714 | Abs Value of | Flow this | 23263.9466 | Abs Value of | Flow this | 30738.4425 | Abs Value of | Flow this | 37881.8088 | Abs Value of | Flow this | 43979.604 | Abs Value of | Flow this | 51569.5445 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2296 |  |  | 90.1049 |  |  | 89.4789 |  |  | 87.3801 |  |  | 82.2082 |  |  | 73.1416 |  |  | 60.3968 |  |  | 44.9196 |  |  | 29.1584 |  |  | 6.2601
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43464 |  |  | 0.43162 |  |  | 0.4215 |  |  | 0.39655 |  |  | 0.35282 |  |  | 0.29134 |  |  | 0.21668 |  |  | 0.14065 |  |  | 0.030197
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2296 |  |  | 30.1049 |  |  | 29.4789 |  |  | 27.3801 |  |  | 22.2082 |  |  | 13.1416 |  |  | 0.39683 |  |  | -15.0804 |  |  | -30.8416 |  |  | -53.7399
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33411 |  |  | 0.32945 |  |  | 0.31334 |  |  | 0.27015 |  |  | 0.17967 |  |  | 0.0065705 |  |  | -0.33572 |  |  | -1.0577 |  |  | -8.5846
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82603 |  |  | 0.82682 |  |  | 0.83297 |  |  | 0.85153 |  |  | 0.89533 |  |  | 0.99588 |  |  | 1.2353 |  |  | 1.597 |  |  | 8.5965
[13 empty] | C Non choked w/ reducers | 5 |  | 0.69458 |  |  | 10.5405 |  |  | 26.2085 |  |  | 53.5206 |  |  | 101.7928 |  |  | 199.1225 |  |  | 1552.0698 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.62196 |  |  | 9.4303 |  |  | 23.4171 |  |  | 47.3132 |  |  | 86.7302 |  |  | 149.7797 |  |  | 257.5748 |  |  | 478.8353 |  |  | 874.8254 |  |  | 8012.8836
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.69458 |  |  | 10.5405 |  |  | 26.2085 |  |  | 53.5206 |  |  | 101.7928 |  |  | 199.1225 |  |  | 1552.0698 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0354 | 131.6369 |  | 1.0595 | 1992.0676 |  | 3.2085 | 4877.8418 |  | 14.1206 | 9500.7907 |  | 40.7928 | 15939.3714 |  | 110.9225 | 23263.9466 |  | 1431.0698 | 30738.4425 |  | 18000 | 37881.8088 |  | 18000 | 43979.604 |  | 18000 | 51569.5445
[13 empty] | Next iteration flow rate |  |  | 134.2696 | Abs Value of | Flow this | 2011.9883 | Abs Value of | Flow this | 4926.6202 | Abs Value of | Flow this | 9595.7986 | Abs Value of | Flow this | 16098.7651 | Abs Value of | Flow this | 23496.5861 | Abs Value of | Flow this | 31045.827 | Abs Value of | Flow this | 38260.6269 | Abs Value of | Flow this | 44419.4001 | Abs Value of | Flow this | 52085.24 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2296 |  |  | 90.1024 |  |  | 89.4638 |  |  | 87.3228 |  |  | 82.047 |  |  | 72.7982 |  |  | 59.7972 |  |  | 44.0089 |  |  | 27.9308 |  |  | 4.5723
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43525 |  |  | 0.43463 |  |  | 0.43155 |  |  | 0.42122 |  |  | 0.39577 |  |  | 0.35116 |  |  | 0.28845 |  |  | 0.21229 |  |  | 0.13473 |  |  | 0.022055
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2296 |  |  | 30.1024 |  |  | 29.4638 |  |  | 27.3228 |  |  | 22.047 |  |  | 12.7982 |  |  | -0.20282 |  |  | -15.9911 |  |  | -32.0692 |  |  | -55.4277
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33409 |  |  | 0.32934 |  |  | 0.31289 |  |  | 0.26871 |  |  | 0.1758 |  |  | -0.0033917 |  |  | -0.36336 |  |  | -1.1482 |  |  | -12.1226
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82604 |  |  | 0.82688 |  |  | 0.83321 |  |  | 0.85232 |  |  | 0.89758 |  |  | 1.0021 |  |  | 1.2546 |  |  | 1.6481 |  |  | 11.7273
[13 empty] | C Non choked w/ reducers | 5 |  | 0.70847 |  |  | 10.6463 |  |  | 26.4777 |  |  | 54.1146 |  |  | 103.1918 |  |  | 203.7617 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.6344 |  |  | 9.5249 |  |  | 23.6553 |  |  | 47.8177 |  |  | 87.7697 |  |  | 151.9912 |  |  | 262.7594 |  |  | 493.632 |  |  | 922.4062 |  |  | 11080.4646
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.70847 |  |  | 10.6463 |  |  | 26.4777 |  |  | 54.1146 |  |  | 103.1918 |  |  | 203.7617 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0215 | 134.2696 |  | 0.95367 | 2011.9883 |  | 3.4777 | 4926.6202 |  | 14.7146 | 9595.7986 |  | 42.1918 | 16098.7651 |  | 115.5617 | 23496.5861 |  | 18000 | 31045.827 |  | 18000 | 38260.6269 |  | 18000 | 44419.4001 |  | 18000 | 52085.24
[13 empty] | Next iteration flow rate |  |  | 136.955 | Abs Value of | Flow this | 2032.1081 | Abs Value of | Flow this | 4975.8864 | Abs Value of | Flow this | 9691.7566 | Abs Value of | Flow this | 16259.7527 | Abs Value of | Flow this | 23731.552 | Abs Value of | Flow this | 31356.2852 | Abs Value of | Flow this | 38643.2332 | Abs Value of | Flow this | 44863.5941 | Abs Value of | Flow this | 52606.0924 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2296 |  |  | 90.0998 |  |  | 89.4484 |  |  | 87.2644 |  |  | 81.8825 |  |  | 72.4478 |  |  | 59.1855 |  |  | 43.0798 |  |  | 26.6786 |  |  | 2.8505
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43462 |  |  | 0.43148 |  |  | 0.42094 |  |  | 0.39498 |  |  | 0.34947 |  |  | 0.2855 |  |  | 0.20781 |  |  | 0.12869 |  |  | 0.01375
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2296 |  |  | 30.0998 |  |  | 29.4484 |  |  | 27.2644 |  |  | 21.8825 |  |  | 12.4478 |  |  | -0.81452 |  |  | -16.9202 |  |  | -33.3214 |  |  | -57.1495
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33407 |  |  | 0.32922 |  |  | 0.31243 |  |  | 0.26724 |  |  | 0.17182 |  |  | -0.013762 |  |  | -0.39276 |  |  | -1.249 |  |  | -20.0487
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82605 |  |  | 0.82695 |  |  | 0.83345 |  |  | 0.85313 |  |  | 0.8999 |  |  | 1.0086 |  |  | 1.2752 |  |  | 1.705 |  |  | 18.7411
[13 empty] | C Non choked w/ reducers | 5 |  | 0.72264 |  |  | 10.7533 |  |  | 26.7498 |  |  | 54.7165 |  |  | 104.6206 |  |  | 208.6398 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.64709 |  |  | 9.6204 |  |  | 23.8959 |  |  | 48.3282 |  |  | 88.8255 |  |  | 154.2536 |  |  | 268.1298 |  |  | 509.3203 |  |  | 975.3584 |  |  | 17950.8192
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.72264 |  |  | 10.7533 |  |  | 26.7498 |  |  | 54.7165 |  |  | 104.6206 |  |  | 208.6398 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0074 | 136.955 |  | 0.84672 | 2032.1081 |  | 3.7498 | 4975.8864 |  | 15.3165 | 9691.7566 |  | 43.6206 | 16259.7527 |  | 120.4398 | 23731.552 |  | 18000 | 31356.2852 |  | 18000 | 38643.2332 |  | 18000 | 44863.5941 |  | 18000 | 52606.0924
[13 empty] | Next iteration flow rate |  |  | 139.6941 | Abs Value of | Flow this | 2052.4292 | Abs Value of | Flow this | 5025.6453 | Abs Value of | Flow this | 9788.6742 | Abs Value of | Flow this | 16422.3503 | Abs Value of | Flow this | 23968.8675 | Abs Value of | Flow this | 31669.8481 | Abs Value of | Flow this | 39029.6655 | Abs Value of | Flow this | 45312.23 | Abs Value of | Flow this | 53132.1533 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2296 |  |  | 90.0972 |  |  | 89.4327 |  |  | 87.2048 |  |  | 81.7147 |  |  | 72.0903 |  |  | 58.5615 |  |  | 42.1321 |  |  | 25.4012 |  |  | 1.0942
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43461 |  |  | 0.4314 |  |  | 0.42065 |  |  | 0.39417 |  |  | 0.34775 |  |  | 0.28249 |  |  | 0.20323 |  |  | 0.12253 |  |  | 0.0052781
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2296 |  |  | 30.0972 |  |  | 29.4327 |  |  | 27.2048 |  |  | 21.7147 |  |  | 12.0903 |  |  | -1.4385 |  |  | -17.8679 |  |  | -34.5988 |  |  | -58.9058
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33405 |  |  | 0.3291 |  |  | 0.31196 |  |  | 0.26574 |  |  | 0.16771 |  |  | -0.024564 |  |  | -0.42409 |  |  | -1.3621 |  |  | -53.8348
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82606 |  |  | 0.82701 |  |  | 0.83371 |  |  | 0.85395 |  |  | 0.9023 |  |  | 1.0154 |  |  | 1.2972 |  |  | 1.7688 |  |  | 48.6384
[13 empty] | C Non choked w/ reducers | 5 |  | 0.7371 |  |  | 10.8613 |  |  | 27.0249 |  |  | 55.3264 |  |  | 106.0803 |  |  | 213.7795 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | C Choked w/ reducers | 5 |  | 0.66003 |  |  | 9.7169 |  |  | 24.1391 |  |  | 48.8449 |  |  | 89.8979 |  |  | 156.5686 |  |  | 273.6967 |  |  | 525.9848 |  |  | 1034.6517 |  |  | 47231.9241
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.7371 |  |  | 10.8613 |  |  | 27.0249 |  |  | 55.3264 |  |  | 106.0803 |  |  | 213.7795 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | #NUM!
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9929 | 139.6941 |  | 0.73869 | 2052.4292 |  | 4.0249 | 5025.6453 |  | 15.9264 | 9788.6742 |  | 45.0803 | 16422.3503 |  | 125.5795 | 23968.8675 |  | 18000 | 31669.8481 |  | 18000 | 39029.6655 |  | 18000 | 45312.23 |  | 18000 | 53132.1533
[13 empty] | Next iteration flow rate |  |  | 142.488 | Abs Value of | Flow this | 2072.9535 | Abs Value of | Flow this | 5075.9017 | Abs Value of | Flow this | 9886.5609 | Abs Value of | Flow this | 16586.5738 | Abs Value of | Flow this | 24208.5562 | Abs Value of | Flow this | 31986.5466 | Abs Value of | Flow this | 39419.9622 | Abs Value of | Flow this | 45765.3523 | Abs Value of | Flow this | 53663.4748 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2295 |  |  | 90.0945 |  |  | 89.4167 |  |  | 87.1439 |  |  | 81.5435 |  |  | 71.7257 |  |  | 57.9249 |  |  | 41.1653 |  |  | 24.0982 |  |  | -0.69744
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43459 |  |  | 0.43132 |  |  | 0.42036 |  |  | 0.39335 |  |  | 0.34599 |  |  | 0.27942 |  |  | 0.19857 |  |  | 0.11624 |  |  | -0.0033643
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2295 |  |  | 30.0945 |  |  | 29.4167 |  |  | 27.1439 |  |  | 21.5435 |  |  | 11.7257 |  |  | -2.0751 |  |  | -18.8347 |  |  | -35.9018 |  |  | -60.6974
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33403 |  |  | 0.32898 |  |  | 0.31148 |  |  | 0.2642 |  |  | 0.16348 |  |  | -0.035823 |  |  | -0.45754 |  |  | -1.4898 |  |  | 87.0293
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82607 |  |  | 0.82707 |  |  | 0.83396 |  |  | 0.8548 |  |  | 0.90476 |  |  | 1.0225 |  |  | 1.3206 |  |  | 1.8409 |  |  | -76.0123
[13 empty] | C Non choked w/ reducers | 5 |  | 0.75184 |  |  | 10.9704 |  |  | 27.3029 |  |  | 55.9446 |  |  | 107.572 |  |  | 219.2064 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -43.2064
[13 empty] | C Choked w/ reducers | 5 |  | 0.67323 |  |  | 9.8143 |  |  | 24.3849 |  |  | 49.3678 |  |  | 90.9875 |  |  | 158.9381 |  |  | 279.4714 |  |  | 543.721 |  |  | 1101.5045 |  |  | 74842.3093
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.75184 |  |  | 10.9704 |  |  | 27.3029 |  |  | 55.9446 |  |  | 107.572 |  |  | 219.2064 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 74842.3093
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9782 | 142.488 |  | 0.62956 | 2072.9535 |  | 4.3029 | 5075.9017 |  | 16.5446 | 9886.5609 |  | 46.572 | 16586.5738 |  | 131.0064 | 24208.5562 |  | 18000 | 31986.5466 |  | 18000 | 39419.9622 |  | 18000 | 45765.3523 |  | 18000 | 53663.4748
[13 empty] | Next iteration flow rate |  |  | 145.3377 | Abs Value of | Flow this | 2093.6831 | Abs Value of | Flow this | 5126.6607 | Abs Value of | Flow this | 9985.4265 | Abs Value of | Flow this | 16752.4395 | Abs Value of | Flow this | 24450.6417 | Abs Value of | Flow this | 32306.412 | Abs Value of | Flow this | 39814.1618 | Abs Value of | Flow this | 46223.0059 | Abs Value of | Flow this | 54200.1096 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2295 |  |  | 90.0918 |  |  | 89.4003 |  |  | 87.0819 |  |  | 81.3689 |  |  | 71.3538 |  |  | 57.2756 |  |  | 40.1791 |  |  | 22.7689 |  |  | -2.5251
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43458 |  |  | 0.43124 |  |  | 0.42006 |  |  | 0.3925 |  |  | 0.34419 |  |  | 0.27628 |  |  | 0.19381 |  |  | 0.10983 |  |  | -0.01218
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2295 |  |  | 30.0918 |  |  | 29.4003 |  |  | 27.0819 |  |  | 21.3689 |  |  | 11.3538 |  |  | -2.7244 |  |  | -19.8209 |  |  | -37.2311 |  |  | -62.5251
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33401 |  |  | 0.32886 |  |  | 0.31099 |  |  | 0.26262 |  |  | 0.15912 |  |  | -0.047566 |  |  | -0.49331 |  |  | -1.6352 |  |  | 24.7616
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82608 |  |  | 0.82713 |  |  | 0.83422 |  |  | 0.85567 |  |  | 0.9073 |  |  | 1.0298 |  |  | 1.3457 |  |  | 1.923 |  |  | -20.9116
[13 empty] | C Non choked w/ reducers | 5 |  | 0.76688 |  |  | 11.0807 |  |  | 27.584 |  |  | 56.5711 |  |  | 109.097 |  |  | 224.9497 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -82.1372
[13 empty] | C Choked w/ reducers | 5 |  | 0.6867 |  |  | 9.9128 |  |  | 24.6333 |  |  | 49.897 |  |  | 92.0946 |  |  | 161.3642 |  |  | 285.4662 |  |  | 562.6374 |  |  | 1177.4687 |  |  | 20878.4411
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.76688 |  |  | 11.0807 |  |  | 27.584 |  |  | 56.5711 |  |  | 109.097 |  |  | 224.9497 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 20878.4411
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9631 | 145.3377 |  | 0.51933 | 2093.6831 |  | 4.584 | 5126.6607 |  | 17.1711 | 9985.4265 |  | 48.097 | 16752.4395 |  | 136.7497 | 24450.6417 |  | 18000 | 32306.412 |  | 18000 | 39814.1618 |  | 18000 | 46223.0059 |  | 18000 | 54200.1096
[13 empty] | Next iteration flow rate |  |  | 148.2445 | Abs Value of | Flow this | 2114.6199 | Abs Value of | Flow this | 5177.9273 | Abs Value of | Flow this | 10085.2808 | Abs Value of | Flow this | 16919.9639 | Abs Value of | Flow this | 24695.1481 | Abs Value of | Flow this | 32629.4762 | Abs Value of | Flow this | 40212.3034 | Abs Value of | Flow this | 46685.2359 | Abs Value of | Flow this | 54742.1107 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2295 |  |  | 90.089 |  |  | 89.3836 |  |  | 87.0186 |  |  | 81.1908 |  |  | 70.9744 |  |  | 56.6132 |  |  | 39.1731 |  |  | 21.4129 |  |  | -4.3895
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43457 |  |  | 0.43116 |  |  | 0.41976 |  |  | 0.39164 |  |  | 0.34236 |  |  | 0.27309 |  |  | 0.18896 |  |  | 0.10329 |  |  | -0.021174
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2295 |  |  | 30.089 |  |  | 29.3836 |  |  | 27.0186 |  |  | 21.1908 |  |  | 10.9744 |  |  | -3.3868 |  |  | -20.8269 |  |  | -38.5871 |  |  | -64.3895
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33399 |  |  | 0.32874 |  |  | 0.31049 |  |  | 0.261 |  |  | 0.15462 |  |  | -0.059823 |  |  | -0.53166 |  |  | -1.802 |  |  | 14.6691
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82609 |  |  | 0.8272 |  |  | 0.83449 |  |  | 0.85656 |  |  | 0.90992 |  |  | 1.0375 |  |  | 1.3726 |  |  | 2.0172 |  |  | -11.9807
[13 empty] | C Non choked w/ reducers | 5 |  | 0.78221 |  |  | 11.192 |  |  | 27.8681 |  |  | 57.2062 |  |  | 110.6564 |  |  | 231.0433 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -108.2225
[13 empty] | C Choked w/ reducers | 5 |  | 0.70043 |  |  | 10.0122 |  |  | 24.8842 |  |  | 50.4326 |  |  | 93.2196 |  |  | 163.8491 |  |  | 291.6943 |  |  | 582.8577 |  |  | 1264.5521 |  |  | 12130.636
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.78221 |  |  | 11.192 |  |  | 27.8681 |  |  | 57.2062 |  |  | 110.6564 |  |  | 231.0433 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 12130.636
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9478 | 148.2445 |  | 0.40798 | 2114.6199 |  | 4.8681 | 5177.9273 |  | 17.8062 | 10085.2808 |  | 49.6564 | 16919.9639 |  | 142.8433 | 24695.1481 |  | 18000 | 32629.4762 |  | 18000 | 40212.3034 |  | 18000 | 46685.2359 |  | 18000 | 54742.1107
[13 empty] | Next iteration flow rate |  |  | 151.2094 | Abs Value of | Flow this | 2135.7661 | Abs Value of | Flow this | 5229.7066 | Abs Value of | Flow this | 10186.1336 | Abs Value of | Flow this | 17089.1635 | Abs Value of | Flow this | 24942.0996 | Abs Value of | Flow this | 32955.7709 | Abs Value of | Flow this | 40614.4265 | Abs Value of | Flow this | 47152.0883 | Abs Value of | Flow this | 55289.5318 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2295 |  |  | 90.0862 |  |  | 89.3666 |  |  | 86.9541 |  |  | 81.0091 |  |  | 70.5873 |  |  | 55.9375 |  |  | 38.1468 |  |  | 20.0297 |  |  | -6.2913
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43455 |  |  | 0.43108 |  |  | 0.41944 |  |  | 0.39077 |  |  | 0.3405 |  |  | 0.26983 |  |  | 0.18401 |  |  | 0.096618 |  |  | -0.030348
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2295 |  |  | 30.0862 |  |  | 29.3666 |  |  | 26.9541 |  |  | 21.0091 |  |  | 10.5873 |  |  | -4.0625 |  |  | -21.8532 |  |  | -39.9703 |  |  | -66.2913
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33397 |  |  | 0.32861 |  |  | 0.30998 |  |  | 0.25934 |  |  | 0.14999 |  |  | -0.072625 |  |  | -0.57287 |  |  | -1.9956 |  |  | 10.537
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82611 |  |  | 0.82727 |  |  | 0.83476 |  |  | 0.85747 |  |  | 0.91262 |  |  | 1.0455 |  |  | 1.4015 |  |  | 2.1264 |  |  | -8.3242
[13 empty] | C Non choked w/ reducers | 5 |  | 0.79786 |  |  | 11.3045 |  |  | 28.1553 |  |  | 57.8499 |  |  | 112.2516 |  |  | 237.5263 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -129.5074
[13 empty] | C Choked w/ reducers | 5 |  | 0.71444 |  |  | 10.1126 |  |  | 25.1379 |  |  | 50.9747 |  |  | 94.3629 |  |  | 166.395 |  |  | 298.17 |  |  | 604.5234 |  |  | 1365.3994 |  |  | 8548.2007
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.79786 |  |  | 11.3045 |  |  | 28.1553 |  |  | 57.8499 |  |  | 112.2516 |  |  | 237.5263 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 8548.2007
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9321 | 151.2094 |  | 0.2955 | 2135.7661 |  | 5.1553 | 5229.7066 |  | 18.4499 | 10186.1336 |  | 51.2516 | 17089.1635 |  | 149.3263 | 24942.0996 |  | 18000 | 32955.7709 |  | 18000 | 40614.4265 |  | 18000 | 47152.0883 |  | 18000 | 55289.5318
[13 empty] | Next iteration flow rate |  |  | 154.2336 | Abs Value of | Flow this | 2157.1237 | Abs Value of | Flow this | 5282.0037 | Abs Value of | Flow this | 10287.995 | Abs Value of | Flow this | 17260.0552 | Abs Value of | Flow this | 25191.5206 | Abs Value of | Flow this | 33285.3286 | Abs Value of | Flow this | 41020.5707 | Abs Value of | Flow this | 47623.6092 | Abs Value of | Flow this | 55842.4271 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2294 |  |  | 90.0833 |  |  | 89.3493 |  |  | 86.8882 |  |  | 80.8238 |  |  | 70.1925 |  |  | 55.2482 |  |  | 37.1 |  |  | 18.6187 |  |  | -8.2314
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43454 |  |  | 0.431 |  |  | 0.41913 |  |  | 0.38987 |  |  | 0.33859 |  |  | 0.2665 |  |  | 0.17896 |  |  | 0.089812 |  |  | -0.039706
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2294 |  |  | 30.0833 |  |  | 29.3493 |  |  | 26.8882 |  |  | 20.8238 |  |  | 10.1925 |  |  | -4.7518 |  |  | -22.9 |  |  | -41.3813 |  |  | -68.2314
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33395 |  |  | 0.32848 |  |  | 0.30946 |  |  | 0.25764 |  |  | 0.14521 |  |  | -0.086008 |  |  | -0.61725 |  |  | -2.2226 |  |  | 8.2892
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82612 |  |  | 0.82734 |  |  | 0.83504 |  |  | 0.8584 |  |  | 0.91541 |  |  | 1.0539 |  |  | 1.4326 |  |  | 2.2545 |  |  | -6.3351
[13 empty] | C Non choked w/ reducers | 5 |  | 0.81382 |  |  | 11.4181 |  |  | 28.4457 |  |  | 58.5026 |  |  | 113.884 |  |  | 244.4445 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -148.1064
[13 empty] | C Choked w/ reducers | 5 |  | 0.72873 |  |  | 10.2141 |  |  | 25.3942 |  |  | 51.5235 |  |  | 95.5251 |  |  | 169.0043 |  |  | 304.9089 |  |  | 627.7975 |  |  | 1483.566 |  |  | 6598.7854
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.81382 |  |  | 11.4181 |  |  | 28.4457 |  |  | 58.5026 |  |  | 113.884 |  |  | 244.4445 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 6598.7854
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.9162 | 154.2336 |  | 0.18187 | 2157.1237 |  | 5.4457 | 5282.0037 |  | 19.1026 | 10287.995 |  | 52.884 | 17260.0552 |  | 156.2445 | 25191.5206 |  | 18000 | 33285.3286 |  | 18000 | 41020.5707 |  | 18000 | 47623.6092 |  | 18000 | 55842.4271
[13 empty] | Next iteration flow rate |  |  | 157.3182 | Abs Value of | Flow this | 2178.695 | Abs Value of | Flow this | 5334.8237 | Abs Value of | Flow this | 10390.8749 | Abs Value of | Flow this | 17432.6557 | Abs Value of | Flow this | 25443.4358 | Abs Value of | Flow this | 33618.1819 | Abs Value of | Flow this | 41430.7764 | Abs Value of | Flow this | 48099.8452 | Abs Value of | Flow this | 56400.8514 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2294 |  |  | 90.0803 |  |  | 89.3316 |  |  | 86.8211 |  |  | 80.6347 |  |  | 69.7898 |  |  | 54.5451 |  |  | 36.032 |  |  | 17.1793 |  |  | -10.2105
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43452 |  |  | 0.43091 |  |  | 0.4188 |  |  | 0.38896 |  |  | 0.33665 |  |  | 0.26311 |  |  | 0.17381 |  |  | 0.082869 |  |  | -0.049253
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2294 |  |  | 30.0803 |  |  | 29.3316 |  |  | 26.8211 |  |  | 20.6347 |  |  | 9.7898 |  |  | -5.4549 |  |  | -23.968 |  |  | -42.8207 |  |  | -70.2105
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33393 |  |  | 0.32834 |  |  | 0.30892 |  |  | 0.2559 |  |  | 0.14028 |  |  | -0.10001 |  |  | -0.66518 |  |  | -2.4926 |  |  | 6.8763
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82613 |  |  | 0.82741 |  |  | 0.83533 |  |  | 0.85936 |  |  | 0.91828 |  |  | 1.0627 |  |  | 1.4661 |  |  | 2.4069 |  |  | -5.0849
[13 empty] | C Non choked w/ reducers | 5 |  | 0.83009 |  |  | 11.5329 |  |  | 28.7392 |  |  | 59.1642 |  |  | 115.5553 |  |  | 251.8515 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -164.9582
[13 empty] | C Choked w/ reducers | 5 |  | 0.7433 |  |  | 10.3166 |  |  | 25.6532 |  |  | 52.079 |  |  | 96.7066 |  |  | 171.6794 |  |  | 311.9279 |  |  | 652.8682 |  |  | 1623.9474 |  |  | 5372.9528
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.83009 |  |  | 11.5329 |  |  | 28.7392 |  |  | 59.1642 |  |  | 115.5553 |  |  | 251.8515 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 5372.9528
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8999 | 157.3182 |  | 0.067094 | 2178.695 |  | 5.7392 | 5334.8237 |  | 19.7642 | 10390.8749 |  | 54.5553 | 17432.6557 |  | 163.6515 | 25443.4358 |  | 18000 | 33618.1819 |  | 18000 | 41430.7764 |  | 18000 | 48099.8452 |  | 18000 | 56400.8514
[13 empty] | Next iteration flow rate |  |  | 160.4646 | Abs Value of | Flow this | 2200.4819 | Abs Value of | Flow this | 5388.172 | Abs Value of | Flow this | 10494.7837 | Abs Value of | Flow this | 17606.9823 | Abs Value of | Flow this | 25697.8702 | Abs Value of | Flow this | 33954.3637 | Abs Value of | Flow this | 41845.0842 | Abs Value of | Flow this | 48580.8437 | Abs Value of | Flow this | 56964.8599 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2294 |  |  | 90.0773 |  |  | 89.3135 |  |  | 86.7525 |  |  | 80.4419 |  |  | 69.3789 |  |  | 53.8278 |  |  | 34.9427 |  |  | 15.711 |  |  | -12.2293
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43451 |  |  | 0.43083 |  |  | 0.41847 |  |  | 0.38803 |  |  | 0.33467 |  |  | 0.25965 |  |  | 0.16855 |  |  | 0.075786 |  |  | -0.058991
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2294 |  |  | 30.0773 |  |  | 29.3135 |  |  | 26.7525 |  |  | 20.4419 |  |  | 9.3789 |  |  | -6.1722 |  |  | -25.0573 |  |  | -44.289 |  |  | -72.2293
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33391 |  |  | 0.32821 |  |  | 0.30838 |  |  | 0.25412 |  |  | 0.13518 |  |  | -0.11467 |  |  | -0.7171 |  |  | -2.819 |  |  | 5.9062
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82614 |  |  | 0.82748 |  |  | 0.83562 |  |  | 0.86034 |  |  | 0.92125 |  |  | 1.0719 |  |  | 1.5025 |  |  | 2.5912 |  |  | -4.2264
[13 empty] | C Non choked w/ reducers | 5 |  | 0.84669 |  |  | 11.6489 |  |  | 29.036 |  |  | 59.8352 |  |  | 117.2668 |  |  | 259.811 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -180.5785
[13 empty] | C Choked w/ reducers | 5 |  | 0.75817 |  |  | 10.4201 |  |  | 25.915 |  |  | 52.6413 |  |  | 97.9078 |  |  | 174.423 |  |  | 319.2452 |  |  | 679.9544 |  |  | 1793.4764 |  |  | 4530.8284
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.84669 |  |  | 11.6489 |  |  | 29.036 |  |  | 59.8352 |  |  | 117.2668 |  |  | 259.811 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 4530.8284
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8833 | 160.4646 |  | 0.04885 | 2200.4819 |  | 6.036 | 5388.172 |  | 20.4352 | 10494.7837 |  | 56.2668 | 17606.9823 |  | 171.611 | 25697.8702 |  | 18000 | 33954.3637 |  | 18000 | 41845.0842 |  | 18000 | 48580.8437 |  | 18000 | 56964.8599
[13 empty] | Next iteration flow rate |  |  | 163.6739 | Abs Value of | Flow this | 2222.4867 | Abs Value of | Flow this | 5442.0537 | Abs Value of | Flow this | 10599.7315 | Abs Value of | Flow this | 17783.0521 | Abs Value of | Flow this | 25954.8489 | Abs Value of | Flow this | 34293.9074 | Abs Value of | Flow this | 42263.535 | Abs Value of | Flow this | 49066.6521 | Abs Value of | Flow this | 57534.5085 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2293 |  |  | 90.0742 |  |  | 89.2951 |  |  | 86.6826 |  |  | 80.2451 |  |  | 68.9598 |  |  | 53.0961 |  |  | 33.8314 |  |  | 14.2131 |  |  | -14.2888
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.4345 |  |  | 0.43074 |  |  | 0.41814 |  |  | 0.38708 |  |  | 0.33264 |  |  | 0.25612 |  |  | 0.16319 |  |  | 0.068561 |  |  | -0.068925
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2293 |  |  | 30.0742 |  |  | 29.2951 |  |  | 26.6826 |  |  | 20.2451 |  |  | 8.9598 |  |  | -6.9039 |  |  | -26.1686 |  |  | -45.7869 |  |  | -74.2888
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33388 |  |  | 0.32807 |  |  | 0.30782 |  |  | 0.25229 |  |  | 0.12993 |  |  | -0.13003 |  |  | -0.7735 |  |  | -3.2215 |  |  | 5.1991
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82615 |  |  | 0.82755 |  |  | 0.83591 |  |  | 0.86134 |  |  | 0.92431 |  |  | 1.0815 |  |  | 1.542 |  |  | 2.8184 |  |  | -3.6007
[13 empty] | C Non choked w/ reducers | 5 |  | 0.86363 |  |  | 11.766 |  |  | 29.336 |  |  | 60.5155 |  |  | 119.0203 |  |  | 268.3988 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -195.2877
[13 empty] | C Choked w/ reducers | 5 |  | 0.77333 |  |  | 10.5247 |  |  | 26.1795 |  |  | 53.2106 |  |  | 99.1294 |  |  | 177.2379 |  |  | 326.881 |  |  | 709.3122 |  |  | 2002.3051 |  |  | 3916.5795
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.86363 |  |  | 11.766 |  |  | 29.336 |  |  | 60.5155 |  |  | 119.0203 |  |  | 268.3988 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 3916.5795
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8664 | 163.6739 |  | 0.16597 | 2222.4867 |  | 6.336 | 5442.0537 |  | 21.1155 | 10599.7315 |  | 58.0203 | 17783.0521 |  | 180.1988 | 25954.8489 |  | 18000 | 34293.9074 |  | 18000 | 42263.535 |  | 18000 | 49066.6521 |  | 18000 | 57534.5085
[13 empty] | Next iteration flow rate |  |  | 166.9474 | Abs Value of | Flow this | 2244.7116 | Abs Value of | Flow this | 5496.4742 | Abs Value of | Flow this | 10705.7288 | Abs Value of | Flow this | 17960.8826 | Abs Value of | Flow this | 26214.3974 | Abs Value of | Flow this | 34636.8464 | Abs Value of | Flow this | 42686.1704 | Abs Value of | Flow this | 49557.3187 | Abs Value of | Flow this | 58109.8536 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2293 |  |  | 90.0711 |  |  | 89.2763 |  |  | 86.6113 |  |  | 80.0444 |  |  | 68.5323 |  |  | 52.3497 |  |  | 32.6978 |  |  | 12.6852 |  |  | -16.3896
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43448 |  |  | 0.43065 |  |  | 0.41779 |  |  | 0.38611 |  |  | 0.33058 |  |  | 0.25252 |  |  | 0.15773 |  |  | 0.06119 |  |  | -0.079059
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2293 |  |  | 30.0711 |  |  | 29.2763 |  |  | 26.6113 |  |  | 20.0444 |  |  | 8.5323 |  |  | -7.6503 |  |  | -27.3022 |  |  | -47.3148 |  |  | -76.3896
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33386 |  |  | 0.32793 |  |  | 0.30725 |  |  | 0.25042 |  |  | 0.1245 |  |  | -0.14614 |  |  | -0.83499 |  |  | -3.7299 |  |  | 4.6609
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82616 |  |  | 0.82763 |  |  | 0.83622 |  |  | 0.86237 |  |  | 0.92747 |  |  | 1.0916 |  |  | 1.5851 |  |  | 3.1054 |  |  | -3.1244
[13 empty] | C Non choked w/ reducers | 5 |  | 0.8809 |  |  | 11.8843 |  |  | 29.6394 |  |  | 61.2054 |  |  | 120.8177 |  |  | 277.7066 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -209.302
[13 empty] | C Choked w/ reducers | 5 |  | 0.7888 |  |  | 10.6303 |  |  | 26.4469 |  |  | 53.787 |  |  | 100.3717 |  |  | 180.1271 |  |  | 334.857 |  |  | 741.2427 |  |  | 2265.9197 |  |  | 3448.6951
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.8809 |  |  | 11.8843 |  |  | 29.6394 |  |  | 61.2054 |  |  | 120.8177 |  |  | 277.7066 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 3448.6951
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8491 | 166.9474 |  | 0.28428 | 2244.7116 |  | 6.6394 | 5496.4742 |  | 21.8054 | 10705.7288 |  | 59.8177 | 17960.8826 |  | 189.5066 | 26214.3974 |  | 18000 | 34636.8464 |  | 18000 | 42686.1704 |  | 18000 | 49557.3187 |  | 18000 | 58109.8536
[13 empty] | Next iteration flow rate |  |  | 170.2863 | Abs Value of | Flow this | 2267.1587 | Abs Value of | Flow this | 5551.439 | Abs Value of | Flow this | 10812.7861 | Abs Value of | Flow this | 18140.4914 | Abs Value of | Flow this | 26476.5413 | Abs Value of | Flow this | 34983.2149 | Abs Value of | Flow this | 43113.0321 | Abs Value of | Flow this | 50052.8918 | Abs Value of | Flow this | 58690.9521 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2293 |  |  | 90.0679 |  |  | 89.2571 |  |  | 86.5386 |  |  | 79.8397 |  |  | 68.0961 |  |  | 51.5884 |  |  | 31.5414 |  |  | 11.1265 |  |  | -18.5327
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43446 |  |  | 0.43055 |  |  | 0.41744 |  |  | 0.38513 |  |  | 0.32848 |  |  | 0.24885 |  |  | 0.15215 |  |  | 0.053672 |  |  | -0.089397
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2293 |  |  | 30.0679 |  |  | 29.2571 |  |  | 26.5386 |  |  | 19.8397 |  |  | 8.0961 |  |  | -8.4116 |  |  | -28.4586 |  |  | -48.8735 |  |  | -78.5327
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33384 |  |  | 0.32778 |  |  | 0.30667 |  |  | 0.24849 |  |  | 0.11889 |  |  | -0.16305 |  |  | -0.90226 |  |  | -4.3925 |  |  | 4.2375
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82618 |  |  | 0.8277 |  |  | 0.83653 |  |  | 0.86343 |  |  | 0.93074 |  |  | 1.1022 |  |  | 1.6323 |  |  | 3.4794 |  |  | -2.7498
[13 empty] | C Non choked w/ reducers | 5 |  | 0.89852 |  |  | 12.0038 |  |  | 29.946 |  |  | 61.9052 |  |  | 122.6608 |  |  | 287.846 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -222.776
[13 empty] | C Choked w/ reducers | 5 |  | 0.80458 |  |  | 10.737 |  |  | 26.7171 |  |  | 54.3705 |  |  | 101.6354 |  |  | 183.0935 |  |  | 343.1972 |  |  | 776.1031 |  |  | 2609.1737 |  |  | 3080.398
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.89852 |  |  | 12.0038 |  |  | 29.946 |  |  | 61.9052 |  |  | 122.6608 |  |  | 287.846 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 3080.398
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8315 | 170.2863 |  | 0.4038 | 2267.1587 |  | 6.946 | 5551.439 |  | 22.5052 | 10812.7861 |  | 61.6608 | 18140.4914 |  | 199.646 | 26476.5413 |  | 18000 | 34983.2149 |  | 18000 | 43113.0321 |  | 18000 | 50052.8918 |  | 18000 | 58690.9521
[13 empty] | Next iteration flow rate |  |  | 173.692 | Abs Value of | Flow this | 2289.8303 | Abs Value of | Flow this | 5606.9533 | Abs Value of | Flow this | 10920.914 | Abs Value of | Flow this | 18321.8964 | Abs Value of | Flow this | 26741.3068 | Abs Value of | Flow this | 35333.0471 | Abs Value of | Flow this | 43544.1624 | Abs Value of | Flow this | 50553.4208 | Abs Value of | Flow this | 59277.8616 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2292 |  |  | 90.0646 |  |  | 89.2375 |  |  | 86.4644 |  |  | 79.6308 |  |  | 67.6512 |  |  | 50.8117 |  |  | 30.3617 |  |  | 9.5365 |  |  | -20.7188
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43445 |  |  | 0.43046 |  |  | 0.41708 |  |  | 0.38412 |  |  | 0.32633 |  |  | 0.2451 |  |  | 0.14646 |  |  | 0.046002 |  |  | -0.099942
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2292 |  |  | 30.0646 |  |  | 29.2375 |  |  | 26.4644 |  |  | 19.6308 |  |  | 7.6512 |  |  | -9.1883 |  |  | -29.6383 |  |  | -50.4635 |  |  | -80.7188
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33381 |  |  | 0.32764 |  |  | 0.30607 |  |  | 0.24652 |  |  | 0.1131 |  |  | -0.18083 |  |  | -0.97617 |  |  | -5.2916 |  |  | 3.8959
[13 empty] | Expansion factor | 12 |  | 0.82551 |  |  | 0.82619 |  |  | 0.82778 |  |  | 0.83685 |  |  | 0.86451 |  |  | 0.93411 |  |  | 1.1133 |  |  | 1.6841 |  |  | 3.9869 |  |  | -2.4475
[13 empty] | C Non choked w/ reducers | 5 |  | 0.91649 |  |  | 12.1245 |  |  | 30.2561 |  |  | 62.6149 |  |  | 124.5516 |  |  | 298.9548 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -235.8254
[13 empty] | C Choked w/ reducers | 5 |  | 0.82067 |  |  | 10.8447 |  |  | 26.9902 |  |  | 54.9613 |  |  | 102.921 |  |  | 186.1406 |  |  | 351.9277 |  |  | 814.3197 |  |  | 3074.6313 |  |  | 2782.925
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.91649 |  |  | 12.1245 |  |  | 30.2561 |  |  | 62.6149 |  |  | 124.5516 |  |  | 298.9548 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 2782.925
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8135 | 173.692 |  | 0.52453 | 2289.8303 |  | 7.2561 | 5606.9533 |  | 23.2149 | 10920.914 |  | 63.5516 | 18321.8964 |  | 210.7548 | 26741.3068 |  | 18000 | 35333.0471 |  | 18000 | 43544.1624 |  | 18000 | 50553.4208 |  | 18000 | 59277.8616
[13 empty] | Next iteration flow rate |  |  | 177.1659 | Abs Value of | Flow this | 2312.7286 | Abs Value of | Flow this | 5663.0229 | Abs Value of | Flow this | 11030.1231 | Abs Value of | Flow this | 18505.1153 | Abs Value of | Flow this | 27008.7198 | Abs Value of | Flow this | 35686.3775 | Abs Value of | Flow this | 43979.604 | Abs Value of | Flow this | 51058.955 | Abs Value of | Flow this | 59870.6402 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2292 |  |  | 90.0613 |  |  | 89.2176 |  |  | 86.3887 |  |  | 79.4178 |  |  | 67.1974 |  |  | 50.0193 |  |  | 29.1584 |  |  | 7.9146 |  |  | -22.9489
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43443 |  |  | 0.43036 |  |  | 0.41672 |  |  | 0.38309 |  |  | 0.32414 |  |  | 0.24128 |  |  | 0.14065 |  |  | 0.038178 |  |  | -0.1107
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2292 |  |  | 30.0613 |  |  | 29.2176 |  |  | 26.3887 |  |  | 19.4178 |  |  | 7.1974 |  |  | -9.9807 |  |  | -30.8416 |  |  | -52.0854 |  |  | -82.9489
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33379 |  |  | 0.32749 |  |  | 0.30546 |  |  | 0.2445 |  |  | 0.10711 |  |  | -0.19954 |  |  | -1.0577 |  |  | -6.5809 |  |  | 3.6145
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.8262 |  |  | 0.82786 |  |  | 0.83717 |  |  | 0.86562 |  |  | 0.9376 |  |  | 1.1251 |  |  | 1.7412 |  |  | 4.7146 |  |  | -2.1985
[13 empty] | C Non choked w/ reducers | 5 |  | 0.93482 |  |  | 12.2465 |  |  | 30.5696 |  |  | 63.3349 |  |  | 126.4923 |  |  | 311.2055 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -248.5401
[13 empty] | C Choked w/ reducers | 5 |  | 0.83708 |  |  | 10.9536 |  |  | 27.2662 |  |  | 55.5596 |  |  | 104.229 |  |  | 189.2717 |  |  | 361.0773 |  |  | 856.4056 |  |  | 3741.7644 |  |  | 2537.617
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.93482 |  |  | 12.2465 |  |  | 30.5696 |  |  | 63.3349 |  |  | 126.4923 |  |  | 311.2055 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 2537.617
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7952 | 177.1659 |  | 0.64649 | 2312.7286 |  | 7.5696 | 5663.0229 |  | 23.9349 | 11030.1231 |  | 65.4923 | 18505.1153 |  | 223.0055 | 27008.7198 |  | 18000 | 35686.3775 |  | 18000 | 43979.604 |  | 18000 | 51058.955 |  | 18000 | 59870.6402
[13 empty] | Next iteration flow rate |  |  | 180.7092 | Abs Value of | Flow this | 2335.8559 | Abs Value of | Flow this | 5719.6531 | Abs Value of | Flow this | 11140.4243 | Abs Value of | Flow this | 18690.1665 | Abs Value of | Flow this | 27278.807 | Abs Value of | Flow this | 36043.2413 | Abs Value of | Flow this | 44419.4001 | Abs Value of | Flow this | 51569.5445 | Abs Value of | Flow this | 60469.3466 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2291 |  |  | 90.0579 |  |  | 89.1972 |  |  | 86.3115 |  |  | 79.2005 |  |  | 66.7344 |  |  | 49.2111 |  |  | 27.9308 |  |  | 6.2601 |  |  | -25.2238
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43442 |  |  | 0.43027 |  |  | 0.41635 |  |  | 0.38204 |  |  | 0.32191 |  |  | 0.23738 |  |  | 0.13473 |  |  | 0.030197 |  |  | -0.12167
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2291 |  |  | 30.0579 |  |  | 29.1972 |  |  | 26.3115 |  |  | 19.2005 |  |  | 6.7344 |  |  | -10.7889 |  |  | -32.0692 |  |  | -53.7399 |  |  | -85.2238
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33376 |  |  | 0.32733 |  |  | 0.30484 |  |  | 0.24243 |  |  | 0.10091 |  |  | -0.21924 |  |  | -1.1482 |  |  | -8.5846 |  |  | 3.3787
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82621 |  |  | 0.82794 |  |  | 0.8375 |  |  | 0.86676 |  |  | 0.94121 |  |  | 1.1374 |  |  | 1.8046 |  |  | 5.8456 |  |  | -1.9898
[13 empty] | C Non choked w/ reducers | 5 |  | 0.95352 |  |  | 12.3697 |  |  | 30.8866 |  |  | 64.0654 |  |  | 128.4853 |  |  | 324.8169 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -260.9917
[13 empty] | C Choked w/ reducers | 5 |  | 0.85382 |  |  | 11.0635 |  |  | 27.5451 |  |  | 56.1654 |  |  | 105.5602 |  |  | 192.4906 |  |  | 370.6777 |  |  | 902.9846 |  |  | 4778.0269 |  |  | 2331.8401
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.95352 |  |  | 12.3697 |  |  | 30.8866 |  |  | 64.0654 |  |  | 128.4853 |  |  | 324.8169 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 2331.8401
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7765 | 180.7092 |  | 0.76969 | 2335.8559 |  | 7.8866 | 5719.6531 |  | 24.6654 | 11140.4243 |  | 67.4853 | 18690.1665 |  | 236.6169 | 27278.807 |  | 18000 | 36043.2413 |  | 18000 | 44419.4001 |  | 18000 | 51569.5445 |  | 18000 | 60469.3466
[13 empty] | Next iteration flow rate |  |  | 184.3234 | Abs Value of | Flow this | 2359.2145 | Abs Value of | Flow this | 5776.8496 | Abs Value of | Flow this | 11251.8286 | Abs Value of | Flow this | 18877.0681 | Abs Value of | Flow this | 27551.5951 | Abs Value of | Flow this | 36403.6737 | Abs Value of | Flow this | 44863.5941 | Abs Value of | Flow this | 52085.24 | Abs Value of | Flow this | 61074.0401 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2291 |  |  | 90.0544 |  |  | 89.1765 |  |  | 86.2327 |  |  | 78.9788 |  |  | 66.2622 |  |  | 48.3866 |  |  | 26.6786 |  |  | 4.5723 |  |  | -27.5444
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.4344 |  |  | 0.43017 |  |  | 0.41597 |  |  | 0.38097 |  |  | 0.31963 |  |  | 0.2334 |  |  | 0.12869 |  |  | 0.022055 |  |  | -0.13287
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2291 |  |  | 30.0544 |  |  | 29.1765 |  |  | 26.2327 |  |  | 18.9788 |  |  | 6.2622 |  |  | -11.6134 |  |  | -33.3214 |  |  | -55.4277 |  |  | -87.5444
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33374 |  |  | 0.32718 |  |  | 0.30421 |  |  | 0.2403 |  |  | 0.094506 |  |  | -0.24001 |  |  | -1.249 |  |  | -12.1226 |  |  | 3.1783
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82623 |  |  | 0.82802 |  |  | 0.83784 |  |  | 0.86793 |  |  | 0.94494 |  |  | 1.1504 |  |  | 1.8753 |  |  | 7.8427 |  |  | -1.8125
[13 empty] | C Non choked w/ reducers | 5 |  | 0.97259 |  |  | 12.4941 |  |  | 31.2071 |  |  | 64.8065 |  |  | 130.533 |  |  | 340.0722 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -273.2394
[13 empty] | C Choked w/ reducers | 5 |  | 0.8709 |  |  | 11.1746 |  |  | 27.827 |  |  | 56.7788 |  |  | 106.9151 |  |  | 195.8011 |  |  | 380.7638 |  |  | 954.8218 |  |  | 6607.2042 |  |  | 2156.7356
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.97259 |  |  | 12.4941 |  |  | 31.2071 |  |  | 64.8065 |  |  | 130.533 |  |  | 340.0722 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 2156.7356
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7574 | 184.3234 |  | 0.89415 | 2359.2145 |  | 8.2071 | 5776.8496 |  | 25.4065 | 11251.8286 |  | 69.533 | 18877.0681 |  | 251.8722 | 27551.5951 |  | 18000 | 36403.6737 |  | 18000 | 44863.5941 |  | 18000 | 52085.24 |  | 18000 | 61074.0401
[13 empty] | Next iteration flow rate |  |  | 188.0098 | Abs Value of | Flow this | 2382.8066 | Abs Value of | Flow this | 5834.6181 | Abs Value of | Flow this | 11364.3469 | Abs Value of | Flow this | 19065.8388 | Abs Value of | Flow this | 27827.111 | Abs Value of | Flow this | 36767.7105 | Abs Value of | Flow this | 45312.23 | Abs Value of | Flow this | 52606.0924 | Abs Value of | Flow this | 61684.7805 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2291 |  |  | 90.0509 |  |  | 89.1553 |  |  | 86.1524 |  |  | 78.7526 |  |  | 65.7804 |  |  | 47.5456 |  |  | 25.4012 |  |  | 2.8505 |  |  | -29.9117
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43438 |  |  | 0.43006 |  |  | 0.41558 |  |  | 0.37988 |  |  | 0.31731 |  |  | 0.22935 |  |  | 0.12253 |  |  | 0.01375 |  |  | -0.14429
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2291 |  |  | 30.0509 |  |  | 29.1553 |  |  | 26.1524 |  |  | 18.7526 |  |  | 5.7804 |  |  | -12.4544 |  |  | -34.5988 |  |  | -57.1495 |  |  | -89.9117
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33371 |  |  | 0.32702 |  |  | 0.30356 |  |  | 0.23812 |  |  | 0.087875 |  |  | -0.26195 |  |  | -1.3621 |  |  | -20.0487 |  |  | 3.0059
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82624 |  |  | 0.8281 |  |  | 0.83819 |  |  | 0.86913 |  |  | 0.94881 |  |  | 1.1642 |  |  | 1.9545 |  |  | 12.3166 |  |  | -1.6599
[13 empty] | C Non choked w/ reducers | 5 |  | 0.99204 |  |  | 12.6199 |  |  | 31.5311 |  |  | 65.5585 |  |  | 132.638 |  |  | 357.3452 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -285.3325
[13 empty] | C Choked w/ reducers | 5 |  | 0.88832 |  |  | 11.2868 |  |  | 28.112 |  |  | 57.4001 |  |  | 108.2943 |  |  | 199.2075 |  |  | 391.3743 |  |  | 1012.8667 |  |  | 10703.949 |  |  | 2005.9077
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 0.99204 |  |  | 12.6199 |  |  | 31.5311 |  |  | 65.5585 |  |  | 132.638 |  |  | 357.3452 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 2005.9077
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.738 | 188.0098 |  | 1.0199 | 2382.8066 |  | 8.5311 | 5834.6181 |  | 26.1585 | 11364.3469 |  | 71.638 | 19065.8388 |  | 269.1452 | 27827.111 |  | 18000 | 36767.7105 |  | 18000 | 45312.23 |  | 18000 | 52606.0924 |  | 18000 | 61684.7805
[13 empty] | Next iteration flow rate |  |  | 191.77 | Abs Value of | Flow this | 2406.6347 | Abs Value of | Flow this | 5892.9643 | Abs Value of | Flow this | 11477.9903 | Abs Value of | Flow this | 19256.4972 | Abs Value of | Flow this | 28105.3822 | Abs Value of | Flow this | 37135.3876 | Abs Value of | Flow this | 45765.3523 | Abs Value of | Flow this | 53132.1533 | Abs Value of | Flow this | 62301.6283 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.229 |  |  | 90.0473 |  |  | 89.1337 |  |  | 86.0704 |  |  | 78.5219 |  |  | 65.289 |  |  | 46.6876 |  |  | 24.0982 |  |  | 1.0942 |  |  | -32.3265
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43437 |  |  | 0.42996 |  |  | 0.41518 |  |  | 0.37877 |  |  | 0.31494 |  |  | 0.22521 |  |  | 0.11624 |  |  | 0.0052781 |  |  | -0.15594
[13 empty] | Delta P at this iteration flow rate |  |  | 30.229 |  |  | 30.0473 |  |  | 29.1337 |  |  | 26.0704 |  |  | 18.5219 |  |  | 5.289 |  |  | -13.3124 |  |  | -35.9018 |  |  | -58.9058 |  |  | -92.3265
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33368 |  |  | 0.32685 |  |  | 0.3029 |  |  | 0.23588 |  |  | 0.081009 |  |  | -0.28514 |  |  | -1.4898 |  |  | -53.8348 |  |  | 2.8561
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82625 |  |  | 0.82819 |  |  | 0.83854 |  |  | 0.87036 |  |  | 0.95281 |  |  | 1.1787 |  |  | 2.044 |  |  | 31.3872 |  |  | -1.5273
[13 empty] | C Non choked w/ reducers | 5 |  | 1.0119 |  |  | 12.7469 |  |  | 31.8588 |  |  | 66.3217 |  |  | 134.8031 |  |  | 377.1416 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -297.3135
[13 empty] | C Choked w/ reducers | 5 |  | 0.90609 |  |  | 11.4001 |  |  | 28.4 |  |  | 58.0293 |  |  | 109.6986 |  |  | 202.714 |  |  | 402.5521 |  |  | 1078.3119 |  |  | 28164.0688 |  |  | 1874.6232
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.0119 |  |  | 12.7469 |  |  | 31.8588 |  |  | 66.3217 |  |  | 134.8031 |  |  | 377.1416 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1874.6232
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7181 | 191.77 |  | 1.1469 | 2406.6347 |  | 8.8588 | 5892.9643 |  | 26.9217 | 11477.9903 |  | 73.8031 | 19256.4972 |  | 288.9416 | 28105.3822 |  | 18000 | 37135.3876 |  | 18000 | 45765.3523 |  | 18000 | 53132.1533 |  | 18000 | 62301.6283
[13 empty] | Next iteration flow rate |  |  | 195.6054 | Abs Value of | Flow this | 2430.701 | Abs Value of | Flow this | 5951.894 | Abs Value of | Flow this | 11592.7702 | Abs Value of | Flow this | 19449.0622 | Abs Value of | Flow this | 28386.436 | Abs Value of | Flow this | 37506.7414 | Abs Value of | Flow this | 46223.0059 | Abs Value of | Flow this | 53663.4748 | Abs Value of | Flow this | 62924.6446 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.229 |  |  | 90.0436 |  |  | 89.1116 |  |  | 85.9868 |  |  | 78.2866 |  |  | 64.7877 |  |  | 45.8124 |  |  | 22.7689 |  |  | -0.69744 |  |  | -34.7899
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43435 |  |  | 0.42985 |  |  | 0.41478 |  |  | 0.37763 |  |  | 0.31252 |  |  | 0.22099 |  |  | 0.10983 |  |  | -0.0033643 |  |  | -0.16782
[13 empty] | Delta P at this iteration flow rate |  |  | 30.229 |  |  | 30.0436 |  |  | 29.1116 |  |  | 25.9868 |  |  | 18.2866 |  |  | 4.7877 |  |  | -14.1876 |  |  | -37.2311 |  |  | -60.6974 |  |  | -94.7899
[13 empty] | Press drop ratio this iteration |  |  | 0.33503 |  |  | 0.33366 |  |  | 0.32669 |  |  | 0.30222 |  |  | 0.23359 |  |  | 0.073898 |  |  | -0.30969 |  |  | -1.6352 |  |  | 87.0293 |  |  | 2.7246
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82627 |  |  | 0.82828 |  |  | 0.8389 |  |  | 0.87162 |  |  | 0.95695 |  |  | 1.1941 |  |  | 2.1459 |  |  | -48.124 |  |  | -1.411
[13 empty] | C Non choked w/ reducers | 5 |  | 1.0321 |  |  | 12.8752 |  |  | 32.1901 |  |  | 67.0963 |  |  | 137.0315 |  |  | 400.1655 |  |  | #NUM! |  |  | #NUM! |  |  | -50.9523 |  |  | -309.2192
[13 empty] | C Choked w/ reducers | 5 |  | 0.92421 |  |  | 11.5146 |  |  | 28.6911 |  |  | 58.6666 |  |  | 111.1286 |  |  | 206.3254 |  |  | 414.3449 |  |  | 1152.6766 |  |  | 44627.95 |  |  | 1759.3045
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.0321 |  |  | 12.8752 |  |  | 32.1901 |  |  | 67.0963 |  |  | 137.0315 |  |  | 400.1655 |  |  | #NUM! |  |  | #NUM! |  |  | 44627.95 |  |  | 1759.3045
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6979 | 195.6054 |  | 1.2752 | 2430.701 |  | 9.1901 | 5951.894 |  | 27.6963 | 11592.7702 |  | 76.0315 | 19449.0622 |  | 311.9655 | 28386.436 |  | 18000 | 37506.7414 |  | 18000 | 46223.0059 |  | 18000 | 53663.4748 |  | 18000 | 62924.6446
[13 empty] | Next iteration flow rate |  |  | 199.5176 | Abs Value of | Flow this | 2455.008 | Abs Value of | Flow this | 6011.4129 | Abs Value of | Flow this | 11708.6979 | Abs Value of | Flow this | 19643.5528 | Abs Value of | Flow this | 28670.3003 | Abs Value of | Flow this | 37881.8088 | Abs Value of | Flow this | 46685.2359 | Abs Value of | Flow this | 54200.1096 | Abs Value of | Flow this | 63553.891 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2289 |  |  | 90.0399 |  |  | 89.0892 |  |  | 85.9015 |  |  | 78.0465 |  |  | 64.2763 |  |  | 44.9196 |  |  | 21.4129 |  |  | -2.5251 |  |  | -37.3028
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43433 |  |  | 0.42974 |  |  | 0.41437 |  |  | 0.37648 |  |  | 0.31005 |  |  | 0.21668 |  |  | 0.10329 |  |  | -0.01218 |  |  | -0.17994
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2289 |  |  | 30.0399 |  |  | 29.0892 |  |  | 25.9015 |  |  | 18.0465 |  |  | 4.2763 |  |  | -15.0804 |  |  | -38.5871 |  |  | -62.5251 |  |  | -97.3028
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33363 |  |  | 0.32652 |  |  | 0.30153 |  |  | 0.23123 |  |  | 0.06653 |  |  | -0.33572 |  |  | -1.802 |  |  | 24.7616 |  |  | 2.6085
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82628 |  |  | 0.82837 |  |  | 0.83927 |  |  | 0.87292 |  |  | 0.96124 |  |  | 1.2104 |  |  | 2.2628 |  |  | -12.9768 |  |  | -1.3082
[13 empty] | C Non choked w/ reducers | 5 |  | 1.0528 |  |  | 13.0048 |  |  | 32.5252 |  |  | 67.8825 |  |  | 139.3263 |  |  | 427.4324 |  |  | #NUM! |  |  | #NUM! |  |  | -98.8218 |  |  | -321.0826
[13 empty] | C Choked w/ reducers | 5 |  | 0.94269 |  |  | 11.6302 |  |  | 28.9853 |  |  | 59.3121 |  |  | 112.5852 |  |  | 210.0466 |  |  | 426.806 |  |  | 1237.9265 |  |  | 12449.6696 |  |  | 1657.1968
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.0528 |  |  | 13.0048 |  |  | 32.5252 |  |  | 67.8825 |  |  | 139.3263 |  |  | 427.4324 |  |  | #NUM! |  |  | #NUM! |  |  | 12449.6696 |  |  | 1657.1968
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6772 | 199.5176 |  | 1.4048 | 2455.008 |  | 9.5252 | 6011.4129 |  | 28.4825 | 11708.6979 |  | 78.3263 | 19643.5528 |  | 339.2324 | 28670.3003 |  | 18000 | 37881.8088 |  | 18000 | 46685.2359 |  | 18000 | 54200.1096 |  | 18000 | 63553.891
[13 empty] | Next iteration flow rate |  |  | 203.5079 | Abs Value of | Flow this | 2479.5581 | Abs Value of | Flow this | 6071.527 | Abs Value of | Flow this | 11825.7849 | Abs Value of | Flow this | 19839.9883 | Abs Value of | Flow this | 28957.0033 | Abs Value of | Flow this | 38260.6269 | Abs Value of | Flow this | 47152.0883 | Abs Value of | Flow this | 54742.1107 | Abs Value of | Flow this | 64189.4299 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2289 |  |  | 90.0361 |  |  | 89.0662 |  |  | 85.8145 |  |  | 77.8016 |  |  | 63.7546 |  |  | 44.0089 |  |  | 20.0297 |  |  | -4.3895 |  |  | -39.8662
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43431 |  |  | 0.42963 |  |  | 0.41395 |  |  | 0.3753 |  |  | 0.30754 |  |  | 0.21229 |  |  | 0.096618 |  |  | -0.021174 |  |  | -0.1923
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2289 |  |  | 30.0361 |  |  | 29.0662 |  |  | 25.8145 |  |  | 17.8016 |  |  | 3.7546 |  |  | -15.9911 |  |  | -39.9703 |  |  | -64.3895 |  |  | -99.8662
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.3336 |  |  | 0.32634 |  |  | 0.30082 |  |  | 0.22881 |  |  | 0.058891 |  |  | -0.36336 |  |  | -1.9956 |  |  | 14.6691 |  |  | 2.505
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.8263 |  |  | 0.82846 |  |  | 0.83965 |  |  | 0.87425 |  |  | 0.96569 |  |  | 1.2277 |  |  | 2.3984 |  |  | -7.28 |  |  | -1.2167
[13 empty] | C Non choked w/ reducers | 5 |  | 1.0738 |  |  | 13.1357 |  |  | 32.864 |  |  | 68.6807 |  |  | 141.6911 |  |  | 460.4723 |  |  | #NUM! |  |  | #NUM! |  |  | -132.9719 |  |  | -332.9331
[13 empty] | C Choked w/ reducers | 5 |  | 0.96155 |  |  | 11.747 |  |  | 29.2827 |  |  | 59.966 |  |  | 114.069 |  |  | 213.883 |  |  | 439.995 |  |  | 1336.6504 |  |  | 7233.4141 |  |  | 1566.1448
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.0738 |  |  | 13.1357 |  |  | 32.864 |  |  | 68.6807 |  |  | 141.6911 |  |  | 460.4723 |  |  | #NUM! |  |  | #NUM! |  |  | 7233.4141 |  |  | 1566.1448
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6562 | 203.5079 |  | 1.5357 | 2479.5581 |  | 9.864 | 6071.527 |  | 29.2807 | 11825.7849 |  | 80.6911 | 19839.9883 |  | 372.2723 | 28957.0033 |  | 18000 | 38260.6269 |  | 18000 | 47152.0883 |  | 18000 | 54742.1107 |  | 18000 | 64189.4299
[13 empty] | Next iteration flow rate |  |  | 207.5781 | Abs Value of | Flow this | 2504.3537 | Abs Value of | Flow this | 6132.2423 | Abs Value of | Flow this | 11944.0428 | Abs Value of | Flow this | 20038.3882 | Abs Value of | Flow this | 29246.5734 | Abs Value of | Flow this | 38643.2332 | Abs Value of | Flow this | 47623.6092 | Abs Value of | Flow this | 55289.5318 | Abs Value of | Flow this | 64831.3242 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2288 |  |  | 90.0321 |  |  | 89.0428 |  |  | 85.7257 |  |  | 77.5518 |  |  | 63.2224 |  |  | 43.0798 |  |  | 18.6187 |  |  | -6.2913 |  |  | -42.4812
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43429 |  |  | 0.42952 |  |  | 0.41352 |  |  | 0.37409 |  |  | 0.30497 |  |  | 0.20781 |  |  | 0.089812 |  |  | -0.030348 |  |  | -0.20492
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2288 |  |  | 30.0321 |  |  | 29.0428 |  |  | 25.7257 |  |  | 17.5518 |  |  | 3.2224 |  |  | -16.9202 |  |  | -41.3813 |  |  | -66.2913 |  |  | -102.4812
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33357 |  |  | 0.32617 |  |  | 0.30009 |  |  | 0.22632 |  |  | 0.05097 |  |  | -0.39276 |  |  | -2.2226 |  |  | 10.537 |  |  | 2.4124
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82631 |  |  | 0.82855 |  |  | 0.84003 |  |  | 0.87562 |  |  | 0.97031 |  |  | 1.2462 |  |  | 2.5575 |  |  | -4.9476 |  |  | -1.1347
[13 empty] | C Non choked w/ reducers | 5 |  | 1.0953 |  |  | 13.268 |  |  | 33.2067 |  |  | 69.4911 |  |  | 144.1297 |  |  | 501.7229 |  |  | #NUM! |  |  | #NUM! |  |  | -162.679 |  |  | -344.7978
[13 empty] | C Choked w/ reducers | 5 |  | 0.98078 |  |  | 11.865 |  |  | 29.5833 |  |  | 60.6283 |  |  | 115.5808 |  |  | 217.8401 |  |  | 453.9786 |  |  | 1452.3289 |  |  | 5097.2328 |  |  | 1484.4378
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.0953 |  |  | 13.268 |  |  | 33.2067 |  |  | 69.4911 |  |  | 144.1297 |  |  | 501.7229 |  |  | #NUM! |  |  | #NUM! |  |  | 5097.2328 |  |  | 1484.4378
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6347 | 207.5781 |  | 1.668 | 2504.3537 |  | 10.2067 | 6132.2423 |  | 30.0911 | 11944.0428 |  | 83.1297 | 20038.3882 |  | 413.5229 | 29246.5734 |  | 18000 | 38643.2332 |  | 18000 | 47623.6092 |  | 18000 | 55289.5318 |  | 18000 | 64831.3242
[13 empty] | Next iteration flow rate |  |  | 211.7296 | Abs Value of | Flow this | 2529.3972 | Abs Value of | Flow this | 6193.5647 | Abs Value of | Flow this | 12063.4832 | Abs Value of | Flow this | 20238.7721 | Abs Value of | Flow this | 29539.0391 | Abs Value of | Flow this | 39029.6655 | Abs Value of | Flow this | 48099.8452 | Abs Value of | Flow this | 55842.4271 | Abs Value of | Flow this | 65479.6375 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2288 |  |  | 90.0282 |  |  | 89.019 |  |  | 85.6352 |  |  | 77.297 |  |  | 62.6796 |  |  | 42.1321 |  |  | 17.1793 |  |  | -8.2314 |  |  | -45.1487
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43427 |  |  | 0.42941 |  |  | 0.41308 |  |  | 0.37286 |  |  | 0.30235 |  |  | 0.20323 |  |  | 0.082869 |  |  | -0.039706 |  |  | -0.21779
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2288 |  |  | 30.0282 |  |  | 29.019 |  |  | 25.6352 |  |  | 17.297 |  |  | 2.6796 |  |  | -17.8679 |  |  | -42.8207 |  |  | -68.2314 |  |  | -105.1487
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33354 |  |  | 0.32599 |  |  | 0.29935 |  |  | 0.22377 |  |  | 0.042751 |  |  | -0.42409 |  |  | -2.4926 |  |  | 8.2892 |  |  | 2.3289
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82633 |  |  | 0.82865 |  |  | 0.84043 |  |  | 0.87702 |  |  | 0.97509 |  |  | 1.2658 |  |  | 2.7467 |  |  | -3.6788 |  |  | -1.0609
[13 empty] | C Non choked w/ reducers | 5 |  | 1.1172 |  |  | 13.4016 |  |  | 33.5532 |  |  | 70.314 |  |  | 146.6462 |  |  | 555.3651 |  |  | #NUM! |  |  | #NUM! |  |  | -190.4179 |  |  | -356.7017
[13 empty] | C Choked w/ reducers | 5 |  | 1.0004 |  |  | 11.9842 |  |  | 29.8871 |  |  | 61.2993 |  |  | 117.1214 |  |  | 221.9241 |  |  | 468.8324 |  |  | 1589.7546 |  |  | 3934.81 |  |  | 1410.7008
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.1172 |  |  | 13.4016 |  |  | 33.5532 |  |  | 70.314 |  |  | 146.6462 |  |  | 555.3651 |  |  | #NUM! |  |  | #NUM! |  |  | 3934.81 |  |  | 1410.7008
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.6128 | 211.7296 |  | 1.8016 | 2529.3972 |  | 10.5532 | 6193.5647 |  | 30.914 | 12063.4832 |  | 85.6462 | 20238.7721 |  | 467.1651 | 29539.0391 |  | 18000 | 39029.6655 |  | 18000 | 48099.8452 |  | 18000 | 55842.4271 |  | 18000 | 65479.6375
[13 empty] | Next iteration flow rate |  |  | 215.9642 | Abs Value of | Flow this | 2554.6912 | Abs Value of | Flow this | 6255.5004 | Abs Value of | Flow this | 12184.118 | Abs Value of | Flow this | 20441.1598 | Abs Value of | Flow this | 29834.4295 | Abs Value of | Flow this | 39419.9622 | Abs Value of | Flow this | 48580.8437 | Abs Value of | Flow this | 56400.8514 | Abs Value of | Flow this | 66134.4339 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2287 |  |  | 90.0241 |  |  | 88.9946 |  |  | 85.5428 |  |  | 77.037 |  |  | 62.1258 |  |  | 41.1653 |  |  | 15.711 |  |  | -10.2105 |  |  | -47.8698
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43425 |  |  | 0.42929 |  |  | 0.41264 |  |  | 0.37161 |  |  | 0.29968 |  |  | 0.19857 |  |  | 0.075786 |  |  | -0.049253 |  |  | -0.23091
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2287 |  |  | 30.0241 |  |  | 28.9946 |  |  | 25.5428 |  |  | 17.037 |  |  | 2.1258 |  |  | -18.8347 |  |  | -44.289 |  |  | -70.2105 |  |  | -107.8698
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33351 |  |  | 0.3258 |  |  | 0.2986 |  |  | 0.22115 |  |  | 0.034218 |  |  | -0.45754 |  |  | -2.819 |  |  | 6.8763 |  |  | 2.2534
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82634 |  |  | 0.82874 |  |  | 0.84083 |  |  | 0.87846 |  |  | 0.98007 |  |  | 1.2868 |  |  | 2.9755 |  |  | -2.8814 |  |  | -0.99404
[13 empty] | C Non choked w/ reducers | 5 |  | 1.1396 |  |  | 13.5366 |  |  | 33.9036 |  |  | 71.1497 |  |  | 149.245 |  |  | 629.3459 |  |  | #NUM! |  |  | #NUM! |  |  | -217.3442 |  |  | -368.6685
[13 empty] | C Choked w/ reducers | 5 |  | 1.0204 |  |  | 12.1046 |  |  | 30.1943 |  |  | 61.9792 |  |  | 118.6918 |  |  | 226.1412 |  |  | 484.6414 |  |  | 1755.7141 |  |  | 3203.8545 |  |  | 1343.8158
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.1396 |  |  | 13.5366 |  |  | 33.9036 |  |  | 71.1497 |  |  | 149.245 |  |  | 629.3459 |  |  | #NUM! |  |  | #NUM! |  |  | 3203.8545 |  |  | 1343.8158
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5904 | 215.9642 |  | 1.9366 | 2554.6912 |  | 10.9036 | 6255.5004 |  | 31.7497 | 12184.118 |  | 88.245 | 20441.1598 |  | 541.1459 | 29834.4295 |  | 18000 | 39419.9622 |  | 18000 | 48580.8437 |  | 18000 | 56400.8514 |  | 18000 | 66134.4339
[13 empty] | Next iteration flow rate |  |  | 220.2835 | Abs Value of | Flow this | 2580.2381 | Abs Value of | Flow this | 6318.0554 | Abs Value of | Flow this | 12305.9592 | Abs Value of | Flow this | 20645.5714 | Abs Value of | Flow this | 30132.7738 | Abs Value of | Flow this | 39814.1618 | Abs Value of | Flow this | 49066.6521 | Abs Value of | Flow this | 56964.8599 | Abs Value of | Flow this | 66795.7782 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2286 |  |  | 90.02 |  |  | 88.9698 |  |  | 85.4486 |  |  | 76.7718 |  |  | 61.5609 |  |  | 40.1791 |  |  | 14.2131 |  |  | -12.2293 |  |  | -50.6456
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43423 |  |  | 0.42917 |  |  | 0.41218 |  |  | 0.37033 |  |  | 0.29695 |  |  | 0.19381 |  |  | 0.068561 |  |  | -0.058991 |  |  | -0.2443
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2286 |  |  | 30.02 |  |  | 28.9698 |  |  | 25.4486 |  |  | 16.7718 |  |  | 1.5609 |  |  | -19.8209 |  |  | -45.7869 |  |  | -72.2293 |  |  | -110.6456
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33348 |  |  | 0.32561 |  |  | 0.29782 |  |  | 0.21846 |  |  | 0.025356 |  |  | -0.49331 |  |  | -3.2215 |  |  | 5.9062 |  |  | 2.1847
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82636 |  |  | 0.82884 |  |  | 0.84124 |  |  | 0.87993 |  |  | 0.98523 |  |  | 1.3092 |  |  | 3.2575 |  |  | -2.3338 |  |  | -0.93325
[13 empty] | C Non choked w/ reducers | 5 |  | 1.1623 |  |  | 13.6729 |  |  | 34.258 |  |  | 71.9984 |  |  | 151.9309 |  |  | 741.2848 |  |  | #NUM! |  |  | #NUM! |  |  | -244.1575 |  |  | -380.7204
[13 empty] | C Choked w/ reducers | 5 |  | 1.0408 |  |  | 12.2262 |  |  | 30.5047 |  |  | 62.668 |  |  | 120.2928 |  |  | 230.4985 |  |  | 501.5024 |  |  | 1960.1458 |  |  | 2701.7016 |  |  | 1282.8649
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.1623 |  |  | 13.6729 |  |  | 34.258 |  |  | 71.9984 |  |  | 151.9309 |  |  | 741.2848 |  |  | #NUM! |  |  | #NUM! |  |  | 2701.7016 |  |  | 1282.8649
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5677 | 220.2835 |  | 2.0729 | 2580.2381 |  | 11.258 | 6318.0554 |  | 32.5984 | 12305.9592 |  | 90.9309 | 20645.5714 |  | 653.0848 | 30132.7738 |  | 18000 | 39814.1618 |  | 18000 | 49066.6521 |  | 18000 | 56964.8599 |  | 18000 | 66795.7782
[13 empty] | Next iteration flow rate |  |  | 224.6892 | Abs Value of | Flow this | 2606.0405 | Abs Value of | Flow this | 6381.2359 | Abs Value of | Flow this | 12429.0188 | Abs Value of | Flow this | 20852.0271 | Abs Value of | Flow this | 30434.1015 | Abs Value of | Flow this | 40212.3034 | Abs Value of | Flow this | 49557.3187 | Abs Value of | Flow this | 57534.5085 | Abs Value of | Flow this | 67463.736 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2286 |  |  | 90.0157 |  |  | 88.9445 |  |  | 85.3525 |  |  | 76.5013 |  |  | 60.9847 |  |  | 39.1731 |  |  | 12.6852 |  |  | -14.2888 |  |  | -53.4772
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43421 |  |  | 0.42905 |  |  | 0.41172 |  |  | 0.36902 |  |  | 0.29417 |  |  | 0.18896 |  |  | 0.06119 |  |  | -0.068925 |  |  | -0.25796
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2286 |  |  | 30.0157 |  |  | 28.9445 |  |  | 25.3525 |  |  | 16.5013 |  |  | 0.98467 |  |  | -20.8269 |  |  | -47.3148 |  |  | -74.2888 |  |  | -113.4772
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33345 |  |  | 0.32542 |  |  | 0.29703 |  |  | 0.2157 |  |  | 0.016146 |  |  | -0.53166 |  |  | -3.7299 |  |  | 5.1991 |  |  | 2.122
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82638 |  |  | 0.82894 |  |  | 0.84166 |  |  | 0.88145 |  |  | 0.99059 |  |  | 1.3332 |  |  | 3.6138 |  |  | -1.9347 |  |  | -0.87774
[13 empty] | C Non choked w/ reducers | 5 |  | 1.1856 |  |  | 13.8107 |  |  | 34.6164 |  |  | 72.8606 |  |  | 154.7091 |  |  | 941.9664 |  |  | #NUM! |  |  | #NUM! |  |  | -271.3631 |  |  | -392.879
[13 empty] | C Choked w/ reducers | 5 |  | 1.0616 |  |  | 12.349 |  |  | 30.8185 |  |  | 63.3659 |  |  | 121.9254 |  |  | 235.0033 |  |  | 519.5255 |  |  | 2218.2099 |  |  | 2335.4292 |  |  | 1227.0869
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.1856 |  |  | 13.8107 |  |  | 34.6164 |  |  | 72.8606 |  |  | 154.7091 |  |  | 941.9664 |  |  | #NUM! |  |  | #NUM! |  |  | 2335.4292 |  |  | 1227.0869
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5444 | 224.6892 |  | 2.2107 | 2606.0405 |  | 11.6164 | 6381.2359 |  | 33.4606 | 12429.0188 |  | 93.7091 | 20852.0271 |  | 853.7664 | 30434.1015 |  | 18000 | 40212.3034 |  | 18000 | 49557.3187 |  | 18000 | 57534.5085 |  | 18000 | 67463.736
[13 empty] | Next iteration flow rate |  |  | 229.183 | Abs Value of | Flow this | 2632.1009 | Abs Value of | Flow this | 6445.0483 | Abs Value of | Flow this | 12553.309 | Abs Value of | Flow this | 21060.5474 | Abs Value of | Flow this | 30738.4425 | Abs Value of | Flow this | 40614.4265 | Abs Value of | Flow this | 50052.8918 | Abs Value of | Flow this | 58109.8536 | Abs Value of | Flow this | 68138.3733 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2285 |  |  | 90.0114 |  |  | 88.9186 |  |  | 85.2545 |  |  | 76.2254 |  |  | 60.3968 |  |  | 38.1468 |  |  | 11.1265 |  |  | -16.3896 |  |  | -56.3657
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43419 |  |  | 0.42892 |  |  | 0.41125 |  |  | 0.36769 |  |  | 0.29134 |  |  | 0.18401 |  |  | 0.053672 |  |  | -0.079059 |  |  | -0.27189
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2285 |  |  | 30.0114 |  |  | 28.9186 |  |  | 25.2545 |  |  | 16.2254 |  |  | 0.39683 |  |  | -21.8532 |  |  | -48.8735 |  |  | -76.3896 |  |  | -116.3657
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33342 |  |  | 0.32523 |  |  | 0.29622 |  |  | 0.21286 |  |  | 0.0065705 |  |  | -0.57287 |  |  | -4.3925 |  |  | 4.6609 |  |  | 2.0645
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82639 |  |  | 0.82905 |  |  | 0.8421 |  |  | 0.88301 |  |  | 0.99617 |  |  | 1.3591 |  |  | 4.0782 |  |  | -1.6308 |  |  | -0.82686
[13 empty] | C Non choked w/ reducers | 5 |  | 1.2093 |  |  | 13.9498 |  |  | 34.9789 |  |  | 73.7366 |  |  | 157.5853 |  |  | 1497.4819 |  |  | #NUM! |  |  | #NUM! |  |  | -299.3794 |  |  | -405.1652
[13 empty] | C Choked w/ reducers | 5 |  | 1.0829 |  |  | 12.4731 |  |  | 31.1358 |  |  | 64.0732 |  |  | 123.5904 |  |  | 239.6635 |  |  | 538.8371 |  |  | 2554.2365 |  |  | 2056.4329 |  |  | 1175.8456
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.2093 |  |  | 13.9498 |  |  | 34.9789 |  |  | 73.7366 |  |  | 157.5853 |  |  | 1497.4819 |  |  | #NUM! |  |  | #NUM! |  |  | 2056.4329 |  |  | 1175.8456
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5207 | 229.183 |  | 2.3498 | 2632.1009 |  | 11.9789 | 6445.0483 |  | 34.3366 | 12553.309 |  | 96.5853 | 21060.5474 |  | 1409.2819 | 30738.4425 |  | 18000 | 40614.4265 |  | 18000 | 50052.8918 |  | 18000 | 58109.8536 |  | 18000 | 68138.3733
[13 empty] | Next iteration flow rate |  |  | 233.7666 | Abs Value of | Flow this | 2658.4219 | Abs Value of | Flow this | 6509.4988 | Abs Value of | Flow this | 12678.8421 | Abs Value of | Flow this | 21271.1529 | Abs Value of | Flow this | 31045.827 | Abs Value of | Flow this | 41020.5707 | Abs Value of | Flow this | 50553.4208 | Abs Value of | Flow this | 58690.9521 | Abs Value of | Flow this | 68819.7571 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2285 |  |  | 90.007 |  |  | 88.8922 |  |  | 85.1545 |  |  | 75.9439 |  |  | 59.7972 |  |  | 37.1 |  |  | 9.5365 |  |  | -18.5327 |  |  | -59.3123
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43417 |  |  | 0.42879 |  |  | 0.41076 |  |  | 0.36633 |  |  | 0.28845 |  |  | 0.17896 |  |  | 0.046002 |  |  | -0.089397 |  |  | -0.28611
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2285 |  |  | 30.007 |  |  | 28.8922 |  |  | 25.1545 |  |  | 15.9439 |  |  | -0.20282 |  |  | -22.9 |  |  | -50.4635 |  |  | -78.5327 |  |  | -119.3123
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33339 |  |  | 0.32503 |  |  | 0.2954 |  |  | 0.20994 |  |  | -0.0033917 |  |  | -0.61725 |  |  | -5.2916 |  |  | 4.2375 |  |  | 2.0116
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82641 |  |  | 0.82915 |  |  | 0.84254 |  |  | 0.88462 |  |  | 1.002 |  |  | 1.3869 |  |  | 4.7082 |  |  | -1.3919 |  |  | -0.78006
[13 empty] | C Non choked w/ reducers | 5 |  | 1.2335 |  |  | 14.0904 |  |  | 35.3456 |  |  | 74.6266 |  |  | 160.5658 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -328.5921 |  |  | -417.5997
[13 empty] | C Choked w/ reducers | 5 |  | 1.1045 |  |  | 12.5984 |  |  | 31.4565 |  |  | 64.7899 |  |  | 125.289 |  |  | 244.4875 |  |  | 559.5823 |  |  | 3009.8938 |  |  | 1836.8199 |  |  | 1128.6051
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.2335 |  |  | 14.0904 |  |  | 35.3456 |  |  | 74.6266 |  |  | 160.5658 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1836.8199 |  |  | 1128.6051
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.4965 | 233.7666 |  | 2.4904 | 2658.4219 |  | 12.3456 | 6509.4988 |  | 35.2266 | 12678.8421 |  | 99.5658 | 21271.1529 |  | 18000 | 31045.827 |  | 18000 | 41020.5707 |  | 18000 | 50553.4208 |  | 18000 | 58690.9521 |  | 18000 | 68819.7571
[13 empty] | Next iteration flow rate |  |  | 238.4419 | Abs Value of | Flow this | 2685.0061 | Abs Value of | Flow this | 6574.5937 | Abs Value of | Flow this | 12805.6305 | Abs Value of | Flow this | 21483.8644 | Abs Value of | Flow this | 31356.2852 | Abs Value of | Flow this | 41430.7764 | Abs Value of | Flow this | 51058.955 | Abs Value of | Flow this | 59277.8616 | Abs Value of | Flow this | 69507.9546 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2284 |  |  | 90.0025 |  |  | 88.8654 |  |  | 85.0524 |  |  | 75.6567 |  |  | 59.1855 |  |  | 36.032 |  |  | 7.9146 |  |  | -20.7188 |  |  | -62.3181
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43415 |  |  | 0.42866 |  |  | 0.41027 |  |  | 0.36495 |  |  | 0.2855 |  |  | 0.17381 |  |  | 0.038178 |  |  | -0.099942 |  |  | -0.30061
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2284 |  |  | 30.0025 |  |  | 28.8654 |  |  | 25.0524 |  |  | 15.6567 |  |  | -0.81452 |  |  | -23.968 |  |  | -52.0854 |  |  | -80.7188 |  |  | -122.3181
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33335 |  |  | 0.32482 |  |  | 0.29455 |  |  | 0.20694 |  |  | -0.013762 |  |  | -0.66518 |  |  | -6.5809 |  |  | 3.8959 |  |  | 1.9628
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82643 |  |  | 0.82926 |  |  | 0.84299 |  |  | 0.88627 |  |  | 1.008 |  |  | 1.4169 |  |  | 5.6117 |  |  | -1.1991 |  |  | -0.73689
[13 empty] | C Non choked w/ reducers | 5 |  | 1.2582 |  |  | 14.2325 |  |  | 35.7165 |  |  | 75.5311 |  |  | 163.6572 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -359.3881 |  |  | -430.2027
[13 empty] | C Choked w/ reducers | 5 |  | 1.1266 |  |  | 12.7251 |  |  | 31.7806 |  |  | 65.5163 |  |  | 127.0222 |  |  | 249.4845 |  |  | 581.9289 |  |  | 3662.9801 |  |  | 1659.4389 |  |  | 1084.9105
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.2582 |  |  | 14.2325 |  |  | 35.7165 |  |  | 75.5311 |  |  | 163.6572 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1659.4389 |  |  | 1084.9105
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.4718 | 238.4419 |  | 2.6325 | 2685.0061 |  | 12.7165 | 6574.5937 |  | 36.1311 | 12805.6305 |  | 102.6572 | 21483.8644 |  | 18000 | 31356.2852 |  | 18000 | 41430.7764 |  | 18000 | 51058.955 |  | 18000 | 59277.8616 |  | 18000 | 69507.9546
[13 empty] | Next iteration flow rate |  |  | 243.2108 | Abs Value of | Flow this | 2711.8562 | Abs Value of | Flow this | 6640.3397 | Abs Value of | Flow this | 12933.6868 | Abs Value of | Flow this | 21698.703 | Abs Value of | Flow this | 31669.8481 | Abs Value of | Flow this | 41845.0842 | Abs Value of | Flow this | 51569.5445 | Abs Value of | Flow this | 59870.6402 | Abs Value of | Flow this | 70203.0342 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2283 |  |  | 89.998 |  |  | 88.8379 |  |  | 84.9484 |  |  | 75.3638 |  |  | 58.5615 |  |  | 34.9427 |  |  | 6.2601 |  |  | -22.9489 |  |  | -65.3843
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43413 |  |  | 0.42853 |  |  | 0.40977 |  |  | 0.36354 |  |  | 0.28249 |  |  | 0.16855 |  |  | 0.030197 |  |  | -0.1107 |  |  | -0.3154
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2283 |  |  | 29.998 |  |  | 28.8379 |  |  | 24.9484 |  |  | 15.3638 |  |  | -1.4385 |  |  | -25.0573 |  |  | -53.7399 |  |  | -82.9489 |  |  | -125.3843
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33332 |  |  | 0.32461 |  |  | 0.29369 |  |  | 0.20386 |  |  | -0.024564 |  |  | -0.7171 |  |  | -8.5846 |  |  | 3.6145 |  |  | 1.9177
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82645 |  |  | 0.82937 |  |  | 0.84345 |  |  | 0.88796 |  |  | 1.0143 |  |  | 1.4495 |  |  | 7.0158 |  |  | -1.0402 |  |  | -0.69693
[13 empty] | C Non choked w/ reducers | 5 |  | 1.2833 |  |  | 14.3759 |  |  | 36.0916 |  |  | 76.4504 |  |  | 166.8671 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -392.1807 |  |  | -442.9947
[13 empty] | C Choked w/ reducers | 5 |  | 1.1491 |  |  | 12.853 |  |  | 32.1084 |  |  | 66.2526 |  |  | 128.7911 |  |  | 254.6643 |  |  | 606.072 |  |  | 4677.4237 |  |  | 1513.1634 |  |  | 1044.3735
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.2833 |  |  | 14.3759 |  |  | 36.0916 |  |  | 76.4504 |  |  | 166.8671 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1513.1634 |  |  | 1044.3735
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.4467 | 243.2108 |  | 2.7759 | 2711.8562 |  | 13.0916 | 6640.3397 |  | 37.0504 | 12933.6868 |  | 105.8671 | 21698.703 |  | 18000 | 31669.8481 |  | 18000 | 41845.0842 |  | 18000 | 51569.5445 |  | 18000 | 59870.6402 |  | 18000 | 70203.0342
[13 empty] | Next iteration flow rate |  |  | 248.075 | Abs Value of | Flow this | 2738.9748 | Abs Value of | Flow this | 6706.7431 | Abs Value of | Flow this | 13063.0237 | Abs Value of | Flow this | 21915.6901 | Abs Value of | Flow this | 31986.5466 | Abs Value of | Flow this | 42263.535 | Abs Value of | Flow this | 52085.24 | Abs Value of | Flow this | 60469.3466 | Abs Value of | Flow this | 70905.0645 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2282 |  |  | 89.9933 |  |  | 88.8099 |  |  | 84.8422 |  |  | 75.065 |  |  | 57.9249 |  |  | 33.8314 |  |  | 4.5723 |  |  | -25.2238 |  |  | -68.5121
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43411 |  |  | 0.4284 |  |  | 0.40926 |  |  | 0.36209 |  |  | 0.27942 |  |  | 0.16319 |  |  | 0.022055 |  |  | -0.12167 |  |  | -0.33049
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2282 |  |  | 29.9933 |  |  | 28.8099 |  |  | 24.8422 |  |  | 15.065 |  |  | -2.0751 |  |  | -26.1686 |  |  | -55.4277 |  |  | -85.2238 |  |  | -128.5121
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33328 |  |  | 0.3244 |  |  | 0.2928 |  |  | 0.20069 |  |  | -0.035823 |  |  | -0.7735 |  |  | -12.1226 |  |  | 3.3787 |  |  | 1.8758
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82646 |  |  | 0.82948 |  |  | 0.84392 |  |  | 0.8897 |  |  | 1.0209 |  |  | 1.4848 |  |  | 9.4952 |  |  | -0.90712 |  |  | -0.65986
[13 empty] | C Non choked w/ reducers | 5 |  | 1.309 |  |  | 14.5209 |  |  | 36.471 |  |  | 77.3849 |  |  | 170.2036 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -427.4322 |  |  | -455.9962
[13 empty] | C Choked w/ reducers | 5 |  | 1.1721 |  |  | 12.9822 |  |  | 32.4397 |  |  | 66.9988 |  |  | 130.5968 |  |  | 260.0374 |  |  | 632.2398 |  |  | 6468.087 |  |  | 1390.4601 |  |  | 1006.6607
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.309 |  |  | 14.5209 |  |  | 36.471 |  |  | 77.3849 |  |  | 170.2036 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1390.4601 |  |  | 1006.6607
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.421 | 248.075 |  | 2.9209 | 2738.9748 |  | 13.471 | 6706.7431 |  | 37.9849 | 13063.0237 |  | 109.2036 | 21915.6901 |  | 18000 | 31986.5466 |  | 18000 | 42263.535 |  | 18000 | 52085.24 |  | 18000 | 60469.3466 |  | 18000 | 70905.0645
[13 empty] | Next iteration flow rate |  |  | 253.0365 | Abs Value of | Flow this | 2766.3645 | Abs Value of | Flow this | 6773.8105 | Abs Value of | Flow this | 13193.6539 | Abs Value of | Flow this | 22134.847 | Abs Value of | Flow this | 32306.412 | Abs Value of | Flow this | 42686.1704 | Abs Value of | Flow this | 52606.0924 | Abs Value of | Flow this | 61074.0401 | Abs Value of | Flow this | 71614.1152 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2282 |  |  | 89.9885 |  |  | 88.7814 |  |  | 84.7339 |  |  | 74.7601 |  |  | 57.2756 |  |  | 32.6978 |  |  | 2.8505 |  |  | -27.5444 |  |  | -71.7029
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43408 |  |  | 0.42826 |  |  | 0.40874 |  |  | 0.36062 |  |  | 0.27628 |  |  | 0.15773 |  |  | 0.01375 |  |  | -0.13287 |  |  | -0.34588
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2282 |  |  | 29.9885 |  |  | 28.7814 |  |  | 24.7339 |  |  | 14.7601 |  |  | -2.7244 |  |  | -27.3022 |  |  | -57.1495 |  |  | -87.5444 |  |  | -131.7029
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33325 |  |  | 0.32418 |  |  | 0.2919 |  |  | 0.19743 |  |  | -0.047566 |  |  | -0.83499 |  |  | -20.0487 |  |  | 3.1783 |  |  | 1.8368
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82648 |  |  | 0.82959 |  |  | 0.8444 |  |  | 0.89149 |  |  | 1.0277 |  |  | 1.5233 |  |  | 15.0496 |  |  | -0.794 |  |  | -0.62537
[13 empty] | C Non choked w/ reducers | 5 |  | 1.3352 |  |  | 14.6673 |  |  | 36.8549 |  |  | 78.335 |  |  | 173.6757 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -465.6798 |  |  | -469.228
[13 empty] | C Choked w/ reducers | 5 |  | 1.1956 |  |  | 13.1127 |  |  | 32.7746 |  |  | 67.7553 |  |  | 132.4406 |  |  | 265.6154 |  |  | 660.7008 |  |  | 10478.5732 |  |  | 1286.0465 |  |  | 971.4837
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.3352 |  |  | 14.6673 |  |  | 36.8549 |  |  | 78.335 |  |  | 173.6757 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1286.0465 |  |  | 971.4837
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.3948 | 253.0365 |  | 3.0673 | 2766.3645 |  | 13.8549 | 6773.8105 |  | 38.935 | 13193.6539 |  | 112.6757 | 22134.847 |  | 18000 | 32306.412 |  | 18000 | 42686.1704 |  | 18000 | 52606.0924 |  | 18000 | 61074.0401 |  | 18000 | 71614.1152
[13 empty] | Next iteration flow rate |  |  | 258.0972 | Abs Value of | Flow this | 2794.0281 | Abs Value of | Flow this | 6841.5486 | Abs Value of | Flow this | 13325.5904 | Abs Value of | Flow this | 22356.1955 | Abs Value of | Flow this | 32629.4762 | Abs Value of | Flow this | 43113.0321 | Abs Value of | Flow this | 53132.1533 | Abs Value of | Flow this | 61684.7805 | Abs Value of | Flow this | 72330.2563 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2281 |  |  | 89.9837 |  |  | 88.7523 |  |  | 84.6234 |  |  | 74.4492 |  |  | 56.6132 |  |  | 31.5414 |  |  | 1.0942 |  |  | -29.9117 |  |  | -74.9577
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43406 |  |  | 0.42812 |  |  | 0.4082 |  |  | 0.35912 |  |  | 0.27309 |  |  | 0.15215 |  |  | 0.0052781 |  |  | -0.14429 |  |  | -0.36158
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2281 |  |  | 29.9837 |  |  | 28.7523 |  |  | 24.6234 |  |  | 14.4492 |  |  | -3.3868 |  |  | -28.4586 |  |  | -58.9058 |  |  | -89.9117 |  |  | -134.9577
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33321 |  |  | 0.32396 |  |  | 0.29098 |  |  | 0.19408 |  |  | -0.059823 |  |  | -0.90226 |  |  | -53.8348 |  |  | 3.0059 |  |  | 1.8005
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.8265 |  |  | 0.82971 |  |  | 0.84489 |  |  | 0.89334 |  |  | 1.0349 |  |  | 1.5655 |  |  | 38.726 |  |  | -0.69669 |  |  | -0.59322
[13 empty] | C Non choked w/ reducers | 5 |  | 1.3619 |  |  | 14.8153 |  |  | 37.2431 |  |  | 79.3011 |  |  | 177.2933 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | -507.5646 |  |  | -482.7114
[13 empty] | C Choked w/ reducers | 5 |  | 1.2195 |  |  | 13.2445 |  |  | 33.1132 |  |  | 68.5222 |  |  | 134.3237 |  |  | 271.4103 |  |  | 691.7733 |  |  | 27571.0634 |  |  | 1196.1088 |  |  | 938.5924
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.3619 |  |  | 14.8153 |  |  | 37.2431 |  |  | 79.3011 |  |  | 177.2933 |  |  | #NUM! |  |  | #NUM! |  |  | #NUM! |  |  | 1196.1088 |  |  | 938.5924
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.3681 | 258.0972 |  | 3.2153 | 2794.0281 |  | 14.2431 | 6841.5486 |  | 39.9011 | 13325.5904 |  | 116.2933 | 22356.1955 |  | 18000 | 32629.4762 |  | 18000 | 43113.0321 |  | 18000 | 53132.1533 |  | 18000 | 61684.7805 |  | 18000 | 72330.2563
[13 empty] | Next iteration flow rate |  |  | 263.2592 | Abs Value of | Flow this | 2821.9684 | Abs Value of | Flow this | 6909.9641 | Abs Value of | Flow this | 13458.8463 | Abs Value of | Flow this | 22579.7574 | Abs Value of | Flow this | 32955.7709 | Abs Value of | Flow this | 43544.1624 | Abs Value of | Flow this | 53663.4748 | Abs Value of | Flow this | 62301.6283 | Abs Value of | Flow this | 73053.5589 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.228 |  |  | 89.9787 |  |  | 88.7226 |  |  | 84.5107 |  |  | 74.132 |  |  | 55.9375 |  |  | 30.3617 |  |  | -0.69744 |  |  | -32.3265 |  |  | -78.278
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43403 |  |  | 0.42798 |  |  | 0.40766 |  |  | 0.35759 |  |  | 0.26983 |  |  | 0.14646 |  |  | -0.0033643 |  |  | -0.15594 |  |  | -0.37759
[13 empty] | Delta P at this iteration flow rate |  |  | 30.228 |  |  | 29.9787 |  |  | 28.7226 |  |  | 24.5107 |  |  | 14.132 |  |  | -4.0625 |  |  | -29.6383 |  |  | -60.6974 |  |  | -92.3265 |  |  | -138.278
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33318 |  |  | 0.32373 |  |  | 0.29003 |  |  | 0.19063 |  |  | -0.072625 |  |  | -0.97617 |  |  | 87.0293 |  |  | 2.8561 |  |  | 1.7665
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82652 |  |  | 0.82983 |  |  | 0.8454 |  |  | 0.89523 |  |  | 1.0423 |  |  | 1.6118 |  |  | -59.9878 |  |  | -0.61211 |  |  | -0.56318
[13 empty] | C Non choked w/ reducers | 5 |  | 1.3891 |  |  | 14.9647 |  |  | 37.6359 |  |  | 80.2836 |  |  | 181.0675 |  |  | #NUM! |  |  | #NUM! |  |  | -35.9125 |  |  | -553.8707 |  |  | -496.4683
[13 empty] | C Choked w/ reducers | 5 |  | 1.2439 |  |  | 13.3777 |  |  | 33.4555 |  |  | 69.2997 |  |  | 136.2474 |  |  | 277.4358 |  |  | 725.8374 |  |  | 43688.2912 |  |  | 1117.8248 |  |  | 907.7685
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.3891 |  |  | 14.9647 |  |  | 37.6359 |  |  | 80.2836 |  |  | 181.0675 |  |  | #NUM! |  |  | #NUM! |  |  | 43688.2912 |  |  | 1117.8248 |  |  | 907.7685
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.3409 | 263.2592 |  | 3.3647 | 2821.9684 |  | 14.6359 | 6909.9641 |  | 40.8836 | 13458.8463 |  | 120.0675 | 22579.7574 |  | 18000 | 32955.7709 |  | 18000 | 43544.1624 |  | 18000 | 53663.4748 |  | 18000 | 62301.6283 |  | 18000 | 73053.5589
[13 empty] | Next iteration flow rate |  |  | 268.5244 | Abs Value of | Flow this | 2850.1881 | Abs Value of | Flow this | 6979.0637 | Abs Value of | Flow this | 13593.4348 | Abs Value of | Flow this | 22805.555 | Abs Value of | Flow this | 33285.3286 | Abs Value of | Flow this | 43979.604 | Abs Value of | Flow this | 54200.1096 | Abs Value of | Flow this | 62924.6446 | Abs Value of | Flow this | 73784.0945 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2279 |  |  | 89.9737 |  |  | 88.6923 |  |  | 84.3958 |  |  | 73.8084 |  |  | 55.2482 |  |  | 29.1584 |  |  | -2.5251 |  |  | -34.7899 |  |  | -81.665
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43401 |  |  | 0.42783 |  |  | 0.4071 |  |  | 0.35603 |  |  | 0.2665 |  |  | 0.14065 |  |  | -0.01218 |  |  | -0.16782 |  |  | -0.39393
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2279 |  |  | 29.9737 |  |  | 28.6923 |  |  | 24.3958 |  |  | 13.8084 |  |  | -4.7518 |  |  | -30.8416 |  |  | -62.5251 |  |  | -94.7899 |  |  | -141.665
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33314 |  |  | 0.3235 |  |  | 0.28906 |  |  | 0.18708 |  |  | -0.086008 |  |  | -1.0577 |  |  | 24.7616 |  |  | 2.7246 |  |  | 1.7347
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82654 |  |  | 0.82995 |  |  | 0.84591 |  |  | 0.89718 |  |  | 1.0501 |  |  | 1.6629 |  |  | -16.3523 |  |  | -0.53793 |  |  | -0.53505
[13 empty] | C Non choked w/ reducers | 5 |  | 1.4169 |  |  | 15.1157 |  |  | 38.0333 |  |  | 81.283 |  |  | 185.0106 |  |  | #NUM! |  |  | #NUM! |  |  | -68.9009 |  |  | -605.5778 |  |  | -510.5214
[13 empty] | C Choked w/ reducers | 5 |  | 1.2688 |  |  | 13.5122 |  |  | 33.8016 |  |  | 70.088 |  |  | 138.2131 |  |  | 283.706 |  |  | 763.3503 |  |  | 12187.537 |  |  | 1049.0611 |  |  | 878.8204
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.4169 |  |  | 15.1157 |  |  | 38.0333 |  |  | 81.283 |  |  | 185.0106 |  |  | #NUM! |  |  | #NUM! |  |  | 12187.537 |  |  | 1049.0611 |  |  | 878.8204
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.3131 | 268.5244 |  | 3.5157 | 2850.1881 |  | 15.0333 | 6979.0637 |  | 41.883 | 13593.4348 |  | 124.0106 | 22805.555 |  | 18000 | 33285.3286 |  | 18000 | 43979.604 |  | 18000 | 54200.1096 |  | 18000 | 62924.6446 |  | 18000 | 73784.0945
[13 empty] | Next iteration flow rate |  |  | 273.8948 | Abs Value of | Flow this | 2878.69 | Abs Value of | Flow this | 7048.8544 | Abs Value of | Flow this | 13729.3692 | Abs Value of | Flow this | 23033.6105 | Abs Value of | Flow this | 33618.1819 | Abs Value of | Flow this | 44419.4001 | Abs Value of | Flow this | 54742.1107 | Abs Value of | Flow this | 63553.891 | Abs Value of | Flow this | 74521.9354 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2278 |  |  | 89.9685 |  |  | 88.6614 |  |  | 84.2785 |  |  | 73.4783 |  |  | 54.5451 |  |  | 27.9308 |  |  | -4.3895 |  |  | -37.3028 |  |  | -85.1201
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43399 |  |  | 0.42768 |  |  | 0.40654 |  |  | 0.35444 |  |  | 0.26311 |  |  | 0.13473 |  |  | -0.021174 |  |  | -0.17994 |  |  | -0.4106
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2278 |  |  | 29.9685 |  |  | 28.6614 |  |  | 24.2785 |  |  | 13.4783 |  |  | -5.4549 |  |  | -32.0692 |  |  | -64.3895 |  |  | -97.3028 |  |  | -145.1201
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.3331 |  |  | 0.32327 |  |  | 0.28807 |  |  | 0.18343 |  |  | -0.10001 |  |  | -1.1482 |  |  | 14.6691 |  |  | 2.6085 |  |  | 1.7049
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82656 |  |  | 0.83008 |  |  | 0.84644 |  |  | 0.89919 |  |  | 1.0583 |  |  | 1.7196 |  |  | -9.2797 |  |  | -0.47235 |  |  | -0.50866
[13 empty] | C Non choked w/ reducers | 5 |  | 1.4453 |  |  | 15.2682 |  |  | 38.4353 |  |  | 82.2998 |  |  | 189.1362 |  |  | #NUM! |  |  | #NUM! |  |  | -91.652 |  |  | -663.9352 |  |  | -524.894
[13 empty] | C Choked w/ reducers | 5 |  | 1.2941 |  |  | 13.6481 |  |  | 34.1516 |  |  | 70.8874 |  |  | 140.2224 |  |  | 290.2369 |  |  | 804.8682 |  |  | 7081.1118 |  |  | 988.175 |  |  | 851.5799
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.4453 |  |  | 15.2682 |  |  | 38.4353 |  |  | 82.2998 |  |  | 189.1362 |  |  | #NUM! |  |  | #NUM! |  |  | 7081.1118 |  |  | 988.175 |  |  | 851.5799
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.2847 | 273.8948 |  | 3.6682 | 2878.69 |  | 15.4353 | 7048.8544 |  | 42.8998 | 13729.3692 |  | 128.1362 | 23033.6105 |  | 18000 | 33618.1819 |  | 18000 | 44419.4001 |  | 18000 | 54742.1107 |  | 18000 | 63553.891 |  | 18000 | 74521.9354
[13 empty] | Next iteration flow rate |  |  | 279.3727 | Abs Value of | Flow this | 2907.4769 | Abs Value of | Flow this | 7119.3429 | Abs Value of | Flow this | 13866.6628 | Abs Value of | Flow this | 23263.9466 | Abs Value of | Flow this | 33954.3637 | Abs Value of | Flow this | 44863.5941 | Abs Value of | Flow this | 55289.5318 | Abs Value of | Flow this | 64189.4299 | Abs Value of | Flow this | 75267.1548 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2277 |  |  | 89.9633 |  |  | 88.6298 |  |  | 84.1589 |  |  | 73.1416 |  |  | 53.8278 |  |  | 26.6786 |  |  | -6.2913 |  |  | -39.8662 |  |  | -88.6446
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43396 |  |  | 0.42753 |  |  | 0.40596 |  |  | 0.35282 |  |  | 0.25965 |  |  | 0.12869 |  |  | -0.030348 |  |  | -0.1923 |  |  | -0.4276
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2277 |  |  | 29.9633 |  |  | 28.6298 |  |  | 24.1589 |  |  | 13.1416 |  |  | -6.1722 |  |  | -33.3214 |  |  | -66.2913 |  |  | -99.8662 |  |  | -148.6446
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33306 |  |  | 0.32303 |  |  | 0.28706 |  |  | 0.17967 |  |  | -0.11467 |  |  | -1.249 |  |  | 10.537 |  |  | 2.505 |  |  | 1.6769
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82658 |  |  | 0.8302 |  |  | 0.84698 |  |  | 0.90125 |  |  | 1.0668 |  |  | 1.7828 |  |  | -6.384 |  |  | -0.41398 |  |  | -0.48386
[13 empty] | C Non choked w/ reducers | 5 |  | 1.4742 |  |  | 15.4223 |  |  | 38.842 |  |  | 83.3345 |  |  | 193.4596 |  |  | #NUM! |  |  | #NUM! |  |  | -110.7689 |  |  | -730.5694 |  |  | -539.6108
[13 empty] | C Choked w/ reducers | 5 |  | 1.32 |  |  | 13.7854 |  |  | 34.5053 |  |  | 71.6981 |  |  | 142.2766 |  |  | 297.0454 |  |  | 851.0728 |  |  | 4989.9086 |  |  | 933.8813 |  |  | 825.898
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.4742 |  |  | 15.4223 |  |  | 38.842 |  |  | 83.3345 |  |  | 193.4596 |  |  | #NUM! |  |  | #NUM! |  |  | 4989.9086 |  |  | 933.8813 |  |  | 825.898
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.2558 | 279.3727 |  | 3.8223 | 2907.4769 |  | 15.842 | 7119.3429 |  | 43.9345 | 13866.6628 |  | 132.4596 | 23263.9466 |  | 18000 | 33954.3637 |  | 18000 | 44863.5941 |  | 18000 | 55289.5318 |  | 18000 | 64189.4299 |  | 18000 | 75267.1548
[13 empty] | Next iteration flow rate |  |  | 284.9602 | Abs Value of | Flow this | 2936.5517 | Abs Value of | Flow this | 7190.5364 | Abs Value of | Flow this | 14005.3295 | Abs Value of | Flow this | 23496.5861 | Abs Value of | Flow this | 34293.9074 | Abs Value of | Flow this | 45312.23 | Abs Value of | Flow this | 55842.4271 | Abs Value of | Flow this | 64831.3242 | Abs Value of | Flow this | 76019.8263 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2276 |  |  | 89.9579 |  |  | 88.5977 |  |  | 84.0368 |  |  | 72.7982 |  |  | 53.0961 |  |  | 25.4012 |  |  | -8.2314 |  |  | -42.4812 |  |  | -92.24
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43524 |  |  | 0.43393 |  |  | 0.42737 |  |  | 0.40537 |  |  | 0.35116 |  |  | 0.25612 |  |  | 0.12253 |  |  | -0.039706 |  |  | -0.20492 |  |  | -0.44494
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2276 |  |  | 29.9579 |  |  | 28.5977 |  |  | 24.0368 |  |  | 12.7982 |  |  | -6.9039 |  |  | -34.5988 |  |  | -68.2314 |  |  | -102.4812 |  |  | -152.24
[13 empty] | Press drop ratio this iteration |  |  | 0.33502 |  |  | 0.33302 |  |  | 0.32278 |  |  | 0.28603 |  |  | 0.1758 |  |  | -0.13003 |  |  | -1.3621 |  |  | 8.2892 |  |  | 2.4124 |  |  | 1.6505
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.8266 |  |  | 0.83033 |  |  | 0.84753 |  |  | 0.90338 |  |  | 1.0757 |  |  | 1.8537 |  |  | -4.8088 |  |  | -0.36168 |  |  | -0.46051
[13 empty] | C Non choked w/ reducers | 5 |  | 1.5036 |  |  | 15.578 |  |  | 39.2535 |  |  | 84.3875 |  |  | 197.9981 |  |  | #NUM! |  |  | #NUM! |  |  | -127.9866 |  |  | -807.6461 |  |  | -554.6975
[13 empty] | C Choked w/ reducers | 5 |  | 1.3464 |  |  | 13.9241 |  |  | 34.863 |  |  | 72.5202 |  |  | 144.3773 |  |  | 304.1502 |  |  | 902.8107 |  |  | 3851.961 |  |  | 885.16 |  |  | 801.6427
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.5036 |  |  | 15.578 |  |  | 39.2535 |  |  | 84.3875 |  |  | 197.9981 |  |  | #NUM! |  |  | #NUM! |  |  | 3851.961 |  |  | 885.16 |  |  | 801.6427
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.2264 | 284.9602 |  | 3.978 | 2936.5517 |  | 16.2535 | 7190.5364 |  | 44.9875 | 14005.3295 |  | 136.9981 | 23496.5861 |  | 18000 | 34293.9074 |  | 18000 | 45312.23 |  | 18000 | 55842.4271 |  | 18000 | 64831.3242 |  | 18000 | 76019.8263
[13 empty] | Next iteration flow rate |  |  | 290.6594 | Abs Value of | Flow this | 2965.9172 | Abs Value of | Flow this | 7262.4417 | Abs Value of | Flow this | 14145.3828 | Abs Value of | Flow this | 23731.552 | Abs Value of | Flow this | 34636.8464 | Abs Value of | Flow this | 45765.3523 | Abs Value of | Flow this | 56400.8514 | Abs Value of | Flow this | 65479.6375 | Abs Value of | Flow this | 76780.0246 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2275 |  |  | 89.9524 |  |  | 88.5648 |  |  | 83.9124 |  |  | 72.4478 |  |  | 52.3497 |  |  | 24.0982 |  |  | -10.2105 |  |  | -45.1487 |  |  | -95.9077
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43391 |  |  | 0.42721 |  |  | 0.40477 |  |  | 0.34947 |  |  | 0.25252 |  |  | 0.11624 |  |  | -0.049253 |  |  | -0.21779 |  |  | -0.46263
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2275 |  |  | 29.9524 |  |  | 28.5648 |  |  | 23.9124 |  |  | 12.4478 |  |  | -7.6503 |  |  | -35.9018 |  |  | -70.2105 |  |  | -105.1487 |  |  | -155.9077
[13 empty] | Press drop ratio this iteration |  |  | 0.33501 |  |  | 0.33298 |  |  | 0.32253 |  |  | 0.28497 |  |  | 0.17182 |  |  | -0.14614 |  |  | -1.4898 |  |  | 6.8763 |  |  | 2.3289 |  |  | 1.6256
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82662 |  |  | 0.83046 |  |  | 0.8481 |  |  | 0.90557 |  |  | 1.0851 |  |  | 1.9338 |  |  | -3.8187 |  |  | -0.31458 |  |  | -0.4385
[13 empty] | C Non choked w/ reducers | 5 |  | 1.5337 |  |  | 15.7353 |  |  | 39.6698 |  |  | 85.4593 |  |  | 202.7711 |  |  | #NUM! |  |  | #NUM! |  |  | -144.082 |  |  | -898.1202 |  |  | -570.1812
[13 empty] | C Choked w/ reducers | 5 |  | 1.3733 |  |  | 14.0642 |  |  | 35.2247 |  |  | 73.3541 |  |  | 146.5264 |  |  | 311.5716 |  |  | 961.1447 |  |  | 3136.3961 |  |  | 841.1911 |  |  | 778.6966
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.5337 |  |  | 15.7353 |  |  | 39.6698 |  |  | 85.4593 |  |  | 202.7711 |  |  | #NUM! |  |  | #NUM! |  |  | 3136.3961 |  |  | 841.1911 |  |  | 778.6966
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.1963 | 290.6594 |  | 4.1353 | 2965.9172 |  | 16.6698 | 7262.4417 |  | 46.0593 | 14145.3828 |  | 141.7711 | 23731.552 |  | 18000 | 34636.8464 |  | 18000 | 45765.3523 |  | 18000 | 56400.8514 |  | 18000 | 65479.6375 |  | 18000 | 76780.0246
[13 empty] | Next iteration flow rate |  |  | 296.4726 | Abs Value of | Flow this | 2995.5764 | Abs Value of | Flow this | 7335.0661 | Abs Value of | Flow this | 14286.8366 | Abs Value of | Flow this | 23968.8675 | Abs Value of | Flow this | 34983.2149 | Abs Value of | Flow this | 46223.0059 | Abs Value of | Flow this | 56964.8599 | Abs Value of | Flow this | 66134.4339 | Abs Value of | Flow this | 77547.8248 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2274 |  |  | 89.9468 |  |  | 88.5314 |  |  | 83.7854 |  |  | 72.0903 |  |  | 51.5884 |  |  | 22.7689 |  |  | -12.2293 |  |  | -47.8698 |  |  | -99.6491
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43388 |  |  | 0.42705 |  |  | 0.40416 |  |  | 0.34775 |  |  | 0.24885 |  |  | 0.10983 |  |  | -0.058991 |  |  | -0.23091 |  |  | -0.48068
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2274 |  |  | 29.9468 |  |  | 28.5314 |  |  | 23.7854 |  |  | 12.0903 |  |  | -8.4116 |  |  | -37.2311 |  |  | -72.2293 |  |  | -107.8698 |  |  | -159.6491
[13 empty] | Press drop ratio this iteration |  |  | 0.33501 |  |  | 0.33294 |  |  | 0.32227 |  |  | 0.28388 |  |  | 0.16771 |  |  | -0.16305 |  |  | -1.6352 |  |  | 5.9062 |  |  | 2.2534 |  |  | 1.6021
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82664 |  |  | 0.8306 |  |  | 0.84867 |  |  | 0.90783 |  |  | 1.095 |  |  | 2.0249 |  |  | -3.1389 |  |  | -0.27194 |  |  | -0.41771
[13 empty] | C Non choked w/ reducers | 5 |  | 1.5644 |  |  | 15.8942 |  |  | 40.0911 |  |  | 86.5506 |  |  | 207.8006 |  |  | #NUM! |  |  | #NUM! |  |  | -159.4905 |  |  | -1006.1389 |  |  | -586.0905
[13 empty] | C Choked w/ reducers | 5 |  | 1.4008 |  |  | 14.2057 |  |  | 35.5904 |  |  | 74.1999 |  |  | 148.7254 |  |  | 319.3318 |  |  | 1027.4292 |  |  | 2644.8162 |  |  | 801.3081 |  |  | 756.9547
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.5644 |  |  | 15.8942 |  |  | 40.0911 |  |  | 86.5506 |  |  | 207.8006 |  |  | #NUM! |  |  | #NUM! |  |  | 2644.8162 |  |  | 801.3081 |  |  | 756.9547
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.1656 | 296.4726 |  | 4.2942 | 2995.5764 |  | 17.0911 | 7335.0661 |  | 47.1506 | 14286.8366 |  | 146.8006 | 23968.8675 |  | 18000 | 34983.2149 |  | 18000 | 46223.0059 |  | 18000 | 56964.8599 |  | 18000 | 66134.4339 |  | 18000 | 77547.8248
[13 empty] | Next iteration flow rate |  |  | 302.402 | Abs Value of | Flow this | 3025.5321 | Abs Value of | Flow this | 7408.4168 | Abs Value of | Flow this | 14429.705 | Abs Value of | Flow this | 24208.5562 | Abs Value of | Flow this | 35333.0471 | Abs Value of | Flow this | 46685.2359 | Abs Value of | Flow this | 57534.5085 | Abs Value of | Flow this | 66795.7782 | Abs Value of | Flow this | 78323.3031 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2273 |  |  | 89.9411 |  |  | 88.4972 |  |  | 83.6558 |  |  | 71.7257 |  |  | 50.8117 |  |  | 21.4129 |  |  | -14.2888 |  |  | -50.6456 |  |  | -103.4656
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43385 |  |  | 0.42689 |  |  | 0.40353 |  |  | 0.34599 |  |  | 0.2451 |  |  | 0.10329 |  |  | -0.068925 |  |  | -0.2443 |  |  | -0.49909
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2273 |  |  | 29.9411 |  |  | 28.4972 |  |  | 23.6558 |  |  | 11.7257 |  |  | -9.1883 |  |  | -38.5871 |  |  | -74.2888 |  |  | -110.6456 |  |  | -163.4656
[13 empty] | Press drop ratio this iteration |  |  | 0.33501 |  |  | 0.3329 |  |  | 0.32201 |  |  | 0.28278 |  |  | 0.16348 |  |  | -0.18083 |  |  | -1.802 |  |  | 5.1991 |  |  | 2.1847 |  |  | 1.5799
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82666 |  |  | 0.83073 |  |  | 0.84926 |  |  | 0.91015 |  |  | 1.1053 |  |  | 2.1295 |  |  | -2.6434 |  |  | -0.23316 |  |  | -0.39806
[13 empty] | C Non choked w/ reducers | 5 |  | 1.5957 |  |  | 16.0548 |  |  | 40.5174 |  |  | 87.662 |  |  | 213.1119 |  |  | #NUM! |  |  | #NUM! |  |  | -174.4921 |  |  | -1137.7167 |  |  | -602.4557
[13 empty] | C Choked w/ reducers | 5 |  | 1.4288 |  |  | 14.3487 |  |  | 35.9602 |  |  | 75.0579 |  |  | 150.9762 |  |  | 327.4552 |  |  | 1103.4159 |  |  | 2286.2558 |  |  | 764.9635 |  |  | 736.3229
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.5957 |  |  | 16.0548 |  |  | 40.5174 |  |  | 87.662 |  |  | 213.1119 |  |  | #NUM! |  |  | #NUM! |  |  | 2286.2558 |  |  | 764.9635 |  |  | 736.3229
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.1343 | 302.402 |  | 4.4548 | 3025.5321 |  | 17.5174 | 7408.4168 |  | 48.262 | 14429.705 |  | 152.1119 | 24208.5562 |  | 18000 | 35333.0471 |  | 18000 | 46685.2359 |  | 18000 | 57534.5085 |  | 18000 | 66795.7782 |  | 18000 | 78323.3031
[13 empty] | Next iteration flow rate |  |  | 308.4501 | Abs Value of | Flow this | 3055.7874 | Abs Value of | Flow this | 7482.501 | Abs Value of | Flow this | 14574.002 | Abs Value of | Flow this | 24450.6417 | Abs Value of | Flow this | 35686.3775 | Abs Value of | Flow this | 47152.0883 | Abs Value of | Flow this | 58109.8536 | Abs Value of | Flow this | 67463.736 | Abs Value of | Flow this | 79106.5361 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2272 |  |  | 89.9353 |  |  | 88.4624 |  |  | 83.5237 |  |  | 71.3538 |  |  | 50.0193 |  |  | 20.0297 |  |  | -16.3896 |  |  | -53.4772 |  |  | -107.3589
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43383 |  |  | 0.42672 |  |  | 0.4029 |  |  | 0.34419 |  |  | 0.24128 |  |  | 0.096618 |  |  | -0.079059 |  |  | -0.25796 |  |  | -0.51787
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2272 |  |  | 29.9353 |  |  | 28.4624 |  |  | 23.5237 |  |  | 11.3538 |  |  | -9.9807 |  |  | -39.9703 |  |  | -76.3896 |  |  | -113.4772 |  |  | -167.3589
[13 empty] | Press drop ratio this iteration |  |  | 0.33501 |  |  | 0.33285 |  |  | 0.32175 |  |  | 0.28164 |  |  | 0.15912 |  |  | -0.19954 |  |  | -1.9956 |  |  | 4.6609 |  |  | 2.122 |  |  | 1.5589
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82669 |  |  | 0.83088 |  |  | 0.84987 |  |  | 0.91255 |  |  | 1.1162 |  |  | 2.2507 |  |  | -2.2662 |  |  | -0.19776 |  |  | -0.37945
[13 empty] | C Non choked w/ reducers | 5 |  | 1.6276 |  |  | 16.217 |  |  | 40.9487 |  |  | 88.7939 |  |  | 218.7336 |  |  | #NUM! |  |  | #NUM! |  |  | -189.2855 |  |  | -1301.9273 |  |  | -619.3091
[13 empty] | C Choked w/ reducers | 5 |  | 1.4574 |  |  | 14.4931 |  |  | 36.3341 |  |  | 75.9285 |  |  | 153.2808 |  |  | 335.9686 |  |  | 1191.4127 |  |  | 2013.134 |  |  | 731.7034 |  |  | 716.717
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.6276 |  |  | 16.217 |  |  | 40.9487 |  |  | 88.7939 |  |  | 218.7336 |  |  | #NUM! |  |  | #NUM! |  |  | 2013.134 |  |  | 731.7034 |  |  | 716.717
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.1024 | 308.4501 |  | 4.617 | 3055.7874 |  | 17.9487 | 7482.501 |  | 49.3939 | 14574.002 |  | 157.7336 | 24450.6417 |  | 18000 | 35686.3775 |  | 18000 | 47152.0883 |  | 18000 | 58109.8536 |  | 18000 | 67463.736 |  | 18000 | 79106.5361
[13 empty] | Next iteration flow rate |  |  | 314.6191 | Abs Value of | Flow this | 3086.3453 | Abs Value of | Flow this | 7557.326 | Abs Value of | Flow this | 14719.742 | Abs Value of | Flow this | 24695.1481 | Abs Value of | Flow this | 36043.2413 | Abs Value of | Flow this | 47623.6092 | Abs Value of | Flow this | 58690.9521 | Abs Value of | Flow this | 68138.3733 | Abs Value of | Flow this | 79897.6015 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2271 |  |  | 89.9294 |  |  | 88.4269 |  |  | 83.3889 |  |  | 70.9744 |  |  | 49.2111 |  |  | 18.6187 |  |  | -18.5327 |  |  | -56.3657 |  |  | -111.3305
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.4338 |  |  | 0.42655 |  |  | 0.40225 |  |  | 0.34236 |  |  | 0.23738 |  |  | 0.089812 |  |  | -0.089397 |  |  | -0.27189 |  |  | -0.53703
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2271 |  |  | 29.9294 |  |  | 28.4269 |  |  | 23.3889 |  |  | 10.9744 |  |  | -10.7889 |  |  | -41.3813 |  |  | -78.5327 |  |  | -116.3657 |  |  | -171.3305
[13 empty] | Press drop ratio this iteration |  |  | 0.33501 |  |  | 0.33281 |  |  | 0.32147 |  |  | 0.28048 |  |  | 0.15462 |  |  | -0.21924 |  |  | -2.2226 |  |  | 4.2375 |  |  | 2.0645 |  |  | 1.5389
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82671 |  |  | 0.83102 |  |  | 0.85049 |  |  | 0.91502 |  |  | 1.1277 |  |  | 2.393 |  |  | -1.9695 |  |  | -0.1653 |  |  | -0.36181
[13 empty] | C Non choked w/ reducers | 5 |  | 1.6602 |  |  | 16.3809 |  |  | 41.3852 |  |  | 89.947 |  |  | 224.6989 |  |  | #NUM! |  |  | #NUM! |  |  | -204.0229 |  |  | -1513.1392 |  |  | -636.6853
[13 empty] | C Choked w/ reducers | 5 |  | 1.4866 |  |  | 14.639 |  |  | 36.7122 |  |  | 76.8117 |  |  | 155.6412 |  |  | 344.9014 |  |  | 1294.5218 |  |  | 1798.145 |  |  | 701.1486 |  |  | 698.0607
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.6602 |  |  | 16.3809 |  |  | 41.3852 |  |  | 89.947 |  |  | 224.6989 |  |  | #NUM! |  |  | #NUM! |  |  | 1798.145 |  |  | 701.1486 |  |  | 698.0607
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.0698 | 314.6191 |  | 4.7809 | 3086.3453 |  | 18.3852 | 7557.326 |  | 50.547 | 14719.742 |  | 163.6989 | 24695.1481 |  | 18000 | 36043.2413 |  | 18000 | 47623.6092 |  | 18000 | 58690.9521 |  | 18000 | 68138.3733 |  | 18000 | 79897.6015
[13 empty] | Next iteration flow rate |  |  | 320.9115 | Abs Value of | Flow this | 3117.2088 | Abs Value of | Flow this | 7632.8992 | Abs Value of | Flow this | 14866.9395 | Abs Value of | Flow this | 24942.0996 | Abs Value of | Flow this | 36403.6737 | Abs Value of | Flow this | 48099.8452 | Abs Value of | Flow this | 59277.8616 | Abs Value of | Flow this | 68819.7571 | Abs Value of | Flow this | 80696.5775 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2269 |  |  | 89.9234 |  |  | 88.3906 |  |  | 83.2514 |  |  | 70.5873 |  |  | 48.3866 |  |  | 17.1793 |  |  | -20.7188 |  |  | -59.3123 |  |  | -115.3818
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43377 |  |  | 0.42637 |  |  | 0.40158 |  |  | 0.3405 |  |  | 0.2334 |  |  | 0.082869 |  |  | -0.099942 |  |  | -0.28611 |  |  | -0.55657
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2269 |  |  | 29.9234 |  |  | 28.3906 |  |  | 23.2514 |  |  | 10.5873 |  |  | -11.6134 |  |  | -42.8207 |  |  | -80.7188 |  |  | -119.3123 |  |  | -175.3818
[13 empty] | Press drop ratio this iteration |  |  | 0.33501 |  |  | 0.33277 |  |  | 0.32119 |  |  | 0.27929 |  |  | 0.14999 |  |  | -0.24001 |  |  | -2.4926 |  |  | 3.8959 |  |  | 2.0116 |  |  | 1.52
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82673 |  |  | 0.83116 |  |  | 0.85112 |  |  | 0.91757 |  |  | 1.1398 |  |  | 2.5623 |  |  | -1.7302 |  |  | -0.13545 |  |  | -0.34506
[13 empty] | C Non choked w/ reducers | 5 |  | 1.6934 |  |  | 16.5464 |  |  | 41.827 |  |  | 91.1221 |  |  | 231.0462 |  |  | #NUM! |  |  | #NUM! |  |  | -218.8292 |  |  | -1795.5471 |  |  | -654.6209
[13 empty] | C Choked w/ reducers | 5 |  | 1.5163 |  |  | 14.7864 |  |  | 37.0945 |  |  | 77.708 |  |  | 158.0596 |  |  | 354.2861 |  |  | 1417.0151 |  |  | 1624.4988 |  |  | 672.9794 |  |  | 680.2854
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.6934 |  |  | 16.5464 |  |  | 41.827 |  |  | 91.1221 |  |  | 231.0462 |  |  | #NUM! |  |  | #NUM! |  |  | 1624.4988 |  |  | 672.9794 |  |  | 680.2854
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.0366 | 320.9115 |  | 4.9464 | 3117.2088 |  | 18.827 | 7632.8992 |  | 51.7221 | 14866.9395 |  | 170.0462 | 24942.0996 |  | 18000 | 36403.6737 |  | 18000 | 48099.8452 |  | 18000 | 59277.8616 |  | 18000 | 68819.7571 |  | 18000 | 80696.5775
[13 empty] | Next iteration flow rate |  |  | 327.3297 | Abs Value of | Flow this | 3148.3809 | Abs Value of | Flow this | 7709.2282 | Abs Value of | Flow this | 15015.6088 | Abs Value of | Flow this | 25191.5206 | Abs Value of | Flow this | 36767.7105 | Abs Value of | Flow this | 48580.8437 | Abs Value of | Flow this | 59870.6402 | Abs Value of | Flow this | 69507.9546 | Abs Value of | Flow this | 81503.5433 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2268 |  |  | 89.9172 |  |  | 88.3536 |  |  | 83.1111 |  |  | 70.1925 |  |  | 47.5456 |  |  | 15.711 |  |  | -22.9489 |  |  | -62.3181 |  |  | -119.5146
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43374 |  |  | 0.4262 |  |  | 0.40091 |  |  | 0.33859 |  |  | 0.22935 |  |  | 0.075786 |  |  | -0.1107 |  |  | -0.30061 |  |  | -0.57651
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2268 |  |  | 29.9172 |  |  | 28.3536 |  |  | 23.1111 |  |  | 10.1925 |  |  | -12.4544 |  |  | -44.289 |  |  | -82.9489 |  |  | -122.3181 |  |  | -179.5146
[13 empty] | Press drop ratio this iteration |  |  | 0.33501 |  |  | 0.33272 |  |  | 0.32091 |  |  | 0.27807 |  |  | 0.14521 |  |  | -0.26195 |  |  | -2.819 |  |  | 3.6145 |  |  | 1.9628 |  |  | 1.502
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82676 |  |  | 0.83131 |  |  | 0.85177 |  |  | 0.9202 |  |  | 1.1526 |  |  | 2.7668 |  |  | -1.533 |  |  | -0.10791 |  |  | -0.32915
[13 empty] | C Non choked w/ reducers | 5 |  | 1.7272 |  |  | 16.7137 |  |  | 42.274 |  |  | 92.3197 |  |  | 237.8203 |  |  | #NUM! |  |  | #NUM! |  |  | -233.8125 |  |  | -2193.3137 |  |  | -673.1557
[13 empty] | C Choked w/ reducers | 5 |  | 1.5466 |  |  | 14.9353 |  |  | 37.4811 |  |  | 78.6175 |  |  | 160.5381 |  |  | 364.1588 |  |  | 1564.9418 |  |  | 1481.3032 |  |  | 646.9246 |  |  | 663.3288
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.7272 |  |  | 16.7137 |  |  | 42.274 |  |  | 92.3197 |  |  | 237.8203 |  |  | #NUM! |  |  | #NUM! |  |  | 1481.3032 |  |  | 646.9246 |  |  | 663.3288
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.0028 | 327.3297 |  | 5.1137 | 3148.3809 |  | 19.274 | 7709.2282 |  | 52.9197 | 15015.6088 |  | 176.8203 | 25191.5206 |  | 18000 | 36767.7105 |  | 18000 | 48580.8437 |  | 18000 | 59870.6402 |  | 18000 | 69507.9546 |  | 18000 | 81503.5433
[13 empty] | Next iteration flow rate |  |  | 333.8763 | Abs Value of | Flow this | 3179.8647 | Abs Value of | Flow this | 7786.3205 | Abs Value of | Flow this | 15165.7649 | Abs Value of | Flow this | 25443.4358 | Abs Value of | Flow this | 37135.3876 | Abs Value of | Flow this | 49066.6521 | Abs Value of | Flow this | 60469.3466 | Abs Value of | Flow this | 70203.0342 | Abs Value of | Flow this | 82318.5787 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2267 |  |  | 89.9109 |  |  | 88.3159 |  |  | 82.968 |  |  | 69.7898 |  |  | 46.6876 |  |  | 14.2131 |  |  | -25.2238 |  |  | -65.3843 |  |  | -123.7305
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43371 |  |  | 0.42601 |  |  | 0.40022 |  |  | 0.33665 |  |  | 0.22521 |  |  | 0.068561 |  |  | -0.12167 |  |  | -0.3154 |  |  | -0.59684
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2267 |  |  | 29.9109 |  |  | 28.3159 |  |  | 22.968 |  |  | 9.7898 |  |  | -13.3124 |  |  | -45.7869 |  |  | -85.2238 |  |  | -125.3843 |  |  | -183.7305
[13 empty] | Press drop ratio this iteration |  |  | 0.33501 |  |  | 0.33267 |  |  | 0.32062 |  |  | 0.27683 |  |  | 0.14028 |  |  | -0.28514 |  |  | -3.2215 |  |  | 3.3787 |  |  | 1.9177 |  |  | 1.4849
[13 empty] | Expansion factor | 12 |  | 0.82552 |  |  | 0.82678 |  |  | 0.83147 |  |  | 0.85243 |  |  | 0.92291 |  |  | 1.1661 |  |  | 3.0191 |  |  | -1.3677 |  |  | -0.082425 |  |  | -0.31401
[13 empty] | C Non choked w/ reducers | 5 |  | 1.7618 |  |  | 16.8827 |  |  | 42.7265 |  |  | 93.5407 |  |  | 245.0738 |  |  | #NUM! |  |  | #NUM! |  |  | -249.0716 |  |  | -2796.5397 |  |  | -692.332
[13 empty] | C Choked w/ reducers | 5 |  | 1.5776 |  |  | 15.0857 |  |  | 37.8721 |  |  | 79.5406 |  |  | 163.0792 |  |  | 374.5593 |  |  | 1747.1604 |  |  | 1361.1834 |  |  | 622.7527 |  |  | 647.1345
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.7618 |  |  | 16.8827 |  |  | 42.7265 |  |  | 93.5407 |  |  | 245.0738 |  |  | #NUM! |  |  | #NUM! |  |  | 1361.1834 |  |  | 622.7527 |  |  | 647.1345
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.9682 | 333.8763 |  | 5.2827 | 3179.8647 |  | 19.7265 | 7786.3205 |  | 54.1407 | 15165.7649 |  | 184.0738 | 25443.4358 |  | 18000 | 37135.3876 |  | 18000 | 49066.6521 |  | 18000 | 60469.3466 |  | 18000 | 70203.0342 |  | 18000 | 82318.5787
[13 empty] | Next iteration flow rate |  |  | 340.5538 | Abs Value of | Flow this | 3211.6633 | Abs Value of | Flow this | 7864.1837 | Abs Value of | Flow this | 15317.4226 | Abs Value of | Flow this | 25697.8702 | Abs Value of | Flow this | 37506.7414 | Abs Value of | Flow this | 49557.3187 | Abs Value of | Flow this | 61074.0401 | Abs Value of | Flow this | 70905.0645 | Abs Value of | Flow this | 83141.7645 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2265 |  |  | 89.9045 |  |  | 88.2774 |  |  | 82.822 |  |  | 69.3789 |  |  | 45.8124 |  |  | 12.6852 |  |  | -27.5444 |  |  | -68.5121 |  |  | -128.0311
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43368 |  |  | 0.42583 |  |  | 0.39951 |  |  | 0.33467 |  |  | 0.22099 |  |  | 0.06119 |  |  | -0.13287 |  |  | -0.33049 |  |  | -0.61759
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2265 |  |  | 29.9045 |  |  | 28.2774 |  |  | 22.822 |  |  | 9.3789 |  |  | -14.1876 |  |  | -47.3148 |  |  | -87.5444 |  |  | -128.5121 |  |  | -188.0311
[13 empty] | Press drop ratio this iteration |  |  | 0.33501 |  |  | 0.33263 |  |  | 0.32032 |  |  | 0.27556 |  |  | 0.13518 |  |  | -0.30969 |  |  | -3.7299 |  |  | 3.1783 |  |  | 1.8758 |  |  | 1.4686
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82681 |  |  | 0.83162 |  |  | 0.85311 |  |  | 0.9257 |  |  | 1.1804 |  |  | 3.3378 |  |  | -1.2273 |  |  | -0.058778 |  |  | -0.2996
[13 empty] | C Non choked w/ reducers | 5 |  | 1.797 |  |  | 17.0535 |  |  | 43.1844 |  |  | 94.7857 |  |  | 252.869 |  |  | #NUM! |  |  | #NUM! |  |  | -264.7001 |  |  | -3822.008 |  |  | -712.196
[13 empty] | C Choked w/ reducers | 5 |  | 1.6091 |  |  | 15.2376 |  |  | 38.2675 |  |  | 80.4776 |  |  | 165.6854 |  |  | 385.5321 |  |  | 1977.1838 |  |  | 1258.9683 |  |  | 600.2648 |  |  | 631.651
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.797 |  |  | 17.0535 |  |  | 43.1844 |  |  | 94.7857 |  |  | 252.869 |  |  | #NUM! |  |  | #NUM! |  |  | 1258.9683 |  |  | 600.2648 |  |  | 631.651
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.933 | 340.5538 |  | 5.4535 | 3211.6633 |  | 20.1844 | 7864.1837 |  | 55.3857 | 15317.4226 |  | 191.869 | 25697.8702 |  | 18000 | 37506.7414 |  | 18000 | 49557.3187 |  | 18000 | 61074.0401 |  | 18000 | 70905.0645 |  | 18000 | 83141.7645
[13 empty] | Next iteration flow rate |  |  | 347.3649 | Abs Value of | Flow this | 3243.7799 | Abs Value of | Flow this | 7942.8256 | Abs Value of | Flow this | 15470.5968 | Abs Value of | Flow this | 25954.8489 | Abs Value of | Flow this | 37881.8088 | Abs Value of | Flow this | 50052.8918 | Abs Value of | Flow this | 61684.7805 | Abs Value of | Flow this | 71614.1152 | Abs Value of | Flow this | 83973.1821 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2264 |  |  | 89.8979 |  |  | 88.2382 |  |  | 82.6731 |  |  | 68.9598 |  |  | 44.9196 |  |  | 11.1265 |  |  | -29.9117 |  |  | -71.7029 |  |  | -132.4182
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43365 |  |  | 0.42564 |  |  | 0.39879 |  |  | 0.33264 |  |  | 0.21668 |  |  | 0.053672 |  |  | -0.14429 |  |  | -0.34588 |  |  | -0.63875
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2264 |  |  | 29.8979 |  |  | 28.2382 |  |  | 22.6731 |  |  | 8.9598 |  |  | -15.0804 |  |  | -48.8735 |  |  | -89.9117 |  |  | -131.7029 |  |  | -192.4182
[13 empty] | Press drop ratio this iteration |  |  | 0.33501 |  |  | 0.33258 |  |  | 0.32002 |  |  | 0.27425 |  |  | 0.12993 |  |  | -0.33572 |  |  | -4.3925 |  |  | 3.0059 |  |  | 1.8368 |  |  | 1.4531
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82683 |  |  | 0.83178 |  |  | 0.85381 |  |  | 0.92859 |  |  | 1.1956 |  |  | 3.7531 |  |  | -1.1065 |  |  | -0.036781 |  |  | -0.28586
[13 empty] | C Non choked w/ reducers | 5 |  | 1.833 |  |  | 17.226 |  |  | 43.6479 |  |  | 96.0555 |  |  | 261.2803 |  |  | #NUM! |  |  | #NUM! |  |  | -280.7905 |  |  | -5956.5549 |  |  | -732.7972
[13 empty] | C Choked w/ reducers | 5 |  | 1.6413 |  |  | 15.3911 |  |  | 38.6674 |  |  | 81.4288 |  |  | 168.3593 |  |  | 397.1266 |  |  | 2276.6984 |  |  | 1170.9243 |  |  | 579.289 |  |  | 616.8314
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.833 |  |  | 17.226 |  |  | 43.6479 |  |  | 96.0555 |  |  | 261.2803 |  |  | #NUM! |  |  | #NUM! |  |  | 1170.9243 |  |  | 579.289 |  |  | 616.8314
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.897 | 347.3649 |  | 5.626 | 3243.7799 |  | 20.6479 | 7942.8256 |  | 56.6555 | 15470.5968 |  | 200.2803 | 25954.8489 |  | 18000 | 37881.8088 |  | 18000 | 50052.8918 |  | 18000 | 61684.7805 |  | 18000 | 71614.1152 |  | 18000 | 83973.1821
[13 empty] | Next iteration flow rate |  |  | 354.3122 | Abs Value of | Flow this | 3276.2177 | Abs Value of | Flow this | 8022.2538 | Abs Value of | Flow this | 15625.3028 | Abs Value of | Flow this | 26214.3974 | Abs Value of | Flow this | 38260.6269 | Abs Value of | Flow this | 50553.4208 | Abs Value of | Flow this | 62301.6283 | Abs Value of | Flow this | 72330.2563 | Abs Value of | Flow this | 84812.9139 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2262 |  |  | 89.8913 |  |  | 88.1981 |  |  | 82.5212 |  |  | 68.5323 |  |  | 44.0089 |  |  | 9.5365 |  |  | -32.3265 |  |  | -74.9577 |  |  | -136.8934
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43361 |  |  | 0.42545 |  |  | 0.39806 |  |  | 0.33058 |  |  | 0.21229 |  |  | 0.046002 |  |  | -0.15594 |  |  | -0.36158 |  |  | -0.66034
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2262 |  |  | 29.8913 |  |  | 28.1981 |  |  | 22.5212 |  |  | 8.5323 |  |  | -15.9911 |  |  | -50.4635 |  |  | -92.3265 |  |  | -134.9577 |  |  | -196.8934
[13 empty] | Press drop ratio this iteration |  |  | 0.335 |  |  | 0.33253 |  |  | 0.31971 |  |  | 0.27291 |  |  | 0.1245 |  |  | -0.36336 |  |  | -5.2916 |  |  | 2.8561 |  |  | 1.8005 |  |  | 1.4383
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82686 |  |  | 0.83194 |  |  | 0.85452 |  |  | 0.93158 |  |  | 1.2117 |  |  | 4.3166 |  |  | -1.0015 |  |  | -0.016271 |  |  | -0.27275
[13 empty] | C Non choked w/ reducers | 5 |  | 1.8696 |  |  | 17.4003 |  |  | 44.1171 |  |  | 97.351 |  |  | 270.3974 |  |  | #NUM! |  |  | #NUM! |  |  | -297.4368 |  |  | -13139.4528 |  |  | -754.1895
[13 empty] | C Choked w/ reducers | 5 |  | 1.6741 |  |  | 15.5462 |  |  | 39.0718 |  |  | 82.3945 |  |  | 171.1037 |  |  | 409.3984 |  |  | 2682.8449 |  |  | 1094.2886 |  |  | 559.6762 |  |  | 602.633
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.8696 |  |  | 17.4003 |  |  | 44.1171 |  |  | 97.351 |  |  | 270.3974 |  |  | #NUM! |  |  | #NUM! |  |  | 1094.2886 |  |  | 559.6762 |  |  | 602.633
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.8604 | 354.3122 |  | 5.8003 | 3276.2177 |  | 21.1171 | 8022.2538 |  | 57.951 | 15625.3028 |  | 209.3974 | 26214.3974 |  | 18000 | 38260.6269 |  | 18000 | 50553.4208 |  | 18000 | 62301.6283 |  | 18000 | 72330.2563 |  | 18000 | 84812.9139
[13 empty] | Next iteration flow rate |  |  | 361.3984 | Abs Value of | Flow this | 3308.9799 | Abs Value of | Flow this | 8102.4763 | Abs Value of | Flow this | 15781.5558 | Abs Value of | Flow this | 26476.5413 | Abs Value of | Flow this | 38643.2332 | Abs Value of | Flow this | 51058.955 | Abs Value of | Flow this | 62924.6446 | Abs Value of | Flow this | 73053.5589 | Abs Value of | Flow this | 85661.0431 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2261 |  |  | 89.8845 |  |  | 88.1573 |  |  | 82.3663 |  |  | 68.0961 |  |  | 43.0798 |  |  | 7.9146 |  |  | -34.7899 |  |  | -78.278 |  |  | -141.4586
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43358 |  |  | 0.42525 |  |  | 0.39731 |  |  | 0.32848 |  |  | 0.20781 |  |  | 0.038178 |  |  | -0.16782 |  |  | -0.37759 |  |  | -0.68236
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2261 |  |  | 29.8845 |  |  | 28.1573 |  |  | 22.3663 |  |  | 8.0961 |  |  | -16.9202 |  |  | -52.0854 |  |  | -94.7899 |  |  | -138.278 |  |  | -201.4586
[13 empty] | Press drop ratio this iteration |  |  | 0.335 |  |  | 0.33248 |  |  | 0.3194 |  |  | 0.27155 |  |  | 0.11889 |  |  | -0.39276 |  |  | -6.5809 |  |  | 2.7246 |  |  | 1.7665 |  |  | 1.4242
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82688 |  |  | 0.83211 |  |  | 0.85525 |  |  | 0.93466 |  |  | 1.2288 |  |  | 5.1247 |  |  | -0.90935 |  |  | 0.0028933 |  |  | -0.26023
[13 empty] | C Non choked w/ reducers | 5 |  | 1.907 |  |  | 17.5764 |  |  | 44.592 |  |  | 98.6731 |  |  | 280.3297 |  |  | #NUM! |  |  | #NUM! |  |  | -314.7373 |  |  | 72149.9708 |  |  | -776.4314
[13 empty] | C Choked w/ reducers | 5 |  | 1.7076 |  |  | 15.7029 |  |  | 39.4808 |  |  | 83.375 |  |  | 173.9216 |  |  | 422.4097 |  |  | 3264.9682 |  |  | 1026.9727 |  |  | 541.296 |  |  | 589.0166
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.907 |  |  | 17.5764 |  |  | 44.592 |  |  | 98.6731 |  |  | 280.3297 |  |  | #NUM! |  |  | #NUM! |  |  | 1026.9727 |  |  | 541.296 |  |  | 589.0166
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.823 | 361.3984 |  | 5.9764 | 3308.9799 |  | 21.592 | 8102.4763 |  | 59.2731 | 15781.5558 |  | 219.3297 | 26476.5413 |  | 18000 | 38643.2332 |  | 18000 | 51058.955 |  | 18000 | 62924.6446 |  | 18000 | 73053.5589 |  | 18000 | 85661.0431
[13 empty] | Next iteration flow rate |  |  | 368.6264 | Abs Value of | Flow this | 3342.0697 | Abs Value of | Flow this | 8183.5011 | Abs Value of | Flow this | 15939.3714 | Abs Value of | Flow this | 26741.3068 | Abs Value of | Flow this | 39029.6655 | Abs Value of | Flow this | 51569.5445 | Abs Value of | Flow this | 63553.891 | Abs Value of | Flow this | 73784.0945 | Abs Value of | Flow this | 86517.6535 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2259 |  |  | 89.8775 |  |  | 88.1156 |  |  | 82.2082 |  |  | 67.6512 |  |  | 42.1321 |  |  | 6.2601 |  |  | -37.3028 |  |  | -81.665 |  |  | -146.1155
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43355 |  |  | 0.42505 |  |  | 0.39655 |  |  | 0.32633 |  |  | 0.20323 |  |  | 0.030197 |  |  | -0.17994 |  |  | -0.39393 |  |  | -0.70482
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2259 |  |  | 29.8775 |  |  | 28.1156 |  |  | 22.2082 |  |  | 7.6512 |  |  | -17.8679 |  |  | -53.7399 |  |  | -97.3028 |  |  | -141.665 |  |  | -206.1155
[13 empty] | Press drop ratio this iteration |  |  | 0.335 |  |  | 0.33242 |  |  | 0.31908 |  |  | 0.27015 |  |  | 0.1131 |  |  | -0.42409 |  |  | -8.5846 |  |  | 2.6085 |  |  | 1.7347 |  |  | 1.4106
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82691 |  |  | 0.83228 |  |  | 0.856 |  |  | 0.93784 |  |  | 1.2471 |  |  | 6.3805 |  |  | -0.82794 |  |  | 0.020837 |  |  | -0.24827
[13 empty] | C Non choked w/ reducers | 5 |  | 1.9452 |  |  | 17.7544 |  |  | 45.0728 |  |  | 100.0227 |  |  | 291.2122 |  |  | #NUM! |  |  | #NUM! |  |  | -332.7967 |  |  | 9787.1211 |  |  | -799.5868
[13 empty] | C Choked w/ reducers | 5 |  | 1.7418 |  |  | 15.8611 |  |  | 39.8944 |  |  | 84.3706 |  |  | 176.816 |  |  | 436.2305 |  |  | 4169.1844 |  |  | 967.3686 |  |  | 524.0345 |  |  | 575.9461
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.9452 |  |  | 17.7544 |  |  | 45.0728 |  |  | 100.0227 |  |  | 291.2122 |  |  | #NUM! |  |  | #NUM! |  |  | 967.3686 |  |  | 524.0345 |  |  | 575.9461
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.7848 | 368.6264 |  | 6.1544 | 3342.0697 |  | 22.0728 | 8183.5011 |  | 60.6227 | 15939.3714 |  | 230.2122 | 26741.3068 |  | 18000 | 39029.6655 |  | 18000 | 51569.5445 |  | 18000 | 63553.891 |  | 18000 | 73784.0945 |  | 18000 | 86517.6535
[13 empty] | Next iteration flow rate |  |  | 375.9989 | Abs Value of | Flow this | 3375.4904 | Abs Value of | Flow this | 8265.3361 | Abs Value of | Flow this | 16098.7651 | Abs Value of | Flow this | 27008.7198 | Abs Value of | Flow this | 39419.9622 | Abs Value of | Flow this | 52085.24 | Abs Value of | Flow this | 64189.4299 | Abs Value of | Flow this | 74521.9354 | Abs Value of | Flow this | 87382.8301 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2257 |  |  | 89.8704 |  |  | 88.0731 |  |  | 82.047 |  |  | 67.1974 |  |  | 41.1653 |  |  | 4.5723 |  |  | -39.8662 |  |  | -85.1201 |  |  | -150.8661
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43351 |  |  | 0.42484 |  |  | 0.39577 |  |  | 0.32414 |  |  | 0.19857 |  |  | 0.022055 |  |  | -0.1923 |  |  | -0.4106 |  |  | -0.72774
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2257 |  |  | 29.8704 |  |  | 28.0731 |  |  | 22.047 |  |  | 7.1974 |  |  | -18.8347 |  |  | -55.4277 |  |  | -99.8662 |  |  | -145.1201 |  |  | -210.8661
[13 empty] | Press drop ratio this iteration |  |  | 0.335 |  |  | 0.33237 |  |  | 0.31875 |  |  | 0.26871 |  |  | 0.10711 |  |  | -0.45754 |  |  | -12.1226 |  |  | 2.505 |  |  | 1.7049 |  |  | 1.3977
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82694 |  |  | 0.83245 |  |  | 0.85676 |  |  | 0.94113 |  |  | 1.2665 |  |  | 8.598 |  |  | -0.75546 |  |  | 0.037671 |  |  | -0.23683
[13 empty] | C Non choked w/ reducers | 5 |  | 1.9841 |  |  | 17.9341 |  |  | 45.5595 |  |  | 101.4006 |  |  | 303.2137 |  |  | #NUM! |  |  | #NUM! |  |  | -351.7287 |  |  | 5291.5687 |  |  | -823.7254
[13 empty] | C Choked w/ reducers | 5 |  | 1.7766 |  |  | 16.021 |  |  | 40.3128 |  |  | 85.3818 |  |  | 179.7902 |  |  | 450.9402 |  |  | 5765.2779 |  |  | 914.2181 |  |  | 507.7912 |  |  | 563.3885
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1.9841 |  |  | 17.9341 |  |  | 45.5595 |  |  | 101.4006 |  |  | 303.2137 |  |  | #NUM! |  |  | #NUM! |  |  | 914.2181 |  |  | 507.7912 |  |  | 563.3885
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.7459 | 375.9989 |  | 6.3341 | 3375.4904 |  | 22.5595 | 8265.3361 |  | 62.0006 | 16098.7651 |  | 242.2137 | 27008.7198 |  | 18000 | 39419.9622 |  | 18000 | 52085.24 |  | 18000 | 64189.4299 |  | 18000 | 74521.9354 |  | 18000 | 87382.8301
[13 empty] | Next iteration flow rate |  |  | 383.5189 | Abs Value of | Flow this | 3409.2453 | Abs Value of | Flow this | 8347.9895 | Abs Value of | Flow this | 16259.7527 | Abs Value of | Flow this | 27278.807 | Abs Value of | Flow this | 39814.1618 | Abs Value of | Flow this | 52606.0924 | Abs Value of | Flow this | 64831.3242 | Abs Value of | Flow this | 75267.1548 | Abs Value of | Flow this | 88256.6584 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2255 |  |  | 89.8632 |  |  | 88.0298 |  |  | 81.8825 |  |  | 66.7344 |  |  | 40.1791 |  |  | 2.8505 |  |  | -42.4812 |  |  | -88.6446 |  |  | -155.7121
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43523 |  |  | 0.43348 |  |  | 0.42463 |  |  | 0.39498 |  |  | 0.32191 |  |  | 0.19381 |  |  | 0.01375 |  |  | -0.20492 |  |  | -0.4276 |  |  | -0.75112
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2255 |  |  | 29.8632 |  |  | 28.0298 |  |  | 21.8825 |  |  | 6.7344 |  |  | -19.8209 |  |  | -57.1495 |  |  | -102.4812 |  |  | -148.6446 |  |  | -215.7121
[13 empty] | Press drop ratio this iteration |  |  | 0.335 |  |  | 0.33232 |  |  | 0.31841 |  |  | 0.26724 |  |  | 0.10091 |  |  | -0.49331 |  |  | -20.0487 |  |  | 2.4124 |  |  | 1.6769 |  |  | 1.3853
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82697 |  |  | 0.83263 |  |  | 0.85754 |  |  | 0.94454 |  |  | 1.2874 |  |  | 13.5658 |  |  | -0.69054 |  |  | 0.05349 |  |  | -0.22588
[13 empty] | C Non choked w/ reducers | 5 |  | 2.0238 |  |  | 18.1158 |  |  | 46.0522 |  |  | 102.8081 |  |  | 316.5486 |  |  | #NUM! |  |  | #NUM! |  |  | -371.6588 |  |  | 3644.2906 |  |  | -848.9235
[13 empty] | C Choked w/ reducers | 5 |  | 1.8121 |  |  | 16.1825 |  |  | 40.736 |  |  | 86.4089 |  |  | 182.8479 |  |  | 466.6287 |  |  | 9339.9929 |  |  | 866.5226 |  |  | 492.4772 |  |  | 551.3134
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.0238 |  |  | 18.1158 |  |  | 46.0522 |  |  | 102.8081 |  |  | 316.5486 |  |  | #NUM! |  |  | #NUM! |  |  | 866.5226 |  |  | 492.4772 |  |  | 551.3134
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.7062 | 383.5189 |  | 6.5158 | 3409.2453 |  | 23.0522 | 8347.9895 |  | 63.4081 | 16259.7527 |  | 255.5486 | 27278.807 |  | 18000 | 39814.1618 |  | 18000 | 52606.0924 |  | 18000 | 64831.3242 |  | 18000 | 75267.1548 |  | 18000 | 88256.6584
[13 empty] | Next iteration flow rate |  |  | 391.1893 | Abs Value of | Flow this | 3443.3378 | Abs Value of | Flow this | 8431.4694 | Abs Value of | Flow this | 16422.3503 | Abs Value of | Flow this | 27551.5951 | Abs Value of | Flow this | 40212.3034 | Abs Value of | Flow this | 53132.1533 | Abs Value of | Flow this | 65479.6375 | Abs Value of | Flow this | 76019.8263 | Abs Value of | Flow this | 89139.2249 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2253 |  |  | 89.8558 |  |  | 87.9855 |  |  | 81.7147 |  |  | 66.2622 |  |  | 39.1731 |  |  | 1.0942 |  |  | -45.1487 |  |  | -92.24 |  |  | -160.6555
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43522 |  |  | 0.43344 |  |  | 0.42442 |  |  | 0.39417 |  |  | 0.31963 |  |  | 0.18896 |  |  | 0.0052781 |  |  | -0.21779 |  |  | -0.44494 |  |  | -0.77496
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2253 |  |  | 29.8558 |  |  | 27.9855 |  |  | 21.7147 |  |  | 6.2622 |  |  | -20.8269 |  |  | -58.9058 |  |  | -105.1487 |  |  | -152.24 |  |  | -220.6555
[13 empty] | Press drop ratio this iteration |  |  | 0.335 |  |  | 0.33226 |  |  | 0.31807 |  |  | 0.26574 |  |  | 0.094506 |  |  | -0.53166 |  |  | -53.8348 |  |  | 2.3289 |  |  | 1.6505 |  |  | 1.3735
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82699 |  |  | 0.83281 |  |  | 0.85835 |  |  | 0.94806 |  |  | 1.3097 |  |  | 34.7417 |  |  | -0.63206 |  |  | 0.068382 |  |  | -0.21538
[13 empty] | C Non choked w/ reducers | 5 |  | 2.0643 |  |  | 18.2993 |  |  | 46.5511 |  |  | 104.246 |  |  | 331.494 |  |  | #NUM! |  |  | #NUM! |  |  | -392.7271 |  |  | 2788.9624 |  |  | -875.2651
[13 empty] | C Choked w/ reducers | 5 |  | 1.8484 |  |  | 16.3457 |  |  | 41.1641 |  |  | 87.4522 |  |  | 185.9926 |  |  | 483.3986 |  |  | 24575.2482 |  |  | 823.4795 |  |  | 478.014 |  |  | 539.6927
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.0643 |  |  | 18.2993 |  |  | 46.5511 |  |  | 104.246 |  |  | 331.494 |  |  | #NUM! |  |  | #NUM! |  |  | 823.4795 |  |  | 478.014 |  |  | 539.6927
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.6657 | 391.1893 |  | 6.6993 | 3443.3378 |  | 23.5511 | 8431.4694 |  | 64.846 | 16422.3503 |  | 270.494 | 27551.5951 |  | 18000 | 40212.3034 |  | 18000 | 53132.1533 |  | 18000 | 65479.6375 |  | 18000 | 76019.8263 |  | 18000 | 89139.2249
[13 empty] | Next iteration flow rate |  |  | 399.0131 | Abs Value of | Flow this | 3477.7712 | Abs Value of | Flow this | 8515.7841 | Abs Value of | Flow this | 16586.5738 | Abs Value of | Flow this | 27827.111 | Abs Value of | Flow this | 40614.4265 | Abs Value of | Flow this | 53663.4748 | Abs Value of | Flow this | 66134.4339 | Abs Value of | Flow this | 76780.0246 | Abs Value of | Flow this | 90030.6172 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2252 |  |  | 89.8483 |  |  | 87.9404 |  |  | 81.5435 |  |  | 65.7804 |  |  | 38.1468 |  |  | -0.69744 |  |  | -47.8698 |  |  | -95.9077 |  |  | -165.6983
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43522 |  |  | 0.43341 |  |  | 0.4242 |  |  | 0.39335 |  |  | 0.31731 |  |  | 0.18401 |  |  | -0.0033643 |  |  | -0.23091 |  |  | -0.46263 |  |  | -0.79929
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2252 |  |  | 29.8483 |  |  | 27.9404 |  |  | 21.5435 |  |  | 5.7804 |  |  | -21.8532 |  |  | -60.6974 |  |  | -107.8698 |  |  | -155.9077 |  |  | -225.6983
[13 empty] | Press drop ratio this iteration |  |  | 0.335 |  |  | 0.33221 |  |  | 0.31772 |  |  | 0.2642 |  |  | 0.087875 |  |  | -0.57287 |  |  | 87.0293 |  |  | 2.2534 |  |  | 1.6256 |  |  | 1.3621
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82702 |  |  | 0.83299 |  |  | 0.85917 |  |  | 0.95171 |  |  | 1.3337 |  |  | -53.5468 |  |  | -0.57912 |  |  | 0.082423 |  |  | -0.20533
[13 empty] | C Non choked w/ reducers | 5 |  | 2.1056 |  |  | 18.4848 |  |  | 47.0563 |  |  | 105.7156 |  |  | 348.4161 |  |  | #NUM! |  |  | -37.919 |  |  | -415.092 |  |  | 2264.7596 |  |  | -902.8425
[13 empty] | C Choked w/ reducers | 5 |  | 1.8854 |  |  | 16.5105 |  |  | 41.597 |  |  | 88.5121 |  |  | 189.2283 |  |  | 501.3673 |  |  | 38941.211 |  |  | 784.4362 |  |  | 464.3314 |  |  | 528.5006
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.1056 |  |  | 18.4848 |  |  | 47.0563 |  |  | 105.7156 |  |  | 348.4161 |  |  | #NUM! |  |  | 38941.211 |  |  | 784.4362 |  |  | 464.3314 |  |  | 528.5006
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.6244 | 399.0131 |  | 6.8848 | 3477.7712 |  | 24.0563 | 8515.7841 |  | 66.3156 | 16586.5738 |  | 287.4161 | 27827.111 |  | 18000 | 40614.4265 |  | 18000 | 53663.4748 |  | 18000 | 66134.4339 |  | 18000 | 76780.0246 |  | 18000 | 90030.6172
[13 empty] | Next iteration flow rate |  |  | 406.9933 | Abs Value of | Flow this | 3512.5489 | Abs Value of | Flow this | 8600.9419 | Abs Value of | Flow this | 16752.4395 | Abs Value of | Flow this | 28105.3822 | Abs Value of | Flow this | 41020.5707 | Abs Value of | Flow this | 54200.1096 | Abs Value of | Flow this | 66795.7782 | Abs Value of | Flow this | 77547.8248 | Abs Value of | Flow this | 90930.9234 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2249 |  |  | 89.8406 |  |  | 87.8944 |  |  | 81.3689 |  |  | 65.289 |  |  | 37.1 |  |  | -2.5251 |  |  | -50.6456 |  |  | -99.6491 |  |  | -170.8425
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43522 |  |  | 0.43337 |  |  | 0.42398 |  |  | 0.3925 |  |  | 0.31494 |  |  | 0.17896 |  |  | -0.01218 |  |  | -0.2443 |  |  | -0.48068 |  |  | -0.8241
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2249 |  |  | 29.8406 |  |  | 27.8944 |  |  | 21.3689 |  |  | 5.289 |  |  | -22.9 |  |  | -62.5251 |  |  | -110.6456 |  |  | -159.6491 |  |  | -230.8425
[13 empty] | Press drop ratio this iteration |  |  | 0.335 |  |  | 0.33215 |  |  | 0.31736 |  |  | 0.26262 |  |  | 0.081009 |  |  | -0.61725 |  |  | 24.7616 |  |  | 2.1847 |  |  | 1.6021 |  |  | 1.3512
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82705 |  |  | 0.83318 |  |  | 0.86001 |  |  | 0.95548 |  |  | 1.3596 |  |  | -14.5197 |  |  | -0.53098 |  |  | 0.095681 |  |  | -0.19568
[13 empty] | C Non choked w/ reducers | 5 |  | 2.1477 |  |  | 18.6722 |  |  | 47.5678 |  |  | 107.218 |  |  | 367.8097 |  |  | #NUM! |  |  | -73.1354 |  |  | -438.9343 |  |  | 1910.3208 |  |  | -931.7579
[13 empty] | C Choked w/ reducers | 5 |  | 1.9231 |  |  | 16.677 |  |  | 42.035 |  |  | 89.589 |  |  | 192.5592 |  |  | 520.6698 |  |  | 10863.2642 |  |  | 748.8569 |  |  | 451.3668 |  |  | 517.713
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.1477 |  |  | 18.6722 |  |  | 47.5678 |  |  | 107.218 |  |  | 367.8097 |  |  | #NUM! |  |  | 10863.2642 |  |  | 748.8569 |  |  | 451.3668 |  |  | 517.713
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.5823 | 406.9933 |  | 7.0722 | 3512.5489 |  | 24.5678 | 8600.9419 |  | 67.818 | 16752.4395 |  | 306.8097 | 28105.3822 |  | 18000 | 41020.5707 |  | 18000 | 54200.1096 |  | 18000 | 66795.7782 |  | 18000 | 77547.8248 |  | 18000 | 90930.9234
[13 empty] | Next iteration flow rate |  |  | 415.1332 | Abs Value of | Flow this | 3547.6744 | Abs Value of | Flow this | 8686.9513 | Abs Value of | Flow this | 16919.9639 | Abs Value of | Flow this | 28386.436 | Abs Value of | Flow this | 41430.7764 | Abs Value of | Flow this | 54742.1107 | Abs Value of | Flow this | 67463.736 | Abs Value of | Flow this | 78323.3031 | Abs Value of | Flow this | 91840.2326 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2247 |  |  | 89.8328 |  |  | 87.8475 |  |  | 81.1908 |  |  | 64.7877 |  |  | 36.032 |  |  | -4.3895 |  |  | -53.4772 |  |  | -103.4656 |  |  | -176.0901
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43522 |  |  | 0.43333 |  |  | 0.42375 |  |  | 0.39164 |  |  | 0.31252 |  |  | 0.17381 |  |  | -0.021174 |  |  | -0.25796 |  |  | -0.49909 |  |  | -0.84941
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2247 |  |  | 29.8328 |  |  | 27.8475 |  |  | 21.1908 |  |  | 4.7877 |  |  | -23.968 |  |  | -64.3895 |  |  | -113.4772 |  |  | -163.4656 |  |  | -236.0901
[13 empty] | Press drop ratio this iteration |  |  | 0.33499 |  |  | 0.33209 |  |  | 0.317 |  |  | 0.261 |  |  | 0.073898 |  |  | -0.66518 |  |  | 14.6691 |  |  | 2.122 |  |  | 1.5799 |  |  | 1.3407
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82708 |  |  | 0.83337 |  |  | 0.86087 |  |  | 0.95939 |  |  | 1.3875 |  |  | -8.1941 |  |  | -0.48702 |  |  | 0.10822 |  |  | -0.18642
[13 empty] | C Non choked w/ reducers | 5 |  | 2.1906 |  |  | 18.8615 |  |  | 48.0857 |  |  | 108.7545 |  |  | 390.364 |  |  | #NUM! |  |  | -97.827 |  |  | -464.4627 |  |  | 1654.4886 |  |  | -962.1242
[13 empty] | C Choked w/ reducers | 5 |  | 1.9615 |  |  | 16.8453 |  |  | 42.478 |  |  | 90.6834 |  |  | 195.9897 |  |  | 541.4625 |  |  | 6311.6927 |  |  | 716.2971 |  |  | 439.0643 |  |  | 507.3078
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.1906 |  |  | 18.8615 |  |  | 48.0857 |  |  | 108.7545 |  |  | 390.364 |  |  | #NUM! |  |  | 6311.6927 |  |  | 716.2971 |  |  | 439.0643 |  |  | 507.3078
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.5394 | 415.1332 |  | 7.2615 | 3547.6744 |  | 25.0857 | 8686.9513 |  | 69.3545 | 16919.9639 |  | 329.364 | 28386.436 |  | 18000 | 41430.7764 |  | 18000 | 54742.1107 |  | 18000 | 67463.736 |  | 18000 | 78323.3031 |  | 18000 | 91840.2326
[13 empty] | Next iteration flow rate |  |  | 423.4359 | Abs Value of | Flow this | 3583.1511 | Abs Value of | Flow this | 8773.8208 | Abs Value of | Flow this | 17089.1635 | Abs Value of | Flow this | 28670.3003 | Abs Value of | Flow this | 41845.0842 | Abs Value of | Flow this | 55289.5318 | Abs Value of | Flow this | 68138.3733 | Abs Value of | Flow this | 79106.5361 | Abs Value of | Flow this | 92758.6349 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2245 |  |  | 89.8248 |  |  | 87.7996 |  |  | 81.0091 |  |  | 64.2763 |  |  | 34.9427 |  |  | -6.2913 |  |  | -56.3657 |  |  | -107.3589 |  |  | -181.4431
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43522 |  |  | 0.43329 |  |  | 0.42352 |  |  | 0.39077 |  |  | 0.31005 |  |  | 0.16855 |  |  | -0.030348 |  |  | -0.27189 |  |  | -0.51787 |  |  | -0.87524
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2245 |  |  | 29.8248 |  |  | 27.7996 |  |  | 21.0091 |  |  | 4.2763 |  |  | -25.0573 |  |  | -66.2913 |  |  | -116.3657 |  |  | -167.3589 |  |  | -241.4431
[13 empty] | Press drop ratio this iteration |  |  | 0.33499 |  |  | 0.33203 |  |  | 0.31663 |  |  | 0.25934 |  |  | 0.06653 |  |  | -0.7171 |  |  | 10.537 |  |  | 2.0645 |  |  | 1.5589 |  |  | 1.3307
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82711 |  |  | 0.83357 |  |  | 0.86176 |  |  | 0.96344 |  |  | 1.4178 |  |  | -5.6042 |  |  | -0.44673 |  |  | 0.12009 |  |  | -0.17752
[13 empty] | C Non choked w/ reducers | 5 |  | 2.2345 |  |  | 19.0528 |  |  | 48.6102 |  |  | 110.3264 |  |  | 417.0729 |  |  | #NUM! |  |  | -118.9272 |  |  | -491.9199 |  |  | 1461.0054 |  |  | -994.0671
[13 empty] | C Choked w/ reducers | 5 |  | 2.0008 |  |  | 17.0152 |  |  | 42.9262 |  |  | 91.7957 |  |  | 199.5245 |  |  | 563.9267 |  |  | 4447.7154 |  |  | 686.3856 |  |  | 427.3734 |  |  | 497.2643
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.2345 |  |  | 19.0528 |  |  | 48.6102 |  |  | 110.3264 |  |  | 417.0729 |  |  | #NUM! |  |  | 4447.7154 |  |  | 686.3856 |  |  | 427.3734 |  |  | 497.2643
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.4955 | 423.4359 |  | 7.4528 | 3583.1511 |  | 25.6102 | 8773.8208 |  | 70.9264 | 17089.1635 |  | 356.0729 | 28670.3003 |  | 18000 | 41845.0842 |  | 18000 | 55289.5318 |  | 18000 | 68138.3733 |  | 18000 | 79106.5361 |  | 18000 | 92758.6349
[13 empty] | Next iteration flow rate |  |  | 431.9046 | Abs Value of | Flow this | 3618.9826 | Abs Value of | Flow this | 8861.5591 | Abs Value of | Flow this | 17260.0552 | Abs Value of | Flow this | 28957.0033 | Abs Value of | Flow this | 42263.535 | Abs Value of | Flow this | 55842.4271 | Abs Value of | Flow this | 68819.7571 | Abs Value of | Flow this | 79897.6015 | Abs Value of | Flow this | 93686.2213 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2243 |  |  | 89.8166 |  |  | 87.7507 |  |  | 80.8238 |  |  | 63.7546 |  |  | 33.8314 |  |  | -8.2314 |  |  | -59.3123 |  |  | -111.3305 |  |  | -186.9037
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43522 |  |  | 0.43325 |  |  | 0.42329 |  |  | 0.38987 |  |  | 0.30754 |  |  | 0.16319 |  |  | -0.039706 |  |  | -0.28611 |  |  | -0.53703 |  |  | -0.90158
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2243 |  |  | 29.8166 |  |  | 27.7507 |  |  | 20.8238 |  |  | 3.7546 |  |  | -26.1686 |  |  | -68.2314 |  |  | -119.3123 |  |  | -171.3305 |  |  | -246.9037
[13 empty] | Press drop ratio this iteration |  |  | 0.33499 |  |  | 0.33197 |  |  | 0.31624 |  |  | 0.25764 |  |  | 0.058891 |  |  | -0.7735 |  |  | 8.2892 |  |  | 2.0116 |  |  | 1.5389 |  |  | 1.321
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82715 |  |  | 0.83377 |  |  | 0.86266 |  |  | 0.96763 |  |  | 1.4506 |  |  | -4.1953 |  |  | -0.40967 |  |  | 0.13134 |  |  | -0.16897
[13 empty] | C Non choked w/ reducers | 5 |  | 2.2792 |  |  | 19.2461 |  |  | 49.1414 |  |  | 111.9351 |  |  | 449.4337 |  |  | #NUM! |  |  | -138.2665 |  |  | -521.591 |  |  | 1309.4541 |  |  | -1027.7264
[13 empty] | C Choked w/ reducers | 5 |  | 2.0408 |  |  | 17.187 |  |  | 43.3796 |  |  | 92.9262 |  |  | 203.1687 |  |  | 588.2748 |  |  | 3433.4149 |  |  | 658.8095 |  |  | 416.2488 |  |  | 487.5635
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.2792 |  |  | 19.2461 |  |  | 49.1414 |  |  | 111.9351 |  |  | 449.4337 |  |  | #NUM! |  |  | 3433.4149 |  |  | 658.8095 |  |  | 416.2488 |  |  | 487.5635
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.4508 | 431.9046 |  | 7.6461 | 3618.9826 |  | 26.1414 | 8861.5591 |  | 72.5351 | 17260.0552 |  | 388.4337 | 28957.0033 |  | 18000 | 42263.535 |  | 18000 | 55842.4271 |  | 18000 | 68819.7571 |  | 18000 | 79897.6015 |  | 18000 | 93686.2213
[13 empty] | Next iteration flow rate |  |  | 440.5427 | Abs Value of | Flow this | 3655.1724 | Abs Value of | Flow this | 8950.1746 | Abs Value of | Flow this | 17432.6557 | Abs Value of | Flow this | 29246.5734 | Abs Value of | Flow this | 42686.1704 | Abs Value of | Flow this | 56400.8514 | Abs Value of | Flow this | 69507.9546 | Abs Value of | Flow this | 80696.5775 | Abs Value of | Flow this | 94623.0835 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2241 |  |  | 89.8083 |  |  | 87.7009 |  |  | 80.6347 |  |  | 63.2224 |  |  | 32.6978 |  |  | -10.2105 |  |  | -62.3181 |  |  | -115.3818 |  |  | -192.4741
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43522 |  |  | 0.43321 |  |  | 0.42305 |  |  | 0.38896 |  |  | 0.30497 |  |  | 0.15773 |  |  | -0.049253 |  |  | -0.30061 |  |  | -0.55657 |  |  | -0.92845
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2241 |  |  | 29.8083 |  |  | 27.7009 |  |  | 20.6347 |  |  | 3.2224 |  |  | -27.3022 |  |  | -70.2105 |  |  | -122.3181 |  |  | -175.3818 |  |  | -252.4741
[13 empty] | Press drop ratio this iteration |  |  | 0.33499 |  |  | 0.33191 |  |  | 0.31586 |  |  | 0.2559 |  |  | 0.05097 |  |  | -0.83499 |  |  | 6.8763 |  |  | 1.9628 |  |  | 1.52 |  |  | 1.3117
[13 empty] | Expansion factor | 12 |  | 0.82553 |  |  | 0.82718 |  |  | 0.83397 |  |  | 0.86359 |  |  | 0.97199 |  |  | 1.4864 |  |  | -3.3098 |  |  | -0.37548 |  |  | 0.14202 |  |  | -0.16075
[13 empty] | C Non choked w/ reducers | 5 |  | 2.3247 |  |  | 19.4414 |  |  | 49.6794 |  |  | 113.5821 |  |  | 489.8317 |  |  | #NUM! |  |  | -156.6772 |  |  | -553.8141 |  |  | 1187.4587 |  |  | -1063.2586
[13 empty] | C Choked w/ reducers | 5 |  | 2.0816 |  |  | 17.3604 |  |  | 43.8383 |  |  | 94.0756 |  |  | 206.9276 |  |  | 614.7567 |  |  | 2795.6017 |  |  | 633.3033 |  |  | 405.6495 |  |  | 478.1874
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.3247 |  |  | 19.4414 |  |  | 49.6794 |  |  | 113.5821 |  |  | 489.8317 |  |  | #NUM! |  |  | 2795.6017 |  |  | 633.3033 |  |  | 405.6495 |  |  | 478.1874
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.4053 | 440.5427 |  | 7.8414 | 3655.1724 |  | 26.6794 | 8950.1746 |  | 74.1821 | 17432.6557 |  | 428.8317 | 29246.5734 |  | 18000 | 42686.1704 |  | 18000 | 56400.8514 |  | 18000 | 69507.9546 |  | 18000 | 80696.5775 |  | 18000 | 94623.0835
[13 empty] | Next iteration flow rate |  |  | 449.3535 | Abs Value of | Flow this | 3691.7242 | Abs Value of | Flow this | 9039.6764 | Abs Value of | Flow this | 17606.9823 | Abs Value of | Flow this | 29539.0391 | Abs Value of | Flow this | 43113.0321 | Abs Value of | Flow this | 56964.8599 | Abs Value of | Flow this | 70203.0342 | Abs Value of | Flow this | 81503.5433 | Abs Value of | Flow this | 95569.3143 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2238 |  |  | 89.7999 |  |  | 87.65 |  |  | 80.4419 |  |  | 62.6796 |  |  | 31.5414 |  |  | -12.2293 |  |  | -65.3843 |  |  | -119.5146 |  |  | -198.1565
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43522 |  |  | 0.43317 |  |  | 0.4228 |  |  | 0.38803 |  |  | 0.30235 |  |  | 0.15215 |  |  | -0.058991 |  |  | -0.3154 |  |  | -0.57651 |  |  | -0.95586
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2238 |  |  | 29.7999 |  |  | 27.65 |  |  | 20.4419 |  |  | 2.6796 |  |  | -28.4586 |  |  | -72.2293 |  |  | -125.3843 |  |  | -179.5146 |  |  | -258.1565
[13 empty] | Press drop ratio this iteration |  |  | 0.33499 |  |  | 0.33185 |  |  | 0.31546 |  |  | 0.25412 |  |  | 0.042751 |  |  | -0.90226 |  |  | 5.9062 |  |  | 1.9177 |  |  | 1.502 |  |  | 1.3028
[13 empty] | Expansion factor | 12 |  | 0.82554 |  |  | 0.82721 |  |  | 0.83418 |  |  | 0.86454 |  |  | 0.9765 |  |  | 1.5256 |  |  | -2.7018 |  |  | -0.34384 |  |  | 0.15217 |  |  | -0.15284
[13 empty] | C Non choked w/ reducers | 5 |  | 2.3713 |  |  | 19.6387 |  |  | 50.2243 |  |  | 115.269 |  |  | 542.3577 |  |  | #NUM! |  |  | -174.6396 |  |  | -588.9937 |  |  | 1087.0803 |  |  | -1100.8392
[13 empty] | C Choked w/ reducers | 5 |  | 2.1233 |  |  | 17.5357 |  |  | 44.3024 |  |  | 95.2441 |  |  | 210.8069 |  |  | 643.6685 |  |  | 2357.4359 |  |  | 609.6404 |  |  | 395.5384 |  |  | 469.1196
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.3713 |  |  | 19.6387 |  |  | 50.2243 |  |  | 115.269 |  |  | 542.3577 |  |  | #NUM! |  |  | 2357.4359 |  |  | 609.6404 |  |  | 395.5384 |  |  | 469.1196
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.3587 | 449.3535 |  | 8.0387 | 3691.7242 |  | 27.2243 | 9039.6764 |  | 75.869 | 17606.9823 |  | 481.3577 | 29539.0391 |  | 18000 | 43113.0321 |  | 18000 | 56964.8599 |  | 18000 | 70203.0342 |  | 18000 | 81503.5433 |  | 18000 | 95569.3143
[13 empty] | Next iteration flow rate |  |  | 458.3406 | Abs Value of | Flow this | 3728.6414 | Abs Value of | Flow this | 9130.0732 | Abs Value of | Flow this | 17783.0521 | Abs Value of | Flow this | 29834.4295 | Abs Value of | Flow this | 43544.1624 | Abs Value of | Flow this | 57534.5085 | Abs Value of | Flow this | 70905.0645 | Abs Value of | Flow this | 82318.5787 | Abs Value of | Flow this | 96525.0075 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2235 |  |  | 89.7912 |  |  | 87.5982 |  |  | 80.2451 |  |  | 62.1258 |  |  | 30.3617 |  |  | -14.2888 |  |  | -68.5121 |  |  | -123.7305 |  |  | -203.9531
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43522 |  |  | 0.43313 |  |  | 0.42255 |  |  | 0.38708 |  |  | 0.29968 |  |  | 0.14646 |  |  | -0.068925 |  |  | -0.33049 |  |  | -0.59684 |  |  | -0.98382
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2235 |  |  | 29.7912 |  |  | 27.5982 |  |  | 20.2451 |  |  | 2.1258 |  |  | -29.6383 |  |  | -74.2888 |  |  | -128.5121 |  |  | -183.7305 |  |  | -263.9531
[13 empty] | Press drop ratio this iteration |  |  | 0.33499 |  |  | 0.33178 |  |  | 0.31505 |  |  | 0.25229 |  |  | 0.034218 |  |  | -0.97617 |  |  | 5.1991 |  |  | 1.8758 |  |  | 1.4849 |  |  | 1.2942
[13 empty] | Expansion factor | 12 |  | 0.82554 |  |  | 0.82724 |  |  | 0.83439 |  |  | 0.86551 |  |  | 0.98119 |  |  | 1.5687 |  |  | -2.2586 |  |  | -0.31448 |  |  | 0.16183 |  |  | -0.14523
[13 empty] | C Non choked w/ reducers | 5 |  | 2.4187 |  |  | 19.8382 |  |  | 50.7762 |  |  | 116.9974 |  |  | 614.7865 |  |  | #NUM! |  |  | -192.4766 |  |  | -627.6187 |  |  | 1002.992 |  |  | -1140.6657
[13 empty] | C Choked w/ reducers | 5 |  | 2.1657 |  |  | 17.7128 |  |  | 44.7719 |  |  | 96.4324 |  |  | 214.8128 |  |  | 675.3638 |  |  | 2037.836 |  |  | 587.626 |  |  | 385.8818 |  |  | 460.3446
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.4187 |  |  | 19.8382 |  |  | 50.7762 |  |  | 116.9974 |  |  | 614.7865 |  |  | #NUM! |  |  | 2037.836 |  |  | 587.626 |  |  | 385.8818 |  |  | 460.3446
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.3113 | 458.3406 |  | 8.2382 | 3728.6414 |  | 27.7762 | 9130.0732 |  | 77.5974 | 17783.0521 |  | 553.7865 | 29834.4295 |  | 18000 | 43544.1624 |  | 18000 | 57534.5085 |  | 18000 | 70905.0645 |  | 18000 | 82318.5787 |  | 18000 | 96525.0075
[13 empty] | Next iteration flow rate |  |  | 467.5074 | Abs Value of | Flow this | 3765.9278 | Abs Value of | Flow this | 9221.3739 | Abs Value of | Flow this | 17960.8826 | Abs Value of | Flow this | 30132.7738 | Abs Value of | Flow this | 43979.604 | Abs Value of | Flow this | 58109.8536 | Abs Value of | Flow this | 71614.1152 | Abs Value of | Flow this | 83141.7645 | Abs Value of | Flow this | 97490.2575 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2233 |  |  | 89.7824 |  |  | 87.5453 |  |  | 80.0444 |  |  | 61.5609 |  |  | 29.1584 |  |  | -16.3896 |  |  | -71.7029 |  |  | -128.0311 |  |  | -209.8661
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43521 |  |  | 0.43309 |  |  | 0.4223 |  |  | 0.38611 |  |  | 0.29695 |  |  | 0.14065 |  |  | -0.079059 |  |  | -0.34588 |  |  | -0.61759 |  |  | -1.0123
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2233 |  |  | 29.7824 |  |  | 27.5453 |  |  | 20.0444 |  |  | 1.5609 |  |  | -30.8416 |  |  | -76.3896 |  |  | -131.7029 |  |  | -188.0311 |  |  | -269.8661
[13 empty] | Press drop ratio this iteration |  |  | 0.33498 |  |  | 0.33172 |  |  | 0.31464 |  |  | 0.25042 |  |  | 0.025356 |  |  | -1.0577 |  |  | 4.6609 |  |  | 1.8368 |  |  | 1.4686 |  |  | 1.2859
[13 empty] | Expansion factor | 12 |  | 0.82554 |  |  | 0.82728 |  |  | 0.83461 |  |  | 0.86651 |  |  | 0.98606 |  |  | 1.6162 |  |  | -1.9213 |  |  | -0.28717 |  |  | 0.17102 |  |  | -0.13789
[13 empty] | C Non choked w/ reducers | 5 |  | 2.4671 |  |  | 20.0397 |  |  | 51.3353 |  |  | 118.7692 |  |  | 724.3548 |  |  | #NUM! |  |  | -210.4324 |  |  | -670.2864 |  |  | 931.486 |  |  | -1182.9615
[13 empty] | C Choked w/ reducers | 5 |  | 2.209 |  |  | 17.8916 |  |  | 45.2469 |  |  | 97.641 |  |  | 218.9519 |  |  | 710.2682 |  |  | 1794.3909 |  |  | 567.0919 |  |  | 376.6491 |  |  | 451.8479
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.4671 |  |  | 20.0397 |  |  | 51.3353 |  |  | 118.7692 |  |  | 724.3548 |  |  | #NUM! |  |  | 1794.3909 |  |  | 567.0919 |  |  | 376.6491 |  |  | 451.8479
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.2629 | 467.5074 |  | 8.4397 | 3765.9278 |  | 28.3353 | 9221.3739 |  | 79.3692 | 17960.8826 |  | 663.3548 | 30132.7738 |  | 18000 | 43979.604 |  | 18000 | 58109.8536 |  | 18000 | 71614.1152 |  | 18000 | 83141.7645 |  | 18000 | 97490.2575
[13 empty] | Next iteration flow rate |  |  | 476.8576 | Abs Value of | Flow this | 3803.5871 | Abs Value of | Flow this | 9313.5876 | Abs Value of | Flow this | 18140.4914 | Abs Value of | Flow this | 30434.1015 | Abs Value of | Flow this | 44419.4001 | Abs Value of | Flow this | 58690.9521 | Abs Value of | Flow this | 72330.2563 | Abs Value of | Flow this | 83973.1821 | Abs Value of | Flow this | 98465.1601 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.223 |  |  | 89.7734 |  |  | 87.4913 |  |  | 79.8397 |  |  | 60.9847 |  |  | 27.9308 |  |  | -18.5327 |  |  | -74.9577 |  |  | -132.4182 |  |  | -215.8981
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43521 |  |  | 0.43304 |  |  | 0.42204 |  |  | 0.38513 |  |  | 0.29417 |  |  | 0.13473 |  |  | -0.089397 |  |  | -0.36158 |  |  | -0.63875 |  |  | -1.0414
[13 empty] | Delta P at this iteration flow rate |  |  | 30.223 |  |  | 29.7734 |  |  | 27.4913 |  |  | 19.8397 |  |  | 0.98467 |  |  | -32.0692 |  |  | -78.5327 |  |  | -134.9577 |  |  | -192.4182 |  |  | -275.8981
[13 empty] | Press drop ratio this iteration |  |  | 0.33498 |  |  | 0.33165 |  |  | 0.31422 |  |  | 0.24849 |  |  | 0.016146 |  |  | -1.1482 |  |  | 4.2375 |  |  | 1.8005 |  |  | 1.4531 |  |  | 1.2779
[13 empty] | Expansion factor | 12 |  | 0.82554 |  |  | 0.82731 |  |  | 0.83483 |  |  | 0.86754 |  |  | 0.99113 |  |  | 1.6689 |  |  | -1.6559 |  |  | -0.26171 |  |  | 0.17979 |  |  | -0.13082
[13 empty] | C Non choked w/ reducers | 5 |  | 2.5164 |  |  | 20.2433 |  |  | 51.9017 |  |  | 120.5861 |  |  | 920.7393 |  |  | #NUM! |  |  | -228.7099 |  |  | -717.7348 |  |  | 869.9021 |  |  | -1227.9799
[13 empty] | C Choked w/ reducers | 5 |  | 2.2532 |  |  | 18.0724 |  |  | 45.7276 |  |  | 98.8703 |  |  | 223.231 |  |  | 748.8989 |  |  | 1602.7622 |  |  | 547.892 |  |  | 367.8123 |  |  | 443.616
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.5164 |  |  | 20.2433 |  |  | 51.9017 |  |  | 120.5861 |  |  | 920.7393 |  |  | #NUM! |  |  | 1602.7622 |  |  | 547.892 |  |  | 367.8123 |  |  | 443.616
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.2136 | 476.8576 |  | 8.6433 | 3803.5871 |  | 28.9017 | 9313.5876 |  | 81.1861 | 18140.4914 |  | 859.7393 | 30434.1015 |  | 18000 | 44419.4001 |  | 18000 | 58690.9521 |  | 18000 | 72330.2563 |  | 18000 | 83973.1821 |  | 18000 | 98465.1601
[13 empty] | Next iteration flow rate |  |  | 486.3947 | Abs Value of | Flow this | 3841.623 | Abs Value of | Flow this | 9406.7235 | Abs Value of | Flow this | 18321.8964 | Abs Value of | Flow this | 30738.4425 | Abs Value of | Flow this | 44863.5941 | Abs Value of | Flow this | 59277.8616 | Abs Value of | Flow this | 73053.5589 | Abs Value of | Flow this | 84812.9139 | Abs Value of | Flow this | 99449.8117 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2227 |  |  | 89.7642 |  |  | 87.4363 |  |  | 79.6308 |  |  | 60.3968 |  |  | 26.6786 |  |  | -20.7188 |  |  | -78.278 |  |  | -136.8934 |  |  | -222.0512
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43521 |  |  | 0.433 |  |  | 0.42177 |  |  | 0.38412 |  |  | 0.29134 |  |  | 0.12869 |  |  | -0.099942 |  |  | -0.37759 |  |  | -0.66034 |  |  | -1.0711
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2227 |  |  | 29.7642 |  |  | 27.4363 |  |  | 19.6308 |  |  | 0.39683 |  |  | -33.3214 |  |  | -80.7188 |  |  | -138.278 |  |  | -196.8934 |  |  | -282.0512
[13 empty] | Press drop ratio this iteration |  |  | 0.33498 |  |  | 0.33158 |  |  | 0.31379 |  |  | 0.24652 |  |  | 0.0065705 |  |  | -1.249 |  |  | 3.8959 |  |  | 1.7665 |  |  | 1.4383 |  |  | 1.2702
[13 empty] | Expansion factor | 12 |  | 0.82554 |  |  | 0.82735 |  |  | 0.83506 |  |  | 0.86859 |  |  | 0.99639 |  |  | 1.7276 |  |  | -1.4418 |  |  | -0.23791 |  |  | 0.18815 |  |  | -0.12401
[13 empty] | C Non choked w/ reducers | 5 |  | 2.5668 |  |  | 20.449 |  |  | 52.4756 |  |  | 122.4503 |  |  | 1464.2048 |  |  | #NUM! |  |  | -247.4917 |  |  | -770.8875 |  |  | 816.2818 |  |  | -1276.0095
[13 empty] | C Choked w/ reducers | 5 |  | 2.2983 |  |  | 18.255 |  |  | 46.2139 |  |  | 100.1209 |  |  | 227.6577 |  |  | 791.8906 |  |  | 1447.9841 |  |  | 529.8988 |  |  | 359.3459 |  |  | 435.6364
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.5668 |  |  | 20.449 |  |  | 52.4756 |  |  | 122.4503 |  |  | 1464.2048 |  |  | #NUM! |  |  | 1447.9841 |  |  | 529.8988 |  |  | 359.3459 |  |  | 435.6364
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.1632 | 486.3947 |  | 8.849 | 3841.623 |  | 29.4756 | 9406.7235 |  | 83.0503 | 18321.8964 |  | 1403.2048 | 30738.4425 |  | 18000 | 44863.5941 |  | 18000 | 59277.8616 |  | 18000 | 73053.5589 |  | 18000 | 84812.9139 |  | 18000 | 99449.8117
[13 empty] | Next iteration flow rate |  |  | 496.1226 | Abs Value of | Flow this | 3880.0392 | Abs Value of | Flow this | 9500.7907 | Abs Value of | Flow this | 18505.1153 | Abs Value of | Flow this | 31045.827 | Abs Value of | Flow this | 45312.23 | Abs Value of | Flow this | 59870.6402 | Abs Value of | Flow this | 73784.0945 | Abs Value of | Flow this | 85661.0431 | Abs Value of | Flow this | 100444.3098 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2224 |  |  | 89.7548 |  |  | 87.3801 |  |  | 79.4178 |  |  | 59.7972 |  |  | 25.4012 |  |  | -22.9489 |  |  | -81.665 |  |  | -141.4586 |  |  | -228.3281
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43521 |  |  | 0.43295 |  |  | 0.4215 |  |  | 0.38309 |  |  | 0.28845 |  |  | 0.12253 |  |  | -0.1107 |  |  | -0.39393 |  |  | -0.68236 |  |  | -1.1014
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2224 |  |  | 29.7548 |  |  | 27.3801 |  |  | 19.4178 |  |  | -0.20282 |  |  | -34.5988 |  |  | -82.9489 |  |  | -141.665 |  |  | -201.4586 |  |  | -288.3281
[13 empty] | Press drop ratio this iteration |  |  | 0.33498 |  |  | 0.33151 |  |  | 0.31334 |  |  | 0.2445 |  |  | -0.0033917 |  |  | -1.3621 |  |  | 3.6145 |  |  | 1.7347 |  |  | 1.4242 |  |  | 1.2628
[13 empty] | Expansion factor | 12 |  | 0.82554 |  |  | 0.82739 |  |  | 0.83529 |  |  | 0.86967 |  |  | 1.0019 |  |  | 1.7935 |  |  | -1.2654 |  |  | -0.21564 |  |  | 0.19613 |  |  | -0.11744
[13 empty] | C Non choked w/ reducers | 5 |  | 2.6181 |  |  | 20.6569 |  |  | 53.057 |  |  | 124.3638 |  |  | #NUM! |  |  | #NUM! |  |  | -266.9532 |  |  | -830.9165 |  |  | 769.1511 |  |  | -1327.3807
[13 empty] | C Choked w/ reducers | 5 |  | 2.3443 |  |  | 18.4394 |  |  | 46.7061 |  |  | 101.3933 |  |  | 232.2401 |  |  | 840.0306 |  |  | 1320.3478 |  |  | 513.0008 |  |  | 351.2265 |  |  | 427.8971
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.6181 |  |  | 20.6569 |  |  | 53.057 |  |  | 124.3638 |  |  | #NUM! |  |  | #NUM! |  |  | 1320.3478 |  |  | 513.0008 |  |  | 351.2265 |  |  | 427.8971
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.1119 | 496.1226 |  | 9.0569 | 3880.0392 |  | 30.057 | 9500.7907 |  | 84.9638 | 18505.1153 |  | 18000 | 31045.827 |  | 18000 | 45312.23 |  | 18000 | 59870.6402 |  | 18000 | 73784.0945 |  | 18000 | 85661.0431 |  | 18000 | 100444.3098
[13 empty] | Next iteration flow rate |  |  | 506.0451 | Abs Value of | Flow this | 3918.8396 | Abs Value of | Flow this | 9595.7986 | Abs Value of | Flow this | 18690.1665 | Abs Value of | Flow this | 31356.2852 | Abs Value of | Flow this | 45765.3523 | Abs Value of | Flow this | 60469.3466 | Abs Value of | Flow this | 74521.9354 | Abs Value of | Flow this | 86517.6535 | Abs Value of | Flow this | 101448.7529 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2221 |  |  | 89.7453 |  |  | 87.3228 |  |  | 79.2005 |  |  | 59.1855 |  |  | 24.0982 |  |  | -25.2238 |  |  | -85.1201 |  |  | -146.1155 |  |  | -234.7311
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43521 |  |  | 0.43291 |  |  | 0.42122 |  |  | 0.38204 |  |  | 0.2855 |  |  | 0.11624 |  |  | -0.12167 |  |  | -0.4106 |  |  | -0.70482 |  |  | -1.1323
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2221 |  |  | 29.7453 |  |  | 27.3228 |  |  | 19.2005 |  |  | -0.81452 |  |  | -35.9018 |  |  | -85.2238 |  |  | -145.1201 |  |  | -206.1155 |  |  | -294.7311
[13 empty] | Press drop ratio this iteration |  |  | 0.33497 |  |  | 0.33144 |  |  | 0.31289 |  |  | 0.24243 |  |  | -0.013762 |  |  | -1.4898 |  |  | 3.3787 |  |  | 1.7049 |  |  | 1.4106 |  |  | 1.2556
[13 empty] | Expansion factor | 12 |  | 0.82554 |  |  | 0.82742 |  |  | 0.83553 |  |  | 0.87077 |  |  | 1.0076 |  |  | 1.8679 |  |  | -1.1177 |  |  | -0.19474 |  |  | 0.20376 |  |  | -0.11109
[13 empty] | C Non choked w/ reducers | 5 |  | 2.6705 |  |  | 20.867 |  |  | 53.6461 |  |  | 126.329 |  |  | #NUM! |  |  | #NUM! |  |  | -287.2717 |  |  | -899.3323 |  |  | 727.3797 |  |  | -1382.4734
[13 empty] | C Choked w/ reducers | 5 |  | 2.3912 |  |  | 18.6258 |  |  | 47.2041 |  |  | 102.6883 |  |  | 236.9867 |  |  | 894.3083 |  |  | 1213.28 |  |  | 497.0994 |  |  | 343.4327 |  |  | 420.3872
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.6705 |  |  | 20.867 |  |  | 53.6461 |  |  | 126.329 |  |  | #NUM! |  |  | #NUM! |  |  | 1213.28 |  |  | 497.0994 |  |  | 343.4327 |  |  | 420.3872
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.0595 | 506.0451 |  | 9.267 | 3918.8396 |  | 30.6461 | 9595.7986 |  | 86.929 | 18690.1665 |  | 18000 | 31356.2852 |  | 18000 | 45765.3523 |  | 18000 | 60469.3466 |  | 18000 | 74521.9354 |  | 18000 | 86517.6535 |  | 18000 | 101448.7529
[13 empty] | Next iteration flow rate |  |  | 516.166 | Abs Value of | Flow this | 3958.028 | Abs Value of | Flow this | 9691.7566 | Abs Value of | Flow this | 18877.0681 | Abs Value of | Flow this | 31669.8481 | Abs Value of | Flow this | 46223.0059 | Abs Value of | Flow this | 61074.0401 | Abs Value of | Flow this | 75267.1548 | Abs Value of | Flow this | 87382.8301 | Abs Value of | Flow this | 102463.2405 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2218 |  |  | 89.7355 |  |  | 87.2644 |  |  | 78.9788 |  |  | 58.5615 |  |  | 22.7689 |  |  | -27.5444 |  |  | -88.6446 |  |  | -150.8661 |  |  | -241.2628
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43521 |  |  | 0.43286 |  |  | 0.42094 |  |  | 0.38097 |  |  | 0.28249 |  |  | 0.10983 |  |  | -0.13287 |  |  | -0.4276 |  |  | -0.72774 |  |  | -1.1638
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2218 |  |  | 29.7355 |  |  | 27.2644 |  |  | 18.9788 |  |  | -1.4385 |  |  | -37.2311 |  |  | -87.5444 |  |  | -148.6446 |  |  | -210.8661 |  |  | -301.2628
[13 empty] | Press drop ratio this iteration |  |  | 0.33497 |  |  | 0.33137 |  |  | 0.31243 |  |  | 0.2403 |  |  | -0.024564 |  |  | -1.6352 |  |  | 3.1783 |  |  | 1.6769 |  |  | 1.3977 |  |  | 1.2487
[13 empty] | Expansion factor | 12 |  | 0.82554 |  |  | 0.82746 |  |  | 0.83577 |  |  | 0.87191 |  |  | 1.0135 |  |  | 1.9526 |  |  | -0.99204 |  |  | -0.1751 |  |  | 0.21106 |  |  | -0.10497
[13 empty] | C Non choked w/ reducers | 5 |  | 2.7239 |  |  | 21.0794 |  |  | 54.243 |  |  | 128.3483 |  |  | #NUM! |  |  | #NUM! |  |  | -308.6344 |  |  | -978.1163 |  |  | 690.0859 |  |  | -1441.727
[13 empty] | C Choked w/ reducers | 5 |  | 2.439 |  |  | 18.8141 |  |  | 47.7081 |  |  | 104.0063 |  |  | 241.9071 |  |  | 955.9834 |  |  | 1122.1714 |  |  | 482.1079 |  |  | 335.9447 |  |  | 413.0961
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.7239 |  |  | 21.0794 |  |  | 54.243 |  |  | 128.3483 |  |  | #NUM! |  |  | #NUM! |  |  | 1122.1714 |  |  | 482.1079 |  |  | 335.9447 |  |  | 413.0961
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.0061 | 516.166 |  | 9.4794 | 3958.028 |  | 31.243 | 9691.7566 |  | 88.9483 | 18877.0681 |  | 18000 | 31669.8481 |  | 18000 | 46223.0059 |  | 18000 | 61074.0401 |  | 18000 | 75267.1548 |  | 18000 | 87382.8301 |  | 18000 | 102463.2405
[13 empty] | Next iteration flow rate |  |  | 526.4893 | Abs Value of | Flow this | 3997.6083 | Abs Value of | Flow this | 9788.6742 | Abs Value of | Flow this | 19065.8388 | Abs Value of | Flow this | 31986.5466 | Abs Value of | Flow this | 46685.2359 | Abs Value of | Flow this | 61684.7805 | Abs Value of | Flow this | 76019.8263 | Abs Value of | Flow this | 88256.6584 | Abs Value of | Flow this | 103487.8729 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2214 |  |  | 89.7256 |  |  | 87.2048 |  |  | 78.7526 |  |  | 57.9249 |  |  | 21.4129 |  |  | -29.9117 |  |  | -92.24 |  |  | -155.7121 |  |  | -247.9259
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43521 |  |  | 0.43281 |  |  | 0.42065 |  |  | 0.37988 |  |  | 0.27942 |  |  | 0.10329 |  |  | -0.14429 |  |  | -0.44494 |  |  | -0.75112 |  |  | -1.1959
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2214 |  |  | 29.7256 |  |  | 27.2048 |  |  | 18.7526 |  |  | -2.0751 |  |  | -38.5871 |  |  | -89.9117 |  |  | -152.24 |  |  | -215.7121 |  |  | -307.9259
[13 empty] | Press drop ratio this iteration |  |  | 0.33497 |  |  | 0.33129 |  |  | 0.31196 |  |  | 0.23812 |  |  | -0.035823 |  |  | -1.802 |  |  | 3.0059 |  |  | 1.6505 |  |  | 1.3853 |  |  | 1.242
[13 empty] | Expansion factor | 12 |  | 0.82554 |  |  | 0.8275 |  |  | 0.83602 |  |  | 0.87307 |  |  | 1.0197 |  |  | 2.0498 |  |  | -0.88399 |  |  | -0.15661 |  |  | 0.21805 |  |  | -0.099054
[13 empty] | C Non choked w/ reducers | 5 |  | 2.7784 |  |  | 21.2939 |  |  | 54.848 |  |  | 130.4242 |  |  | #NUM! |  |  | #NUM! |  |  | -331.2458 |  |  | -1069.9208 |  |  | 656.572 |  |  | -1505.652
[13 empty] | C Choked w/ reducers | 5 |  | 2.4878 |  |  | 19.0044 |  |  | 48.2181 |  |  | 105.348 |  |  | 247.0111 |  |  | 1026.6862 |  |  | 1043.6941 |  |  | 467.9492 |  |  | 328.7444 |  |  | 406.014
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.7784 |  |  | 21.2939 |  |  | 54.848 |  |  | 130.4242 |  |  | #NUM! |  |  | #NUM! |  |  | 1043.6941 |  |  | 467.9492 |  |  | 328.7444 |  |  | 406.014
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9516 | 526.4893 |  | 9.6939 | 3997.6083 |  | 31.848 | 9788.6742 |  | 91.0242 | 19065.8388 |  | 18000 | 31986.5466 |  | 18000 | 46685.2359 |  | 18000 | 61684.7805 |  | 18000 | 76019.8263 |  | 18000 | 88256.6584 |  | 18000 | 103487.8729
[13 empty] | Next iteration flow rate |  |  | 537.0191 | Abs Value of | Flow this | 4037.5843 | Abs Value of | Flow this | 9886.5609 | Abs Value of | Flow this | 19256.4972 | Abs Value of | Flow this | 32306.412 | Abs Value of | Flow this | 47152.0883 | Abs Value of | Flow this | 62301.6283 | Abs Value of | Flow this | 76780.0246 | Abs Value of | Flow this | 89139.2249 | Abs Value of | Flow this | 104522.7516 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2211 |  |  | 89.7154 |  |  | 87.1439 |  |  | 78.5219 |  |  | 57.2756 |  |  | 20.0297 |  |  | -32.3265 |  |  | -95.9077 |  |  | -160.6555 |  |  | -254.7228
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4352 |  |  | 0.43276 |  |  | 0.42036 |  |  | 0.37877 |  |  | 0.27628 |  |  | 0.096618 |  |  | -0.15594 |  |  | -0.46263 |  |  | -0.77496 |  |  | -1.2287
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2211 |  |  | 29.7154 |  |  | 27.1439 |  |  | 18.5219 |  |  | -2.7244 |  |  | -39.9703 |  |  | -92.3265 |  |  | -155.9077 |  |  | -220.6555 |  |  | -314.7228
[13 empty] | Press drop ratio this iteration |  |  | 0.33497 |  |  | 0.33122 |  |  | 0.31148 |  |  | 0.23588 |  |  | -0.047566 |  |  | -1.9956 |  |  | 2.8561 |  |  | 1.6256 |  |  | 1.3735 |  |  | 1.2356
[13 empty] | Expansion factor | 12 |  | 0.82555 |  |  | 0.82754 |  |  | 0.83627 |  |  | 0.87426 |  |  | 1.0261 |  |  | 2.1625 |  |  | -0.79007 |  |  | -0.13918 |  |  | 0.22474 |  |  | -0.09334
[13 empty] | C Non choked w/ reducers | 5 |  | 2.834 |  |  | 21.5107 |  |  | 55.4611 |  |  | 132.5597 |  |  | #NUM! |  |  | #NUM! |  |  | -355.3347 |  |  | -1178.3797 |  |  | 626.2785 |  |  | -1574.8456
[13 empty] | C Choked w/ reducers | 5 |  | 2.5376 |  |  | 19.1966 |  |  | 48.7342 |  |  | 106.7141 |  |  | 252.3095 |  |  | 1108.5638 |  |  | 975.3854 |  |  | 454.5547 |  |  | 321.815 |  |  | 399.1319
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.834 |  |  | 21.5107 |  |  | 55.4611 |  |  | 132.5597 |  |  | #NUM! |  |  | #NUM! |  |  | 975.3854 |  |  | 454.5547 |  |  | 321.815 |  |  | 399.1319
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.896 | 537.0191 |  | 9.9107 | 4037.5843 |  | 32.4611 | 9886.5609 |  | 93.1597 | 19256.4972 |  | 18000 | 32306.412 |  | 18000 | 47152.0883 |  | 18000 | 62301.6283 |  | 18000 | 76780.0246 |  | 18000 | 89139.2249 |  | 18000 | 104522.7516
[13 empty] | Next iteration flow rate |  |  | 547.7594 | Abs Value of | Flow this | 4077.9602 | Abs Value of | Flow this | 9985.4265 | Abs Value of | Flow this | 19449.0622 | Abs Value of | Flow this | 32629.4762 | Abs Value of | Flow this | 47623.6092 | Abs Value of | Flow this | 62924.6446 | Abs Value of | Flow this | 77547.8248 | Abs Value of | Flow this | 90030.6172 | Abs Value of | Flow this | 105567.9791 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2207 |  |  | 89.7051 |  |  | 87.0819 |  |  | 78.2866 |  |  | 56.6132 |  |  | 18.6187 |  |  | -34.7899 |  |  | -99.6491 |  |  | -165.6983 |  |  | -261.6563
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4352 |  |  | 0.43271 |  |  | 0.42006 |  |  | 0.37763 |  |  | 0.27309 |  |  | 0.089812 |  |  | -0.16782 |  |  | -0.48068 |  |  | -0.79929 |  |  | -1.2622
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2207 |  |  | 29.7051 |  |  | 27.0819 |  |  | 18.2866 |  |  | -3.3868 |  |  | -41.3813 |  |  | -94.7899 |  |  | -159.6491 |  |  | -225.6983 |  |  | -321.6563
[13 empty] | Press drop ratio this iteration |  |  | 0.33496 |  |  | 0.33114 |  |  | 0.31099 |  |  | 0.23359 |  |  | -0.059823 |  |  | -2.2226 |  |  | 2.7246 |  |  | 1.6021 |  |  | 1.3621 |  |  | 1.2293
[13 empty] | Expansion factor | 12 |  | 0.82555 |  |  | 0.82758 |  |  | 0.83653 |  |  | 0.87549 |  |  | 1.0329 |  |  | 2.2948 |  |  | -0.7077 |  |  | -0.12272 |  |  | 0.23116 |  |  | -0.087816
[13 empty] | C Non choked w/ reducers | 5 |  | 2.8907 |  |  | 21.7298 |  |  | 56.0825 |  |  | 134.7577 |  |  | #NUM! |  |  | #NUM! |  |  | -381.1631 |  |  | -1308.6096 |  |  | 598.7518 |  |  | -1650.0105
[13 empty] | C Choked w/ reducers | 5 |  | 2.5883 |  |  | 19.3908 |  |  | 49.2567 |  |  | 108.1053 |  |  | 257.8142 |  |  | 1204.5029 |  |  | 915.3839 |  |  | 441.8631 |  |  | 315.1412 |  |  | 392.441
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.8907 |  |  | 21.7298 |  |  | 56.0825 |  |  | 134.7577 |  |  | #NUM! |  |  | #NUM! |  |  | 915.3839 |  |  | 441.8631 |  |  | 315.1412 |  |  | 392.441
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.8393 | 547.7594 |  | 10.1298 | 4077.9602 |  | 33.0825 | 9985.4265 |  | 95.3577 | 19449.0622 |  | 18000 | 32629.4762 |  | 18000 | 47623.6092 |  | 18000 | 62924.6446 |  | 18000 | 77547.8248 |  | 18000 | 90030.6172 |  | 18000 | 105567.9791
[13 empty] | Next iteration flow rate |  |  | 558.7146 | Abs Value of | Flow this | 4118.7398 | Abs Value of | Flow this | 10085.2808 | Abs Value of | Flow this | 19643.5528 | Abs Value of | Flow this | 32955.7709 | Abs Value of | Flow this | 48099.8452 | Abs Value of | Flow this | 63553.891 | Abs Value of | Flow this | 78323.3031 | Abs Value of | Flow this | 90930.9234 | Abs Value of | Flow this | 106623.6589 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2203 |  |  | 89.6945 |  |  | 87.0186 |  |  | 78.0465 |  |  | 55.9375 |  |  | 17.1793 |  |  | -37.3028 |  |  | -103.4656 |  |  | -170.8425 |  |  | -268.7293
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4352 |  |  | 0.43266 |  |  | 0.41976 |  |  | 0.37648 |  |  | 0.26983 |  |  | 0.082869 |  |  | -0.17994 |  |  | -0.49909 |  |  | -0.8241 |  |  | -1.2963
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2203 |  |  | 29.6945 |  |  | 27.0186 |  |  | 18.0465 |  |  | -4.0625 |  |  | -42.8207 |  |  | -97.3028 |  |  | -163.4656 |  |  | -230.8425 |  |  | -328.7293
[13 empty] | Press drop ratio this iteration |  |  | 0.33496 |  |  | 0.33106 |  |  | 0.31049 |  |  | 0.23123 |  |  | -0.072625 |  |  | -2.4926 |  |  | 2.6085 |  |  | 1.5799 |  |  | 1.3512 |  |  | 1.2233
[13 empty] | Expansion factor | 12 |  | 0.82555 |  |  | 0.82762 |  |  | 0.83679 |  |  | 0.87674 |  |  | 1.0399 |  |  | 2.4521 |  |  | -0.63489 |  |  | -0.10715 |  |  | 0.23731 |  |  | -0.082476
[13 empty] | C Non choked w/ reducers | 5 |  | 2.9485 |  |  | 21.9512 |  |  | 56.7124 |  |  | 137.0214 |  |  | #NUM! |  |  | #NUM! |  |  | -409.0365 |  |  | -1468.0528 |  |  | 573.6198 |  |  | -1731.9796
[13 empty] | C Choked w/ reducers | 5 |  | 2.6401 |  |  | 19.587 |  |  | 49.7854 |  |  | 109.5222 |  |  | 263.5378 |  |  | 1318.4782 |  |  | 862.2563 |  |  | 429.8196 |  |  | 308.7087 |  |  | 385.9331
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2.9485 |  |  | 21.9512 |  |  | 56.7124 |  |  | 137.0214 |  |  | #NUM! |  |  | #NUM! |  |  | 862.2563 |  |  | 429.8196 |  |  | 308.7087 |  |  | 385.9331
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7815 | 558.7146 |  | 10.3512 | 4118.7398 |  | 33.7124 | 10085.2808 |  | 97.6214 | 19643.5528 |  | 18000 | 32955.7709 |  | 18000 | 48099.8452 |  | 18000 | 63553.891 |  | 18000 | 78323.3031 |  | 18000 | 90930.9234 |  | 18000 | 106623.6589
[13 empty] | Next iteration flow rate |  |  | 569.8889 | Abs Value of | Flow this | 4159.9272 | Abs Value of | Flow this | 10186.1336 | Abs Value of | Flow this | 19839.9883 | Abs Value of | Flow this | 33285.3286 | Abs Value of | Flow this | 48580.8437 | Abs Value of | Flow this | 64189.4299 | Abs Value of | Flow this | 79106.5361 | Abs Value of | Flow this | 91840.2326 | Abs Value of | Flow this | 107689.8955 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2199 |  |  | 89.6838 |  |  | 86.9541 |  |  | 77.8016 |  |  | 55.2482 |  |  | 15.711 |  |  | -39.8662 |  |  | -107.3589 |  |  | -176.0901 |  |  | -275.9444
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4352 |  |  | 0.43261 |  |  | 0.41944 |  |  | 0.3753 |  |  | 0.2665 |  |  | 0.075786 |  |  | -0.1923 |  |  | -0.51787 |  |  | -0.84941 |  |  | -1.3311
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2199 |  |  | 29.6838 |  |  | 26.9541 |  |  | 17.8016 |  |  | -4.7518 |  |  | -44.289 |  |  | -99.8662 |  |  | -167.3589 |  |  | -236.0901 |  |  | -335.9444
[13 empty] | Press drop ratio this iteration |  |  | 0.33496 |  |  | 0.33098 |  |  | 0.30998 |  |  | 0.22881 |  |  | -0.086008 |  |  | -2.819 |  |  | 2.505 |  |  | 1.5589 |  |  | 1.3407 |  |  | 1.2174
[13 empty] | Expansion factor | 12 |  | 0.82555 |  |  | 0.82766 |  |  | 0.83706 |  |  | 0.87803 |  |  | 1.0473 |  |  | 2.6423 |  |  | -0.57006 |  |  | -0.092416 |  |  | 0.24322 |  |  | -0.07731
[13 empty] | C Non choked w/ reducers | 5 |  | 3.0075 |  |  | 22.1749 |  |  | 57.3509 |  |  | 139.3544 |  |  | #NUM! |  |  | #NUM! |  |  | -439.3166 |  |  | -1667.9692 |  |  | 550.5747 |  |  | -1821.7477
[13 empty] | C Choked w/ reducers | 5 |  | 2.6929 |  |  | 19.7852 |  |  | 50.3206 |  |  | 110.9656 |  |  | 269.494 |  |  | 1456.1182 |  |  | 814.881 |  |  | 418.3748 |  |  | 302.5041 |  |  | 379.6006
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.0075 |  |  | 22.1749 |  |  | 57.3509 |  |  | 139.3544 |  |  | #NUM! |  |  | #NUM! |  |  | 814.881 |  |  | 418.3748 |  |  | 302.5041 |  |  | 379.6006
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7225 | 569.8889 |  | 10.5749 | 4159.9272 |  | 34.3509 | 10186.1336 |  | 99.9544 | 19839.9883 |  | 18000 | 33285.3286 |  | 18000 | 48580.8437 |  | 18000 | 64189.4299 |  | 18000 | 79106.5361 |  | 18000 | 91840.2326 |  | 18000 | 107689.8955
[13 empty] | Next iteration flow rate |  |  | 581.2867 | Abs Value of | Flow this | 4201.5265 | Abs Value of | Flow this | 10287.995 | Abs Value of | Flow this | 20038.3882 | Abs Value of | Flow this | 33618.1819 | Abs Value of | Flow this | 49066.6521 | Abs Value of | Flow this | 64831.3242 | Abs Value of | Flow this | 79897.6015 | Abs Value of | Flow this | 92758.6349 | Abs Value of | Flow this | 108766.7944 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2195 |  |  | 89.6728 |  |  | 86.8882 |  |  | 77.5518 |  |  | 54.5451 |  |  | 14.2131 |  |  | -42.4812 |  |  | -111.3305 |  |  | -181.4431 |  |  | -283.3045
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4352 |  |  | 0.43256 |  |  | 0.41913 |  |  | 0.37409 |  |  | 0.26311 |  |  | 0.068561 |  |  | -0.20492 |  |  | -0.53703 |  |  | -0.87524 |  |  | -1.3666
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2195 |  |  | 29.6728 |  |  | 26.8882 |  |  | 17.5518 |  |  | -5.4549 |  |  | -45.7869 |  |  | -102.4812 |  |  | -171.3305 |  |  | -241.4431 |  |  | -343.3045
[13 empty] | Press drop ratio this iteration |  |  | 0.33496 |  |  | 0.3309 |  |  | 0.30946 |  |  | 0.22632 |  |  | -0.10001 |  |  | -3.2215 |  |  | 2.4124 |  |  | 1.5389 |  |  | 1.3307 |  |  | 1.2118
[13 empty] | Expansion factor | 12 |  | 0.82555 |  |  | 0.8277 |  |  | 0.83733 |  |  | 0.87936 |  |  | 1.055 |  |  | 2.8767 |  |  | -0.512 |  |  | -0.078445 |  |  | 0.24889 |  |  | -0.072311
[13 empty] | C Non choked w/ reducers | 5 |  | 3.0677 |  |  | 22.401 |  |  | 57.9982 |  |  | 141.7604 |  |  | #NUM! |  |  | #NUM! |  |  | -472.4385 |  |  | -1926.2457 |  |  | 529.3595 |  |  | -1920.5124
[13 empty] | C Choked w/ reducers | 5 |  | 2.7468 |  |  | 19.9855 |  |  | 50.8623 |  |  | 112.4362 |  |  | 275.6977 |  |  | 1625.6656 |  |  | 772.368 |  |  | 407.4845 |  |  | 296.5153 |  |  | 373.4361
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.0677 |  |  | 22.401 |  |  | 57.9982 |  |  | 141.7604 |  |  | #NUM! |  |  | #NUM! |  |  | 772.368 |  |  | 407.4845 |  |  | 296.5153 |  |  | 373.4361
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6623 | 581.2867 |  | 10.801 | 4201.5265 |  | 34.9982 | 10287.995 |  | 102.3604 | 20038.3882 |  | 18000 | 33618.1819 |  | 18000 | 49066.6521 |  | 18000 | 64831.3242 |  | 18000 | 79897.6015 |  | 18000 | 92758.6349 |  | 18000 | 108766.7944
[13 empty] | Next iteration flow rate |  |  | 592.9124 | Abs Value of | Flow this | 4243.5417 | Abs Value of | Flow this | 10390.8749 | Abs Value of | Flow this | 20238.7721 | Abs Value of | Flow this | 33954.3637 | Abs Value of | Flow this | 49557.3187 | Abs Value of | Flow this | 65479.6375 | Abs Value of | Flow this | 80696.5775 | Abs Value of | Flow this | 93686.2213 | Abs Value of | Flow this | 109854.4624 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2191 |  |  | 89.6616 |  |  | 86.8211 |  |  | 77.297 |  |  | 53.8278 |  |  | 12.6852 |  |  | -45.1487 |  |  | -115.3818 |  |  | -186.9037 |  |  | -290.8125
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43519 |  |  | 0.43251 |  |  | 0.4188 |  |  | 0.37286 |  |  | 0.25965 |  |  | 0.06119 |  |  | -0.21779 |  |  | -0.55657 |  |  | -0.90158 |  |  | -1.4028
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2191 |  |  | 29.6616 |  |  | 26.8211 |  |  | 17.297 |  |  | -6.1722 |  |  | -47.3148 |  |  | -105.1487 |  |  | -175.3818 |  |  | -246.9037 |  |  | -350.8125
[13 empty] | Press drop ratio this iteration |  |  | 0.33495 |  |  | 0.33082 |  |  | 0.30892 |  |  | 0.22377 |  |  | -0.11467 |  |  | -3.7299 |  |  | 2.3289 |  |  | 1.52 |  |  | 1.321 |  |  | 1.2063
[13 empty] | Expansion factor | 12 |  | 0.82555 |  |  | 0.82775 |  |  | 0.83762 |  |  | 0.88072 |  |  | 1.063 |  |  | 3.1729 |  |  | -0.4597 |  |  | -0.065184 |  |  | 0.25434 |  |  | -0.067472
[13 empty] | C Non choked w/ reducers | 5 |  | 3.1291 |  |  | 22.6295 |  |  | 58.6545 |  |  | 144.2434 |  |  | #NUM! |  |  | #NUM! |  |  | -508.9323 |  |  | -2273.1135 |  |  | 509.7579 |  |  | -2029.7293
[13 empty] | C Choked w/ reducers | 5 |  | 2.8017 |  |  | 20.1879 |  |  | 51.4107 |  |  | 113.935 |  |  | 282.1651 |  |  | 1839.6936 |  |  | 734.0019 |  |  | 397.1084 |  |  | 290.7307 |  |  | 367.4329
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.1291 |  |  | 22.6295 |  |  | 58.6545 |  |  | 144.2434 |  |  | #NUM! |  |  | #NUM! |  |  | 734.0019 |  |  | 397.1084 |  |  | 290.7307 |  |  | 367.4329
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6009 | 592.9124 |  | 11.0295 | 4243.5417 |  | 35.6545 | 10390.8749 |  | 104.8434 | 20238.7721 |  | 18000 | 33954.3637 |  | 18000 | 49557.3187 |  | 18000 | 65479.6375 |  | 18000 | 80696.5775 |  | 18000 | 93686.2213 |  | 18000 | 109854.4624
[13 empty] | Next iteration flow rate |  |  | 604.7707 | Abs Value of | Flow this | 4285.9771 | Abs Value of | Flow this | 10494.7837 | Abs Value of | Flow this | 20441.1598 | Abs Value of | Flow this | 34293.9074 | Abs Value of | Flow this | 50052.8918 | Abs Value of | Flow this | 66134.4339 | Abs Value of | Flow this | 81503.5433 | Abs Value of | Flow this | 94623.0835 | Abs Value of | Flow this | 110953.007 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2186 |  |  | 89.6502 |  |  | 86.7525 |  |  | 77.037 |  |  | 53.0961 |  |  | 11.1265 |  |  | -47.8698 |  |  | -119.5146 |  |  | -192.4741 |  |  | -298.4715
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43519 |  |  | 0.43245 |  |  | 0.41847 |  |  | 0.37161 |  |  | 0.25612 |  |  | 0.053672 |  |  | -0.23091 |  |  | -0.57651 |  |  | -0.92845 |  |  | -1.4398
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2186 |  |  | 29.6502 |  |  | 26.7525 |  |  | 17.037 |  |  | -6.9039 |  |  | -48.8735 |  |  | -107.8698 |  |  | -179.5146 |  |  | -252.4741 |  |  | -358.4715
[13 empty] | Press drop ratio this iteration |  |  | 0.33495 |  |  | 0.33073 |  |  | 0.30838 |  |  | 0.22115 |  |  | -0.13003 |  |  | -4.3925 |  |  | 2.2534 |  |  | 1.502 |  |  | 1.3117 |  |  | 1.201
[13 empty] | Expansion factor | 12 |  | 0.82556 |  |  | 0.82779 |  |  | 0.8379 |  |  | 0.88211 |  |  | 1.0715 |  |  | 3.5589 |  |  | -0.41235 |  |  | -0.052583 |  |  | 0.25959 |  |  | -0.062788
[13 empty] | C Non choked w/ reducers | 5 |  | 3.1917 |  |  | 22.8605 |  |  | 59.32 |  |  | 146.8078 |  |  | #NUM! |  |  | #NUM! |  |  | -549.4538 |  |  | -2764.0193 |  |  | 491.5868 |  |  | -2151.185
[13 empty] | C Choked w/ reducers | 5 |  | 2.8578 |  |  | 20.3924 |  |  | 51.9658 |  |  | 115.4627 |  |  | 288.914 |  |  | 2118.3805 |  |  | 699.201 |  |  | 387.2102 |  |  | 285.1399 |  |  | 361.5844
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.1917 |  |  | 22.8605 |  |  | 59.32 |  |  | 146.8078 |  |  | #NUM! |  |  | #NUM! |  |  | 699.201 |  |  | 387.2102 |  |  | 285.1399 |  |  | 361.5844
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5383 | 604.7707 |  | 11.2605 | 4285.9771 |  | 36.32 | 10494.7837 |  | 107.4078 | 20441.1598 |  | 18000 | 34293.9074 |  | 18000 | 50052.8918 |  | 18000 | 66134.4339 |  | 18000 | 81503.5433 |  | 18000 | 94623.0835 |  | 18000 | 110953.007
[13 empty] | Next iteration flow rate |  |  | 616.8661 | Abs Value of | Flow this | 4328.8369 | Abs Value of | Flow this | 10599.7315 | Abs Value of | Flow this | 20645.5714 | Abs Value of | Flow this | 34636.8464 | Abs Value of | Flow this | 50553.4208 | Abs Value of | Flow this | 66795.7782 | Abs Value of | Flow this | 82318.5787 | Abs Value of | Flow this | 95569.3143 | Abs Value of | Flow this | 112062.5371 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2182 |  |  | 89.6385 |  |  | 86.6826 |  |  | 76.7718 |  |  | 52.3497 |  |  | 9.5365 |  |  | -50.6456 |  |  | -123.7305 |  |  | -198.1565 |  |  | -306.2844
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43519 |  |  | 0.43239 |  |  | 0.41814 |  |  | 0.37033 |  |  | 0.25252 |  |  | 0.046002 |  |  | -0.2443 |  |  | -0.59684 |  |  | -0.95586 |  |  | -1.4774
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2182 |  |  | 29.6385 |  |  | 26.6826 |  |  | 16.7718 |  |  | -7.6503 |  |  | -50.4635 |  |  | -110.6456 |  |  | -183.7305 |  |  | -258.1565 |  |  | -366.2844
[13 empty] | Press drop ratio this iteration |  |  | 0.33495 |  |  | 0.33064 |  |  | 0.30782 |  |  | 0.21846 |  |  | -0.14614 |  |  | -5.2916 |  |  | 2.1847 |  |  | 1.4849 |  |  | 1.3028 |  |  | 1.1959
[13 empty] | Expansion factor | 12 |  | 0.82556 |  |  | 0.82784 |  |  | 0.8382 |  |  | 0.88355 |  |  | 1.0803 |  |  | 4.0827 |  |  | -0.36929 |  |  | -0.040595 |  |  | 0.26463 |  |  | -0.05825
[13 empty] | C Non choked w/ reducers | 5 |  | 3.2555 |  |  | 23.0939 |  |  | 59.9948 |  |  | 149.4584 |  |  | #NUM! |  |  | #NUM! |  |  | -594.8262 |  |  | -3512.8454 |  |  | 474.6899 |  |  | -2287.0967
[13 empty] | C Choked w/ reducers | 5 |  | 2.915 |  |  | 20.599 |  |  | 52.5278 |  |  | 117.0201 |  |  | 295.9637 |  |  | 2496.2841 |  |  | 667.4876 |  |  | 377.7569 |  |  | 279.7328 |  |  | 355.8845
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.2555 |  |  | 23.0939 |  |  | 59.9948 |  |  | 149.4584 |  |  | #NUM! |  |  | #NUM! |  |  | 667.4876 |  |  | 377.7569 |  |  | 279.7328 |  |  | 355.8845
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4745 | 616.8661 |  | 11.4939 | 4328.8369 |  | 36.9948 | 10599.7315 |  | 110.0584 | 20645.5714 |  | 18000 | 34636.8464 |  | 18000 | 50553.4208 |  | 18000 | 66795.7782 |  | 18000 | 82318.5787 |  | 18000 | 95569.3143 |  | 18000 | 112062.5371
[13 empty] | Next iteration flow rate |  |  | 629.2034 | Abs Value of | Flow this | 4372.1253 | Abs Value of | Flow this | 10705.7288 | Abs Value of | Flow this | 20852.0271 | Abs Value of | Flow this | 34983.2149 | Abs Value of | Flow this | 51058.955 | Abs Value of | Flow this | 67463.736 | Abs Value of | Flow this | 83141.7645 | Abs Value of | Flow this | 96525.0075 | Abs Value of | Flow this | 113183.1624 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2177 |  |  | 89.6266 |  |  | 86.6113 |  |  | 76.5013 |  |  | 51.5884 |  |  | 7.9146 |  |  | -53.4772 |  |  | -128.0311 |  |  | -203.9531 |  |  | -314.2543
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43519 |  |  | 0.43234 |  |  | 0.41779 |  |  | 0.36902 |  |  | 0.24885 |  |  | 0.038178 |  |  | -0.25796 |  |  | -0.61759 |  |  | -0.98382 |  |  | -1.5159
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2177 |  |  | 29.6266 |  |  | 26.6113 |  |  | 16.5013 |  |  | -8.4116 |  |  | -52.0854 |  |  | -113.4772 |  |  | -188.0311 |  |  | -263.9531 |  |  | -374.2543
[13 empty] | Press drop ratio this iteration |  |  | 0.33494 |  |  | 0.33056 |  |  | 0.30725 |  |  | 0.2157 |  |  | -0.16305 |  |  | -6.5809 |  |  | 2.122 |  |  | 1.4686 |  |  | 1.2942 |  |  | 1.1909
[13 empty] | Expansion factor | 12 |  | 0.82556 |  |  | 0.82788 |  |  | 0.83849 |  |  | 0.88502 |  |  | 1.0896 |  |  | 4.8338 |  |  | -0.32998 |  |  | -0.029181 |  |  | 0.26949 |  |  | -0.053854
[13 empty] | C Non choked w/ reducers | 5 |  | 3.3207 |  |  | 23.3297 |  |  | 60.6791 |  |  | 152.2003 |  |  | #NUM! |  |  | #NUM! |  |  | -646.0992 |  |  | -4796.433 |  |  | 458.9328 |  |  | -2440.2512
[13 empty] | C Choked w/ reducers | 5 |  | 2.9733 |  |  | 20.8077 |  |  | 53.0967 |  |  | 118.6082 |  |  | 303.3351 |  |  | 3037.9275 |  |  | 638.4658 |  |  | 368.7186 |  |  | 274.5003 |  |  | 350.3273
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.3207 |  |  | 23.3297 |  |  | 60.6791 |  |  | 152.2003 |  |  | #NUM! |  |  | #NUM! |  |  | 638.4658 |  |  | 368.7186 |  |  | 274.5003 |  |  | 350.3273
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4093 | 629.2034 |  | 11.7297 | 4372.1253 |  | 37.6791 | 10705.7288 |  | 112.8003 | 20852.0271 |  | 18000 | 34983.2149 |  | 18000 | 51058.955 |  | 18000 | 67463.736 |  | 18000 | 83141.7645 |  | 18000 | 96525.0075 |  | 18000 | 113183.1624
[13 empty] | Next iteration flow rate |  |  | 641.7875 | Abs Value of | Flow this | 4415.8465 | Abs Value of | Flow this | 10812.7861 | Abs Value of | Flow this | 21060.5474 | Abs Value of | Flow this | 35333.0471 | Abs Value of | Flow this | 51569.5445 | Abs Value of | Flow this | 68138.3733 | Abs Value of | Flow this | 83973.1821 | Abs Value of | Flow this | 97490.2575 | Abs Value of | Flow this | 114314.9941 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2172 |  |  | 89.6145 |  |  | 86.5386 |  |  | 76.2254 |  |  | 50.8117 |  |  | 6.2601 |  |  | -56.3657 |  |  | -132.4182 |  |  | -209.8661 |  |  | -322.3844
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43519 |  |  | 0.43228 |  |  | 0.41744 |  |  | 0.36769 |  |  | 0.2451 |  |  | 0.030197 |  |  | -0.27189 |  |  | -0.63875 |  |  | -1.0123 |  |  | -1.5551
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2172 |  |  | 29.6145 |  |  | 26.5386 |  |  | 16.2254 |  |  | -9.1883 |  |  | -53.7399 |  |  | -116.3657 |  |  | -192.4182 |  |  | -269.8661 |  |  | -382.3844
[13 empty] | Press drop ratio this iteration |  |  | 0.33494 |  |  | 0.33047 |  |  | 0.30667 |  |  | 0.21286 |  |  | -0.18083 |  |  | -8.5846 |  |  | 2.0645 |  |  | 1.4531 |  |  | 1.2859 |  |  | 1.1861
[13 empty] | Expansion factor | 12 |  | 0.82556 |  |  | 0.82793 |  |  | 0.8388 |  |  | 0.88653 |  |  | 1.0994 |  |  | 6.0011 |  |  | -0.29394 |  |  | -0.0183 |  |  | 0.27417 |  |  | -0.049593
[13 empty] | C Non choked w/ reducers | 5 |  | 3.3871 |  |  | 23.5681 |  |  | 61.3732 |  |  | 155.0392 |  |  | #NUM! |  |  | #NUM! |  |  | -704.6349 |  |  | -7508.4282 |  |  | 444.1999 |  |  | -2614.1992
[13 empty] | C Choked w/ reducers | 5 |  | 3.0328 |  |  | 21.0187 |  |  | 53.6728 |  |  | 120.228 |  |  | 311.0516 |  |  | 3879.266 |  |  | 611.8044 |  |  | 360.0679 |  |  | 269.4338 |  |  | 344.9074
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.3871 |  |  | 23.5681 |  |  | 61.3732 |  |  | 155.0392 |  |  | #NUM! |  |  | #NUM! |  |  | 611.8044 |  |  | 360.0679 |  |  | 269.4338 |  |  | 344.9074
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.3429 | 641.7875 |  | 11.9681 | 4415.8465 |  | 38.3732 | 10812.7861 |  | 115.6392 | 21060.5474 |  | 18000 | 35333.0471 |  | 18000 | 51569.5445 |  | 18000 | 68138.3733 |  | 18000 | 83973.1821 |  | 18000 | 97490.2575 |  | 18000 | 114314.9941
[13 empty] | Next iteration flow rate |  |  | 654.6232 | Abs Value of | Flow this | 4460.005 | Abs Value of | Flow this | 10920.914 | Abs Value of | Flow this | 21271.1529 | Abs Value of | Flow this | 35686.3775 | Abs Value of | Flow this | 52085.24 | Abs Value of | Flow this | 68819.7571 | Abs Value of | Flow this | 84812.9139 | Abs Value of | Flow this | 98465.1601 | Abs Value of | Flow this | 115458.144 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2166 |  |  | 89.6021 |  |  | 86.4644 |  |  | 75.9439 |  |  | 50.0193 |  |  | 4.5723 |  |  | -59.3123 |  |  | -136.8934 |  |  | -215.8981 |  |  | -330.678
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43518 |  |  | 0.43222 |  |  | 0.41708 |  |  | 0.36633 |  |  | 0.24128 |  |  | 0.022055 |  |  | -0.28611 |  |  | -0.66034 |  |  | -1.0414 |  |  | -1.5951
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2166 |  |  | 29.6021 |  |  | 26.4644 |  |  | 15.9439 |  |  | -9.9807 |  |  | -55.4277 |  |  | -119.3123 |  |  | -196.8934 |  |  | -275.8981 |  |  | -390.678
[13 empty] | Press drop ratio this iteration |  |  | 0.33493 |  |  | 0.33037 |  |  | 0.30607 |  |  | 0.20994 |  |  | -0.19954 |  |  | -12.1226 |  |  | 2.0116 |  |  | 1.4383 |  |  | 1.2779 |  |  | 1.1814
[13 empty] | Expansion factor | 12 |  | 0.82556 |  |  | 0.82798 |  |  | 0.83911 |  |  | 0.88809 |  |  | 1.1097 |  |  | 8.0623 |  |  | -0.26079 |  |  | -0.0079201 |  |  | 0.27868 |  |  | -0.045462
[13 empty] | C Non choked w/ reducers | 5 |  | 3.4549 |  |  | 23.809 |  |  | 62.0773 |  |  | 157.9812 |  |  | #NUM! |  |  | #NUM! |  |  | -772.2353 |  |  | -17037.0079 |  |  | 430.3906 |  |  | -2813.5376
[13 empty] | C Choked w/ reducers | 5 |  | 3.0934 |  |  | 21.2318 |  |  | 54.256 |  |  | 121.8804 |  |  | 319.1385 |  |  | 5364.3697 |  |  | 587.2246 |  |  | 351.7797 |  |  | 264.5252 |  |  | 339.6196
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.4549 |  |  | 23.809 |  |  | 62.0773 |  |  | 157.9812 |  |  | #NUM! |  |  | #NUM! |  |  | 587.2246 |  |  | 351.7797 |  |  | 264.5252 |  |  | 339.6196
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2751 | 654.6232 |  | 12.209 | 4460.005 |  | 39.0773 | 10920.914 |  | 118.5812 | 21271.1529 |  | 18000 | 35686.3775 |  | 18000 | 52085.24 |  | 18000 | 68819.7571 |  | 18000 | 84812.9139 |  | 18000 | 98465.1601 |  | 18000 | 115458.144
[13 empty] | Next iteration flow rate |  |  | 667.7157 | Abs Value of | Flow this | 4504.605 | Abs Value of | Flow this | 11030.1231 | Abs Value of | Flow this | 21483.8644 | Abs Value of | Flow this | 36043.2413 | Abs Value of | Flow this | 52606.0924 | Abs Value of | Flow this | 69507.9546 | Abs Value of | Flow this | 85661.0431 | Abs Value of | Flow this | 99449.8117 | Abs Value of | Flow this | 116612.7255 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2161 |  |  | 89.5895 |  |  | 86.3887 |  |  | 75.6567 |  |  | 49.2111 |  |  | 2.8505 |  |  | -62.3181 |  |  | -141.4586 |  |  | -222.0512 |  |  | -339.1383
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43518 |  |  | 0.43216 |  |  | 0.41672 |  |  | 0.36495 |  |  | 0.23738 |  |  | 0.01375 |  |  | -0.30061 |  |  | -0.68236 |  |  | -1.0711 |  |  | -1.6359
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2161 |  |  | 29.5895 |  |  | 26.3887 |  |  | 15.6567 |  |  | -10.7889 |  |  | -57.1495 |  |  | -122.3181 |  |  | -201.4586 |  |  | -282.0512 |  |  | -399.1383
[13 empty] | Press drop ratio this iteration |  |  | 0.33493 |  |  | 0.33028 |  |  | 0.30546 |  |  | 0.20694 |  |  | -0.21924 |  |  | -20.0487 |  |  | 1.9628 |  |  | 1.4242 |  |  | 1.2702 |  |  | 1.1769
[13 empty] | Expansion factor | 12 |  | 0.82557 |  |  | 0.82803 |  |  | 0.83943 |  |  | 0.88969 |  |  | 1.1205 |  |  | 12.6798 |  |  | -0.23021 |  |  | 0.0019922 |  |  | 0.28303 |  |  | -0.041457
[13 empty] | C Non choked w/ reducers | 5 |  | 3.524 |  |  | 24.0525 |  |  | 62.7915 |  |  | 161.0331 |  |  | #NUM! |  |  | #NUM! |  |  | -851.3378 |  |  | 66527.7453 |  |  | 417.4173 |  |  | -3044.3243
[13 empty] | C Choked w/ reducers | 5 |  | 3.1553 |  |  | 21.4471 |  |  | 54.8466 |  |  | 123.5664 |  |  | 327.6238 |  |  | 8690.5048 |  |  | 564.4899 |  |  | 343.8313 |  |  | 259.767 |  |  | 334.4588
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.524 |  |  | 24.0525 |  |  | 62.7915 |  |  | 161.0331 |  |  | #NUM! |  |  | #NUM! |  |  | 564.4899 |  |  | 343.8313 |  |  | 259.767 |  |  | 334.4588
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.206 | 667.7157 |  | 12.4525 | 4504.605 |  | 39.7915 | 11030.1231 |  | 121.6331 | 21483.8644 |  | 18000 | 36043.2413 |  | 18000 | 52606.0924 |  | 18000 | 69507.9546 |  | 18000 | 85661.0431 |  | 18000 | 99449.8117 |  | 18000 | 116612.7255
[13 empty] | Next iteration flow rate |  |  | 681.07 | Abs Value of | Flow this | 4549.6511 | Abs Value of | Flow this | 11140.4243 | Abs Value of | Flow this | 21698.703 | Abs Value of | Flow this | 36403.6737 | Abs Value of | Flow this | 53132.1533 | Abs Value of | Flow this | 70203.0342 | Abs Value of | Flow this | 86517.6535 | Abs Value of | Flow this | 100444.3098 | Abs Value of | Flow this | 117778.8527 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2155 |  |  | 89.5766 |  |  | 86.3115 |  |  | 75.3638 |  |  | 48.3866 |  |  | 1.0942 |  |  | -65.3843 |  |  | -146.1155 |  |  | -228.3281 |  |  | -347.7686
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43518 |  |  | 0.4321 |  |  | 0.41635 |  |  | 0.36354 |  |  | 0.2334 |  |  | 0.0052781 |  |  | -0.3154 |  |  | -0.70482 |  |  | -1.1014 |  |  | -1.6775
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2155 |  |  | 29.5766 |  |  | 26.3115 |  |  | 15.3638 |  |  | -11.6134 |  |  | -58.9058 |  |  | -125.3843 |  |  | -206.1155 |  |  | -288.3281 |  |  | -407.7686
[13 empty] | Press drop ratio this iteration |  |  | 0.33493 |  |  | 0.33018 |  |  | 0.30484 |  |  | 0.20386 |  |  | -0.24001 |  |  | -53.8348 |  |  | 1.9177 |  |  | 1.4106 |  |  | 1.2628 |  |  | 1.1725
[13 empty] | Expansion factor | 12 |  | 0.82557 |  |  | 0.82808 |  |  | 0.83976 |  |  | 0.89133 |  |  | 1.1319 |  |  | 32.3624 |  |  | -0.20191 |  |  | 0.011466 |  |  | 0.28722 |  |  | -0.037572
[13 empty] | C Non choked w/ reducers | 5 |  | 3.5945 |  |  | 24.2986 |  |  | 63.5161 |  |  | 164.2021 |  |  | #NUM! |  |  | #NUM! |  |  | -945.3242 |  |  | 11357.2274 |  |  | 405.203 |  |  | -3314.7097
[13 empty] | C Choked w/ reducers | 5 |  | 3.2184 |  |  | 21.6647 |  |  | 55.4446 |  |  | 125.2871 |  |  | 336.5384 |  |  | 22866.3248 |  |  | 543.3981 |  |  | 336.2015 |  |  | 255.1521 |  |  | 329.4203
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.5945 |  |  | 24.2986 |  |  | 63.5161 |  |  | 164.2021 |  |  | #NUM! |  |  | #NUM! |  |  | 543.3981 |  |  | 336.2015 |  |  | 255.1521 |  |  | 329.4203
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1355 | 681.07 |  | 12.6986 | 4549.6511 |  | 40.5161 | 11140.4243 |  | 124.8021 | 21698.703 |  | 18000 | 36403.6737 |  | 18000 | 53132.1533 |  | 18000 | 70203.0342 |  | 18000 | 86517.6535 |  | 18000 | 100444.3098 |  | 18000 | 117778.8527
[13 empty] | Next iteration flow rate |  |  | 694.6914 | Abs Value of | Flow this | 4595.1476 | Abs Value of | Flow this | 11251.8286 | Abs Value of | Flow this | 21915.6901 | Abs Value of | Flow this | 36767.7105 | Abs Value of | Flow this | 53663.4748 | Abs Value of | Flow this | 70905.0645 | Abs Value of | Flow this | 87382.8301 | Abs Value of | Flow this | 101448.7529 | Abs Value of | Flow this | 118956.6412 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2149 |  |  | 89.5635 |  |  | 86.2327 |  |  | 75.065 |  |  | 47.5456 |  |  | -0.69744 |  |  | -68.5121 |  |  | -150.8661 |  |  | -234.7311 |  |  | -356.5723
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43517 |  |  | 0.43203 |  |  | 0.41597 |  |  | 0.36209 |  |  | 0.22935 |  |  | -0.0033643 |  |  | -0.33049 |  |  | -0.72774 |  |  | -1.1323 |  |  | -1.72
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2149 |  |  | 29.5635 |  |  | 26.2327 |  |  | 15.065 |  |  | -12.4544 |  |  | -60.6974 |  |  | -128.5121 |  |  | -210.8661 |  |  | -294.7311 |  |  | -416.5723
[13 empty] | Press drop ratio this iteration |  |  | 0.33492 |  |  | 0.33008 |  |  | 0.30421 |  |  | 0.20069 |  |  | -0.26195 |  |  | 87.0293 |  |  | 1.8758 |  |  | 1.3977 |  |  | 1.2556 |  |  | 1.1683
[13 empty] | Expansion factor | 12 |  | 0.82557 |  |  | 0.82813 |  |  | 0.84009 |  |  | 0.89302 |  |  | 1.144 |  |  | -49.7005 |  |  | -0.17566 |  |  | 0.020527 |  |  | 0.29127 |  |  | -0.033802
[13 empty] | C Non choked w/ reducers | 5 |  | 3.6665 |  |  | 24.5473 |  |  | 64.2513 |  |  | 167.4963 |  |  | #NUM! |  |  | -39.4282 |  |  | -1059.0289 |  |  | 6234.1046 |  |  | 393.6802 |  |  | -3635.9253
[13 empty] | C Choked w/ reducers | 5 |  | 3.2828 |  |  | 21.8846 |  |  | 56.0502 |  |  | 127.0437 |  |  | 345.9165 |  |  | 36233.3017 |  |  | 523.7757 |  |  | 328.8712 |  |  | 250.674 |  |  | 324.4998
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.6665 |  |  | 24.5473 |  |  | 64.2513 |  |  | 167.4963 |  |  | #NUM! |  |  | 36233.3017 |  |  | 523.7757 |  |  | 328.8712 |  |  | 250.674 |  |  | 324.4998
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0635 | 694.6914 |  | 12.9473 | 4595.1476 |  | 41.2513 | 11251.8286 |  | 128.0963 | 21915.6901 |  | 18000 | 36767.7105 |  | 18000 | 53663.4748 |  | 18000 | 70905.0645 |  | 18000 | 87382.8301 |  | 18000 | 101448.7529 |  | 18000 | 118956.6412
[13 empty] | Next iteration flow rate |  |  | 708.5852 | Abs Value of | Flow this | 4641.0991 | Abs Value of | Flow this | 11364.3469 | Abs Value of | Flow this | 22134.847 | Abs Value of | Flow this | 37135.3876 | Abs Value of | Flow this | 54200.1096 | Abs Value of | Flow this | 71614.1152 | Abs Value of | Flow this | 88256.6584 | Abs Value of | Flow this | 102463.2405 | Abs Value of | Flow this | 120146.2076 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2143 |  |  | 89.5501 |  |  | 86.1524 |  |  | 74.7601 |  |  | 46.6876 |  |  | -2.5251 |  |  | -71.7029 |  |  | -155.7121 |  |  | -241.2628 |  |  | -365.5531
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43517 |  |  | 0.43197 |  |  | 0.41558 |  |  | 0.36062 |  |  | 0.22521 |  |  | -0.01218 |  |  | -0.34588 |  |  | -0.75112 |  |  | -1.1638 |  |  | -1.7633
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2143 |  |  | 29.5501 |  |  | 26.1524 |  |  | 14.7601 |  |  | -13.3124 |  |  | -62.5251 |  |  | -131.7029 |  |  | -215.7121 |  |  | -301.2628 |  |  | -425.5531
[13 empty] | Press drop ratio this iteration |  |  | 0.33492 |  |  | 0.32998 |  |  | 0.30356 |  |  | 0.19743 |  |  | -0.28514 |  |  | 24.7616 |  |  | 1.8368 |  |  | 1.3853 |  |  | 1.2487 |  |  | 1.1641
[13 empty] | Expansion factor | 12 |  | 0.82557 |  |  | 0.82818 |  |  | 0.84043 |  |  | 0.89476 |  |  | 1.1567 |  |  | -13.4253 |  |  | -0.15123 |  |  | 0.0292 |  |  | 0.29517 |  |  | -0.030144
[13 empty] | C Non choked w/ reducers | 5 |  | 3.7398 |  |  | 24.7987 |  |  | 64.9973 |  |  | 170.9248 |  |  | #NUM! |  |  | -76.3373 |  |  | -1199.6159 |  |  | 4307.5257 |  |  | 382.7893 |  |  | -4023.8918
[13 empty] | C Choked w/ reducers | 5 |  | 3.3485 |  |  | 22.1067 |  |  | 56.6635 |  |  | 128.8374 |  |  | 355.796 |  |  | 10107.8503 |  |  | 505.4728 |  |  | 321.8225 |  |  | 246.3263 |  |  | 319.6929
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.7398 |  |  | 24.7987 |  |  | 64.9973 |  |  | 170.9248 |  |  | #NUM! |  |  | 10107.8503 |  |  | 505.4728 |  |  | 321.8225 |  |  | 246.3263 |  |  | 319.6929
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.99015 | 708.5852 |  | 13.1987 | 4641.0991 |  | 41.9973 | 11364.3469 |  | 131.5248 | 22134.847 |  | 18000 | 37135.3876 |  | 18000 | 54200.1096 |  | 18000 | 71614.1152 |  | 18000 | 88256.6584 |  | 18000 | 102463.2405 |  | 18000 | 120146.2076
[13 empty] | Next iteration flow rate |  |  | 722.757 | Abs Value of | Flow this | 4687.5101 | Abs Value of | Flow this | 11477.9903 | Abs Value of | Flow this | 22356.1955 | Abs Value of | Flow this | 37506.7414 | Abs Value of | Flow this | 54742.1107 | Abs Value of | Flow this | 72330.2563 | Abs Value of | Flow this | 89139.2249 | Abs Value of | Flow this | 103487.8729 | Abs Value of | Flow this | 121347.6697 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2137 |  |  | 89.5364 |  |  | 86.0704 |  |  | 74.4492 |  |  | 45.8124 |  |  | -4.3895 |  |  | -74.9577 |  |  | -160.6555 |  |  | -247.9259 |  |  | -374.7143
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43517 |  |  | 0.4319 |  |  | 0.41518 |  |  | 0.35912 |  |  | 0.22099 |  |  | -0.021174 |  |  | -0.36158 |  |  | -0.77496 |  |  | -1.1959 |  |  | -1.8075
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2137 |  |  | 29.5364 |  |  | 26.0704 |  |  | 14.4492 |  |  | -14.1876 |  |  | -64.3895 |  |  | -134.9577 |  |  | -220.6555 |  |  | -307.9259 |  |  | -434.7143
[13 empty] | Press drop ratio this iteration |  |  | 0.33491 |  |  | 0.32988 |  |  | 0.3029 |  |  | 0.19408 |  |  | -0.30969 |  |  | 14.6691 |  |  | 1.8005 |  |  | 1.3735 |  |  | 1.242 |  |  | 1.1601
[13 empty] | Expansion factor | 12 |  | 0.82557 |  |  | 0.82823 |  |  | 0.84078 |  |  | 0.89654 |  |  | 1.1702 |  |  | -7.5457 |  |  | -0.12846 |  |  | 0.037509 |  |  | 0.29894 |  |  | -0.026593
[13 empty] | C Non choked w/ reducers | 5 |  | 3.8147 |  |  | 25.0528 |  |  | 65.7545 |  |  | 174.4972 |  |  | #NUM! |  |  | -102.5256 |  |  | -1378.1759 |  |  | 3296.8038 |  |  | 372.4771 |  |  | -4501.9511
[13 empty] | C Choked w/ reducers | 5 |  | 3.4155 |  |  | 22.3312 |  |  | 57.2846 |  |  | 130.6692 |  |  | 366.2191 |  |  | 5872.7877 |  |  | 488.3591 |  |  | 315.0391 |  |  | 242.1034 |  |  | 314.9957
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.8147 |  |  | 25.0528 |  |  | 65.7545 |  |  | 174.4972 |  |  | #NUM! |  |  | 5872.7877 |  |  | 488.3591 |  |  | 315.0391 |  |  | 242.1034 |  |  | 314.9957
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.91532 | 722.757 |  | 13.4528 | 4687.5101 |  | 42.7545 | 11477.9903 |  | 135.0972 | 22356.1955 |  | 18000 | 37506.7414 |  | 18000 | 54742.1107 |  | 18000 | 72330.2563 |  | 18000 | 89139.2249 |  | 18000 | 103487.8729 |  | 18000 | 121347.6697
[13 empty] | Next iteration flow rate |  |  | 737.2121 | Abs Value of | Flow this | 4734.3852 | Abs Value of | Flow this | 11592.7702 | Abs Value of | Flow this | 22579.7574 | Abs Value of | Flow this | 37881.8088 | Abs Value of | Flow this | 55289.5318 | Abs Value of | Flow this | 73053.5589 | Abs Value of | Flow this | 90030.6172 | Abs Value of | Flow this | 104522.7516 | Abs Value of | Flow this | 122561.1464 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.213 |  |  | 89.5225 |  |  | 85.9868 |  |  | 74.132 |  |  | 44.9196 |  |  | -6.2913 |  |  | -78.278 |  |  | -165.6983 |  |  | -254.7228 |  |  | -384.0597
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43517 |  |  | 0.43183 |  |  | 0.41478 |  |  | 0.35759 |  |  | 0.21668 |  |  | -0.030348 |  |  | -0.37759 |  |  | -0.79929 |  |  | -1.2287 |  |  | -1.8526
[13 empty] | Delta P at this iteration flow rate |  |  | 30.213 |  |  | 29.5225 |  |  | 25.9868 |  |  | 14.132 |  |  | -15.0804 |  |  | -66.2913 |  |  | -138.278 |  |  | -225.6983 |  |  | -314.7228 |  |  | -444.0597
[13 empty] | Press drop ratio this iteration |  |  | 0.33491 |  |  | 0.32978 |  |  | 0.30222 |  |  | 0.19063 |  |  | -0.33572 |  |  | 10.537 |  |  | 1.7665 |  |  | 1.3621 |  |  | 1.2356 |  |  | 1.1562
[13 empty] | Expansion factor | 12 |  | 0.82558 |  |  | 0.82829 |  |  | 0.84114 |  |  | 0.89838 |  |  | 1.1845 |  |  | -5.1385 |  |  | -0.10718 |  |  | 0.045474 |  |  | 0.30259 |  |  | -0.023145
[13 empty] | C Non choked w/ reducers | 5 |  | 3.891 |  |  | 25.3096 |  |  | 66.5229 |  |  | 178.2245 |  |  | #NUM! |  |  | -125.1798 |  |  | -1612.8471 |  |  | 2674.0474 |  |  | 362.6967 |  |  | -5105.7617
[13 empty] | C Choked w/ reducers | 5 |  | 3.4838 |  |  | 22.558 |  |  | 57.9138 |  |  | 132.5406 |  |  | 377.2328 |  |  | 4138.4284 |  |  | 472.3211 |  |  | 308.5058 |  |  | 237.9996 |  |  | 310.4041
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.891 |  |  | 25.3096 |  |  | 66.5229 |  |  | 178.2245 |  |  | #NUM! |  |  | 4138.4284 |  |  | 472.3211 |  |  | 308.5058 |  |  | 237.9996 |  |  | 310.4041
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.83898 | 737.2121 |  | 13.7096 | 4734.3852 |  | 43.5229 | 11592.7702 |  | 138.8245 | 22579.7574 |  | 18000 | 37881.8088 |  | 18000 | 55289.5318 |  | 18000 | 73053.5589 |  | 18000 | 90030.6172 |  | 18000 | 104522.7516 |  | 18000 | 122561.1464
[13 empty] | Next iteration flow rate |  |  | 751.9563 | Abs Value of | Flow this | 4781.729 | Abs Value of | Flow this | 11708.6979 | Abs Value of | Flow this | 22805.555 | Abs Value of | Flow this | 38260.6269 | Abs Value of | Flow this | 55842.4271 | Abs Value of | Flow this | 73784.0945 | Abs Value of | Flow this | 90930.9234 | Abs Value of | Flow this | 105567.9791 | Abs Value of | Flow this | 123786.7579 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2123 |  |  | 89.5082 |  |  | 85.9015 |  |  | 73.8084 |  |  | 44.0089 |  |  | -8.2314 |  |  | -81.665 |  |  | -170.8425 |  |  | -261.6563 |  |  | -393.5929
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43516 |  |  | 0.43177 |  |  | 0.41437 |  |  | 0.35603 |  |  | 0.21229 |  |  | -0.039706 |  |  | -0.39393 |  |  | -0.8241 |  |  | -1.2622 |  |  | -1.8986
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2123 |  |  | 29.5082 |  |  | 25.9015 |  |  | 13.8084 |  |  | -15.9911 |  |  | -68.2314 |  |  | -141.665 |  |  | -230.8425 |  |  | -321.6563 |  |  | -453.5929
[13 empty] | Press drop ratio this iteration |  |  | 0.3349 |  |  | 0.32967 |  |  | 0.30153 |  |  | 0.18708 |  |  | -0.36336 |  |  | 8.2892 |  |  | 1.7347 |  |  | 1.3512 |  |  | 1.2293 |  |  | 1.1524
[13 empty] | Expansion factor | 12 |  | 0.82558 |  |  | 0.82834 |  |  | 0.8415 |  |  | 0.90027 |  |  | 1.1997 |  |  | -3.829 |  |  | -0.087252 |  |  | 0.053115 |  |  | 0.30611 |  |  | -0.019797
[13 empty] | C Non choked w/ reducers | 5 |  | 3.9689 |  |  | 25.5692 |  |  | 67.3029 |  |  | 182.1189 |  |  | #NUM! |  |  | -146.2096 |  |  | -1935.4749 |  |  | 2251.6829 |  |  | 353.4059 |  |  | -5892.6564
[13 empty] | C Choked w/ reducers | 5 |  | 3.5535 |  |  | 22.7872 |  |  | 58.551 |  |  | 134.4529 |  |  | 388.8899 |  |  | 3194.6607 |  |  | 457.2592 |  |  | 302.2087 |  |  | 234.0098 |  |  | 305.9147
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3.9689 |  |  | 25.5692 |  |  | 67.3029 |  |  | 182.1189 |  |  | #NUM! |  |  | 3194.6607 |  |  | 457.2592 |  |  | 302.2087 |  |  | 234.0098 |  |  | 305.9147
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.76111 | 751.9563 |  | 13.9692 | 4781.729 |  | 44.3029 | 11708.6979 |  | 142.7189 | 22805.555 |  | 18000 | 38260.6269 |  | 18000 | 55842.4271 |  | 18000 | 73784.0945 |  | 18000 | 90930.9234 |  | 18000 | 105567.9791 |  | 18000 | 123786.7579
[13 empty] | Next iteration flow rate |  |  | 766.9955 | Abs Value of | Flow this | 4829.5463 | Abs Value of | Flow this | 11825.7849 | Abs Value of | Flow this | 23033.6105 | Abs Value of | Flow this | 38643.2332 | Abs Value of | Flow this | 56400.8514 | Abs Value of | Flow this | 74521.9354 | Abs Value of | Flow this | 91840.2326 | Abs Value of | Flow this | 106623.6589 | Abs Value of | Flow this | 125024.6255 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2116 |  |  | 89.4937 |  |  | 85.8145 |  |  | 73.4783 |  |  | 43.0798 |  |  | -10.2105 |  |  | -85.1201 |  |  | -176.0901 |  |  | -268.7293 |  |  | -403.3178
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43516 |  |  | 0.4317 |  |  | 0.41395 |  |  | 0.35444 |  |  | 0.20781 |  |  | -0.049253 |  |  | -0.4106 |  |  | -0.84941 |  |  | -1.2963 |  |  | -1.9455
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2116 |  |  | 29.4937 |  |  | 25.8145 |  |  | 13.4783 |  |  | -16.9202 |  |  | -70.2105 |  |  | -145.1201 |  |  | -236.0901 |  |  | -328.7293 |  |  | -463.3178
[13 empty] | Press drop ratio this iteration |  |  | 0.3349 |  |  | 0.32956 |  |  | 0.30082 |  |  | 0.18343 |  |  | -0.39276 |  |  | 6.8763 |  |  | 1.7049 |  |  | 1.3407 |  |  | 1.2233 |  |  | 1.1488
[13 empty] | Expansion factor | 12 |  | 0.82558 |  |  | 0.8284 |  |  | 0.84188 |  |  | 0.90222 |  |  | 1.2159 |  |  | -3.0059 |  |  | -0.06856 |  |  | 0.060449 |  |  | 0.30952 |  |  | -0.016544
[13 empty] | C Non choked w/ reducers | 5 |  | 4.0483 |  |  | 25.8315 |  |  | 68.0948 |  |  | 186.1939 |  |  | #NUM! |  |  | -166.4984 |  |  | -2407.5788 |  |  | 1946.2757 |  |  | 344.567 |  |  | -6961.0617
[13 empty] | C Choked w/ reducers | 5 |  | 3.6246 |  |  | 23.0188 |  |  | 59.1964 |  |  | 136.4074 |  |  | 401.2494 |  |  | 2601.2 |  |  | 443.0856 |  |  | 296.1348 |  |  | 230.1292 |  |  | 301.5238
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.0483 |  |  | 25.8315 |  |  | 68.0948 |  |  | 186.1939 |  |  | #NUM! |  |  | 2601.2 |  |  | 443.0856 |  |  | 296.1348 |  |  | 230.1292 |  |  | 301.5238
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.68168 | 766.9955 |  | 14.2315 | 4829.5463 |  | 45.0948 | 11825.7849 |  | 146.7939 | 23033.6105 |  | 18000 | 38643.2332 |  | 18000 | 56400.8514 |  | 18000 | 74521.9354 |  | 18000 | 91840.2326 |  | 18000 | 106623.6589 |  | 18000 | 125024.6255
[13 empty] | Next iteration flow rate |  |  | 782.3354 | Abs Value of | Flow this | 4877.8418 | Abs Value of | Flow this | 11944.0428 | Abs Value of | Flow this | 23263.9466 | Abs Value of | Flow this | 39029.6655 | Abs Value of | Flow this | 56964.8599 | Abs Value of | Flow this | 75267.1548 | Abs Value of | Flow this | 92758.6349 | Abs Value of | Flow this | 107689.8955 | Abs Value of | Flow this | 126274.8717 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2109 |  |  | 89.4789 |  |  | 85.7257 |  |  | 73.1416 |  |  | 42.1321 |  |  | -12.2293 |  |  | -88.6446 |  |  | -181.4431 |  |  | -275.9444 |  |  | -413.2381
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43515 |  |  | 0.43162 |  |  | 0.41352 |  |  | 0.35282 |  |  | 0.20323 |  |  | -0.058991 |  |  | -0.4276 |  |  | -0.87524 |  |  | -1.3311 |  |  | -1.9934
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2109 |  |  | 29.4789 |  |  | 25.7257 |  |  | 13.1416 |  |  | -17.8679 |  |  | -72.2293 |  |  | -148.6446 |  |  | -241.4431 |  |  | -335.9444 |  |  | -473.2381
[13 empty] | Press drop ratio this iteration |  |  | 0.33489 |  |  | 0.32945 |  |  | 0.30009 |  |  | 0.17967 |  |  | -0.42409 |  |  | 5.9062 |  |  | 1.6769 |  |  | 1.3307 |  |  | 1.2174 |  |  | 1.1452
[13 empty] | Expansion factor | 12 |  | 0.82559 |  |  | 0.82846 |  |  | 0.84226 |  |  | 0.90422 |  |  | 1.2331 |  |  | -2.4408 |  |  | -0.050994 |  |  | 0.067494 |  |  | 0.31281 |  |  | -0.013384
[13 empty] | C Non choked w/ reducers | 5 |  | 4.1293 |  |  | 26.0967 |  |  | 68.8988 |  |  | 190.4646 |  |  | #NUM! |  |  | -186.5716 |  |  | -3165.4237 |  |  | 1715.0679 |  |  | 336.1462 |  |  | -8495.3529
[13 empty] | C Choked w/ reducers | 5 |  | 3.6972 |  |  | 23.2529 |  |  | 59.8503 |  |  | 138.4057 |  |  | 414.3778 |  |  | 2193.5036 |  |  | 429.7231 |  |  | 290.272 |  |  | 226.3532 |  |  | 297.2282
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.1293 |  |  | 26.0967 |  |  | 68.8988 |  |  | 190.4646 |  |  | #NUM! |  |  | 2193.5036 |  |  | 429.7231 |  |  | 290.272 |  |  | 226.3532 |  |  | 297.2282
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.60066 | 782.3354 |  | 14.4967 | 4877.8418 |  | 45.8988 | 11944.0428 |  | 151.0646 | 23263.9466 |  | 18000 | 39029.6655 |  | 18000 | 56964.8599 |  | 18000 | 75267.1548 |  | 18000 | 92758.6349 |  | 18000 | 107689.8955 |  | 18000 | 126274.8717
[13 empty] | Next iteration flow rate |  |  | 797.9821 | Abs Value of | Flow this | 4926.6202 | Abs Value of | Flow this | 12063.4832 | Abs Value of | Flow this | 23496.5861 | Abs Value of | Flow this | 39419.9622 | Abs Value of | Flow this | 57534.5085 | Abs Value of | Flow this | 76019.8263 | Abs Value of | Flow this | 93686.2213 | Abs Value of | Flow this | 108766.7944 | Abs Value of | Flow this | 127537.6204 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2101 |  |  | 89.4638 |  |  | 85.6352 |  |  | 72.7982 |  |  | 41.1653 |  |  | -14.2888 |  |  | -92.24 |  |  | -186.9037 |  |  | -283.3045 |  |  | -423.3578
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43515 |  |  | 0.43155 |  |  | 0.41308 |  |  | 0.35116 |  |  | 0.19857 |  |  | -0.068925 |  |  | -0.44494 |  |  | -0.90158 |  |  | -1.3666 |  |  | -2.0422
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2101 |  |  | 29.4638 |  |  | 25.6352 |  |  | 12.7982 |  |  | -18.8347 |  |  | -74.2888 |  |  | -152.24 |  |  | -246.9037 |  |  | -343.3045 |  |  | -483.3578
[13 empty] | Press drop ratio this iteration |  |  | 0.33489 |  |  | 0.32934 |  |  | 0.29935 |  |  | 0.1758 |  |  | -0.45754 |  |  | 5.1991 |  |  | 1.6505 |  |  | 1.321 |  |  | 1.2118 |  |  | 1.1417
[13 empty] | Expansion factor | 12 |  | 0.82559 |  |  | 0.82852 |  |  | 0.84265 |  |  | 0.90629 |  |  | 1.2515 |  |  | -2.0288 |  |  | -0.034458 |  |  | 0.074264 |  |  | 0.316 |  |  | -0.010313
[13 empty] | C Non choked w/ reducers | 5 |  | 4.212 |  |  | 26.3648 |  |  | 69.7152 |  |  | 194.9481 |  |  | #NUM! |  |  | -206.7996 |  |  | -4583.0707 |  |  | 1533.8818 |  |  | 328.1128 |  |  | -10885.8711
[13 empty] | C Choked w/ reducers | 5 |  | 3.7711 |  |  | 23.4893 |  |  | 60.5127 |  |  | 140.4494 |  |  | 428.3507 |  |  | 1896.1281 |  |  | 417.1028 |  |  | 284.6093 |  |  | 222.6774 |  |  | 293.0247
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.212 |  |  | 26.3648 |  |  | 69.7152 |  |  | 194.9481 |  |  | #NUM! |  |  | 1896.1281 |  |  | 417.1028 |  |  | 284.6093 |  |  | 222.6774 |  |  | 293.0247
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.51801 | 797.9821 |  | 14.7648 | 4926.6202 |  | 46.7152 | 12063.4832 |  | 155.5481 | 23496.5861 |  | 18000 | 39419.9622 |  | 18000 | 57534.5085 |  | 18000 | 76019.8263 |  | 18000 | 93686.2213 |  | 18000 | 108766.7944 |  | 18000 | 127537.6204
[13 empty] | Next iteration flow rate |  |  | 813.9417 | Abs Value of | Flow this | 4975.8864 | Abs Value of | Flow this | 12184.118 | Abs Value of | Flow this | 23731.552 | Abs Value of | Flow this | 39814.1618 | Abs Value of | Flow this | 58109.8536 | Abs Value of | Flow this | 76780.0246 | Abs Value of | Flow this | 94623.0835 | Abs Value of | Flow this | 109854.4624 | Abs Value of | Flow this | 128812.9966 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2093 |  |  | 89.4484 |  |  | 85.5428 |  |  | 72.4478 |  |  | 40.1791 |  |  | -16.3896 |  |  | -95.9077 |  |  | -192.4741 |  |  | -290.8125 |  |  | -433.6809
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43515 |  |  | 0.43148 |  |  | 0.41264 |  |  | 0.34947 |  |  | 0.19381 |  |  | -0.079059 |  |  | -0.46263 |  |  | -0.92845 |  |  | -1.4028 |  |  | -2.092
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2093 |  |  | 29.4484 |  |  | 25.5428 |  |  | 12.4478 |  |  | -19.8209 |  |  | -76.3896 |  |  | -155.9077 |  |  | -252.4741 |  |  | -350.8125 |  |  | -493.6809
[13 empty] | Press drop ratio this iteration |  |  | 0.33488 |  |  | 0.32922 |  |  | 0.2986 |  |  | 0.17182 |  |  | -0.49331 |  |  | 4.6609 |  |  | 1.6256 |  |  | 1.3117 |  |  | 1.2063 |  |  | 1.1384
[13 empty] | Expansion factor | 12 |  | 0.82559 |  |  | 0.82858 |  |  | 0.84304 |  |  | 0.90841 |  |  | 1.2711 |  |  | -1.7153 |  |  | -0.018868 |  |  | 0.080775 |  |  | 0.31909 |  |  | -0.0073276
[13 empty] | C Non choked w/ reducers | 5 |  | 4.2963 |  |  | 26.6358 |  |  | 70.5443 |  |  | 199.6636 |  |  | #NUM! |  |  | -227.4798 |  |  | -8192.5919 |  |  | 1388.017 |  |  | 320.4393 |  |  | -15127.9756
[13 empty] | C Choked w/ reducers | 5 |  | 3.8466 |  |  | 23.7283 |  |  | 61.1838 |  |  | 142.5399 |  |  | 443.2532 |  |  | 1669.6119 |  |  | 405.1637 |  |  | 279.1361 |  |  | 219.0977 |  |  | 288.9101
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.2963 |  |  | 26.6358 |  |  | 70.5443 |  |  | 199.6636 |  |  | #NUM! |  |  | 1669.6119 |  |  | 405.1637 |  |  | 279.1361 |  |  | 219.0977 |  |  | 288.9101
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.43371 | 813.9417 |  | 15.0358 | 4975.8864 |  | 47.5443 | 12184.118 |  | 160.2636 | 23731.552 |  | 18000 | 39814.1618 |  | 18000 | 58109.8536 |  | 18000 | 76780.0246 |  | 18000 | 94623.0835 |  | 18000 | 109854.4624 |  | 18000 | 128812.9966
[13 empty] | Next iteration flow rate |  |  | 830.2205 | Abs Value of | Flow this | 5025.6453 | Abs Value of | Flow this | 12305.9592 | Abs Value of | Flow this | 23968.8675 | Abs Value of | Flow this | 40212.3034 | Abs Value of | Flow this | 58690.9521 | Abs Value of | Flow this | 77547.8248 | Abs Value of | Flow this | 95569.3143 | Abs Value of | Flow this | 110953.007 | Abs Value of | Flow this | 130101.1266 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2084 |  |  | 89.4327 |  |  | 85.4486 |  |  | 72.0903 |  |  | 39.1731 |  |  | -18.5327 |  |  | -99.6491 |  |  | -198.1565 |  |  | -298.4715 |  |  | -444.2115
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43514 |  |  | 0.4314 |  |  | 0.41218 |  |  | 0.34775 |  |  | 0.18896 |  |  | -0.089397 |  |  | -0.48068 |  |  | -0.95586 |  |  | -1.4398 |  |  | -2.1428
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2084 |  |  | 29.4327 |  |  | 25.4486 |  |  | 12.0903 |  |  | -20.8269 |  |  | -78.5327 |  |  | -159.6491 |  |  | -258.1565 |  |  | -358.4715 |  |  | -504.2115
[13 empty] | Press drop ratio this iteration |  |  | 0.33487 |  |  | 0.3291 |  |  | 0.29782 |  |  | 0.16771 |  |  | -0.53166 |  |  | 4.2375 |  |  | 1.6021 |  |  | 1.3028 |  |  | 1.201 |  |  | 1.1351
[13 empty] | Expansion factor | 12 |  | 0.82559 |  |  | 0.82864 |  |  | 0.84345 |  |  | 0.9106 |  |  | 1.2922 |  |  | -1.4686 |  |  | -0.0041458 |  |  | 0.087039 |  |  | 0.32208 |  |  | -0.0044253
[13 empty] | C Non choked w/ reducers | 5 |  | 4.3823 |  |  | 26.9097 |  |  | 71.3864 |  |  | 204.6329 |  |  | #NUM! |  |  | -248.8774 |  |  | -36508.0843 |  |  | 1268.0206 |  |  | 313.1008 |  |  | -24735.8225
[13 empty] | C Choked w/ reducers | 5 |  | 3.9236 |  |  | 23.9698 |  |  | 61.8638 |  |  | 144.6791 |  |  | 459.1831 |  |  | 1491.3087 |  |  | 393.8512 |  |  | 273.8429 |  |  | 215.6103 |  |  | 284.8818
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.3823 |  |  | 26.9097 |  |  | 71.3864 |  |  | 204.6329 |  |  | #NUM! |  |  | 1491.3087 |  |  | 393.8512 |  |  | 273.8429 |  |  | 215.6103 |  |  | 284.8818
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.34772 | 830.2205 |  | 15.3097 | 5025.6453 |  | 48.3864 | 12305.9592 |  | 165.2329 | 23968.8675 |  | 18000 | 40212.3034 |  | 18000 | 58690.9521 |  | 18000 | 77547.8248 |  | 18000 | 95569.3143 |  | 18000 | 110953.007 |  | 18000 | 130101.1266
[13 empty] | Next iteration flow rate |  |  | 846.825 | Abs Value of | Flow this | 5075.9017 | Abs Value of | Flow this | 12429.0188 | Abs Value of | Flow this | 24208.5562 | Abs Value of | Flow this | 40614.4265 | Abs Value of | Flow this | 59277.8616 | Abs Value of | Flow this | 78323.3031 | Abs Value of | Flow this | 96525.0075 | Abs Value of | Flow this | 112062.5371 | Abs Value of | Flow this | 131402.1379 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2075 |  |  | 89.4167 |  |  | 85.3525 |  |  | 71.7257 |  |  | 38.1468 |  |  | -20.7188 |  |  | -103.4656 |  |  | -203.9531 |  |  | -306.2844 |  |  | -454.9538
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43514 |  |  | 0.43132 |  |  | 0.41172 |  |  | 0.34599 |  |  | 0.18401 |  |  | -0.099942 |  |  | -0.49909 |  |  | -0.98382 |  |  | -1.4774 |  |  | -2.1946
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2075 |  |  | 29.4167 |  |  | 25.3525 |  |  | 11.7257 |  |  | -21.8532 |  |  | -80.7188 |  |  | -163.4656 |  |  | -263.9531 |  |  | -366.2844 |  |  | -514.9538
[13 empty] | Press drop ratio this iteration |  |  | 0.33487 |  |  | 0.32898 |  |  | 0.29703 |  |  | 0.16348 |  |  | -0.57287 |  |  | 3.8959 |  |  | 1.5799 |  |  | 1.2942 |  |  | 1.1959 |  |  | 1.1319
[13 empty] | Expansion factor | 12 |  | 0.8256 |  |  | 0.8287 |  |  | 0.84387 |  |  | 0.91286 |  |  | 1.3148 |  |  | -1.2696 |  |  | 0.0097748 |  |  | 0.09307 |  |  | 0.32497 |  |  | -0.0016031
[13 empty] | C Non choked w/ reducers | 5 |  | 4.47 |  |  | 27.1866 |  |  | 72.2419 |  |  | 209.8809 |  |  | #NUM! |  |  | -271.2494 |  |  | 15167.7073 |  |  | 1167.5377 |  |  | 306.0745 |  |  | -67430.3471
[13 empty] | C Choked w/ reducers | 5 |  | 4.0021 |  |  | 24.2139 |  |  | 62.5528 |  |  | 146.8687 |  |  | 476.2516 |  |  | 1347.2936 |  |  | 383.1163 |  |  | 268.7206 |  |  | 212.2114 |  |  | 280.9367
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.47 |  |  | 27.1866 |  |  | 72.2419 |  |  | 209.8809 |  |  | #NUM! |  |  | 1347.2936 |  |  | 383.1163 |  |  | 268.7206 |  |  | 212.2114 |  |  | 280.9367
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.26001 | 846.825 |  | 15.5866 | 5075.9017 |  | 49.2419 | 12429.0188 |  | 170.4809 | 24208.5562 |  | 18000 | 40614.4265 |  | 18000 | 59277.8616 |  | 18000 | 78323.3031 |  | 18000 | 96525.0075 |  | 18000 | 112062.5371 |  | 18000 | 131402.1379
[13 empty] | Next iteration flow rate |  |  | 863.7615 | Abs Value of | Flow this | 5126.6607 | Abs Value of | Flow this | 12553.309 | Abs Value of | Flow this | 24450.6417 | Abs Value of | Flow this | 41020.5707 | Abs Value of | Flow this | 59870.6402 | Abs Value of | Flow this | 79106.5361 | Abs Value of | Flow this | 97490.2575 | Abs Value of | Flow this | 113183.1624 | Abs Value of | Flow this | 132716.1593 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2066 |  |  | 89.4003 |  |  | 85.2545 |  |  | 71.3538 |  |  | 37.1 |  |  | -22.9489 |  |  | -107.3589 |  |  | -209.8661 |  |  | -314.2543 |  |  | -465.912
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43513 |  |  | 0.43124 |  |  | 0.41125 |  |  | 0.34419 |  |  | 0.17896 |  |  | -0.1107 |  |  | -0.51787 |  |  | -1.0123 |  |  | -1.5159 |  |  | -2.2474
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2066 |  |  | 29.4003 |  |  | 25.2545 |  |  | 11.3538 |  |  | -22.9 |  |  | -82.9489 |  |  | -167.3589 |  |  | -269.8661 |  |  | -374.2543 |  |  | -525.912
[13 empty] | Press drop ratio this iteration |  |  | 0.33486 |  |  | 0.32886 |  |  | 0.29622 |  |  | 0.15912 |  |  | -0.61725 |  |  | 3.6145 |  |  | 1.5589 |  |  | 1.2859 |  |  | 1.1909 |  |  | 1.1288
[13 empty] | Expansion factor | 12 |  | 0.8256 |  |  | 0.82877 |  |  | 0.84429 |  |  | 0.91518 |  |  | 1.3392 |  |  | -1.1057 |  |  | 0.022955 |  |  | 0.098878 |  |  | 0.32778 |  |  | 0.0011417
[13 empty] | C Non choked w/ reducers | 5 |  | 4.5595 |  |  | 27.4665 |  |  | 73.111 |  |  | 215.4361 |  |  | #NUM! |  |  | -294.8615 |  |  | 6328.9503 |  |  | 1082.1382 |  |  | 299.3398 |  |  | 93510.5917
[13 empty] | C Choked w/ reducers | 5 |  | 4.0822 |  |  | 24.4605 |  |  | 63.251 |  |  | 149.1106 |  |  | 494.5872 |  |  | 1228.5329 |  |  | 372.9151 |  |  | 263.7607 |  |  | 208.8977 |  |  | 277.0724
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.5595 |  |  | 27.4665 |  |  | 73.111 |  |  | 215.4361 |  |  | #NUM! |  |  | 1228.5329 |  |  | 372.9151 |  |  | 263.7607 |  |  | 208.8977 |  |  | 277.0724
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.17054 | 863.7615 |  | 15.8665 | 5126.6607 |  | 50.111 | 12553.309 |  | 176.0361 | 24450.6417 |  | 18000 | 41020.5707 |  | 18000 | 59870.6402 |  | 18000 | 79106.5361 |  | 18000 | 97490.2575 |  | 18000 | 113183.1624 |  | 18000 | 132716.1593
[13 empty] | Next iteration flow rate |  |  | 881.0367 | Abs Value of | Flow this | 5177.9273 | Abs Value of | Flow this | 12678.8421 | Abs Value of | Flow this | 24695.1481 | Abs Value of | Flow this | 41430.7764 | Abs Value of | Flow this | 60469.3466 | Abs Value of | Flow this | 79897.6015 | Abs Value of | Flow this | 98465.1601 | Abs Value of | Flow this | 114314.9941 | Abs Value of | Flow this | 134043.3208 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2057 |  |  | 89.3836 |  |  | 85.1545 |  |  | 70.9744 |  |  | 36.032 |  |  | -25.2238 |  |  | -111.3305 |  |  | -215.8981 |  |  | -322.3844 |  |  | -477.0905
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43513 |  |  | 0.43116 |  |  | 0.41076 |  |  | 0.34236 |  |  | 0.17381 |  |  | -0.12167 |  |  | -0.53703 |  |  | -1.0414 |  |  | -1.5551 |  |  | -2.3014
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2057 |  |  | 29.3836 |  |  | 25.1545 |  |  | 10.9744 |  |  | -23.968 |  |  | -85.2238 |  |  | -171.3305 |  |  | -275.8981 |  |  | -382.3844 |  |  | -537.0905
[13 empty] | Press drop ratio this iteration |  |  | 0.33485 |  |  | 0.32874 |  |  | 0.2954 |  |  | 0.15462 |  |  | -0.66518 |  |  | 3.3787 |  |  | 1.5389 |  |  | 1.2779 |  |  | 1.1861 |  |  | 1.1258
[13 empty] | Expansion factor | 12 |  | 0.82561 |  |  | 0.82883 |  |  | 0.84472 |  |  | 0.91758 |  |  | 1.3656 |  |  | -0.96833 |  |  | 0.035451 |  |  | 0.10448 |  |  | 0.33049 |  |  | 0.0038118
[13 empty] | C Non choked w/ reducers | 5 |  | 4.6507 |  |  | 27.7494 |  |  | 73.9941 |  |  | 221.3311 |  |  | #NUM! |  |  | -320.0027 |  |  | 4017.2373 |  |  | 1008.6397 |  |  | 292.8779 |  |  | 27662.2269
[13 empty] | C Choked w/ reducers | 5 |  | 4.1638 |  |  | 24.7097 |  |  | 63.9585 |  |  | 151.4068 |  |  | 514.3383 |  |  | 1128.9105 |  |  | 363.208 |  |  | 258.9555 |  |  | 205.6659 |  |  | 273.2863
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.6507 |  |  | 27.7494 |  |  | 73.9941 |  |  | 221.3311 |  |  | #NUM! |  |  | 1128.9105 |  |  | 363.208 |  |  | 258.9555 |  |  | 205.6659 |  |  | 273.2863
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.07927 | 881.0367 |  | 16.1494 | 5177.9273 |  | 50.9941 | 12678.8421 |  | 181.9311 | 24695.1481 |  | 18000 | 41430.7764 |  | 18000 | 60469.3466 |  | 18000 | 79897.6015 |  | 18000 | 98465.1601 |  | 18000 | 114314.9941 |  | 18000 | 134043.3208
[13 empty] | Next iteration flow rate |  |  | 898.6574 | Abs Value of | Flow this | 5229.7066 | Abs Value of | Flow this | 12805.6305 | Abs Value of | Flow this | 24942.0996 | Abs Value of | Flow this | 41845.0842 | Abs Value of | Flow this | 61074.0401 | Abs Value of | Flow this | 80696.5775 | Abs Value of | Flow this | 99449.8117 | Abs Value of | Flow this | 115458.144 | Abs Value of | Flow this | 135383.7541 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2047 |  |  | 89.3666 |  |  | 85.0524 |  |  | 70.5873 |  |  | 34.9427 |  |  | -27.5444 |  |  | -115.3818 |  |  | -222.0512 |  |  | -330.678 |  |  | -488.4936
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43512 |  |  | 0.43108 |  |  | 0.41027 |  |  | 0.3405 |  |  | 0.16855 |  |  | -0.13287 |  |  | -0.55657 |  |  | -1.0711 |  |  | -1.5951 |  |  | -2.3564
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2047 |  |  | 29.3666 |  |  | 25.0524 |  |  | 10.5873 |  |  | -25.0573 |  |  | -87.5444 |  |  | -175.3818 |  |  | -282.0512 |  |  | -390.678 |  |  | -548.4936
[13 empty] | Press drop ratio this iteration |  |  | 0.33485 |  |  | 0.32861 |  |  | 0.29455 |  |  | 0.14999 |  |  | -0.7171 |  |  | 3.1783 |  |  | 1.52 |  |  | 1.2702 |  |  | 1.1814 |  |  | 1.1228
[13 empty] | Expansion factor | 12 |  | 0.82561 |  |  | 0.8289 |  |  | 0.84517 |  |  | 0.92005 |  |  | 1.3941 |  |  | -0.85158 |  |  | 0.047312 |  |  | 0.10987 |  |  | 0.33313 |  |  | 0.0064096
[13 empty] | C Non choked w/ reducers | 5 |  | 4.7438 |  |  | 28.0354 |  |  | 74.8916 |  |  | 227.604 |  |  | #NUM! |  |  | -346.9989 |  |  | 2951.7121 |  |  | 944.6965 |  |  | 286.6714 |  |  | 16248.4686
[13 empty] | C Choked w/ reducers | 5 |  | 4.2472 |  |  | 24.9615 |  |  | 64.6756 |  |  | 153.7594 |  |  | 535.6772 |  |  | 1044.1374 |  |  | 353.9594 |  |  | 254.2975 |  |  | 202.5128 |  |  | 269.5759
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.7438 |  |  | 28.0354 |  |  | 74.8916 |  |  | 227.604 |  |  | #NUM! |  |  | 1044.1374 |  |  | 353.9594 |  |  | 254.2975 |  |  | 202.5128 |  |  | 269.5759
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.013826 | 898.6574 |  | 16.4354 | 5229.7066 |  | 51.8916 | 12805.6305 |  | 188.204 | 24942.0996 |  | 18000 | 41845.0842 |  | 18000 | 61074.0401 |  | 18000 | 80696.5775 |  | 18000 | 99449.8117 |  | 18000 | 115458.144 |  | 18000 | 135383.7541
[13 empty] | Next iteration flow rate |  |  | 916.6306 | Abs Value of | Flow this | 5282.0037 | Abs Value of | Flow this | 12933.6868 | Abs Value of | Flow this | 25191.5206 | Abs Value of | Flow this | 42263.535 | Abs Value of | Flow this | 61684.7805 | Abs Value of | Flow this | 81503.5433 | Abs Value of | Flow this | 100444.3098 | Abs Value of | Flow this | 116612.7255 | Abs Value of | Flow this | 136737.5916 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2036 |  |  | 89.3493 |  |  | 84.9484 |  |  | 70.1925 |  |  | 33.8314 |  |  | -29.9117 |  |  | -119.5146 |  |  | -228.3281 |  |  | -339.1383 |  |  | -500.1259
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43512 |  |  | 0.431 |  |  | 0.40977 |  |  | 0.33859 |  |  | 0.16319 |  |  | -0.14429 |  |  | -0.57651 |  |  | -1.1014 |  |  | -1.6359 |  |  | -2.4125
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2036 |  |  | 29.3493 |  |  | 24.9484 |  |  | 10.1925 |  |  | -26.1686 |  |  | -89.9117 |  |  | -179.5146 |  |  | -288.3281 |  |  | -399.1383 |  |  | -560.1259
[13 empty] | Press drop ratio this iteration |  |  | 0.33484 |  |  | 0.32848 |  |  | 0.29369 |  |  | 0.14521 |  |  | -0.7735 |  |  | 3.0059 |  |  | 1.502 |  |  | 1.2628 |  |  | 1.1769 |  |  | 1.12
[13 empty] | Expansion factor | 12 |  | 0.82561 |  |  | 0.82897 |  |  | 0.84562 |  |  | 0.9226 |  |  | 1.4251 |  |  | -0.75115 |  |  | 0.058582 |  |  | 0.11508 |  |  | 0.33568 |  |  | 0.0089376
[13 empty] | C Non choked w/ reducers | 5 |  | 4.8388 |  |  | 28.3246 |  |  | 75.8038 |  |  | 234.299 |  |  | #NUM! |  |  | -376.2288 |  |  | 2338.2953 |  |  | 888.5421 |  |  | 280.7047 |  |  | 11510.0406
[13 empty] | C Choked w/ reducers | 5 |  | 4.3322 |  |  | 25.216 |  |  | 65.4024 |  |  | 156.1705 |  |  | 558.8056 |  |  | 971.1173 |  |  | 345.1367 |  |  | 249.7798 |  |  | 199.4354 |  |  | 265.939
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.8388 |  |  | 28.3246 |  |  | 75.8038 |  |  | 234.299 |  |  | #NUM! |  |  | 971.1173 |  |  | 345.1367 |  |  | 249.7798 |  |  | 199.4354 |  |  | 265.939
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.10879 | 916.6306 |  | 16.7246 | 5282.0037 |  | 52.8038 | 12933.6868 |  | 194.899 | 25191.5206 |  | 18000 | 42263.535 |  | 18000 | 61684.7805 |  | 18000 | 81503.5433 |  | 18000 | 100444.3098 |  | 18000 | 116612.7255 |  | 18000 | 136737.5916
[13 empty] | Next iteration flow rate |  |  | 934.9632 | Abs Value of | Flow this | 5334.8237 | Abs Value of | Flow this | 13063.0237 | Abs Value of | Flow this | 25443.4358 | Abs Value of | Flow this | 42686.1704 | Abs Value of | Flow this | 62301.6283 | Abs Value of | Flow this | 82318.5787 | Abs Value of | Flow this | 101448.7529 | Abs Value of | Flow this | 117778.8527 | Abs Value of | Flow this | 138104.9675 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2026 |  |  | 89.3316 |  |  | 84.8422 |  |  | 69.7898 |  |  | 32.6978 |  |  | -32.3265 |  |  | -123.7305 |  |  | -234.7311 |  |  | -347.7686 |  |  | -511.9921
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43511 |  |  | 0.43091 |  |  | 0.40926 |  |  | 0.33665 |  |  | 0.15773 |  |  | -0.15594 |  |  | -0.59684 |  |  | -1.1323 |  |  | -1.6775 |  |  | -2.4697
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2026 |  |  | 29.3316 |  |  | 24.8422 |  |  | 9.7898 |  |  | -27.3022 |  |  | -92.3265 |  |  | -183.7305 |  |  | -294.7311 |  |  | -407.7686 |  |  | -571.9921
[13 empty] | Press drop ratio this iteration |  |  | 0.33483 |  |  | 0.32834 |  |  | 0.2928 |  |  | 0.14028 |  |  | -0.83499 |  |  | 2.8561 |  |  | 1.4849 |  |  | 1.2556 |  |  | 1.1725 |  |  | 1.1172
[13 empty] | Expansion factor | 12 |  | 0.82562 |  |  | 0.82903 |  |  | 0.84609 |  |  | 0.92523 |  |  | 1.4589 |  |  | -0.66385 |  |  | 0.069303 |  |  | 0.1201 |  |  | 0.33816 |  |  | 0.011398
[13 empty] | C Non choked w/ reducers | 5 |  | 4.9357 |  |  | 28.6169 |  |  | 76.7311 |  |  | 241.4683 |  |  | #NUM! |  |  | -408.1434 |  |  | 1939.3812 |  |  | 838.8205 |  |  | 274.9633 |  |  | 8915.4747
[13 empty] | C Choked w/ reducers | 5 |  | 4.4189 |  |  | 25.4733 |  |  | 66.1391 |  |  | 158.6425 |  |  | 583.9609 |  |  | 907.5587 |  |  | 336.7106 |  |  | 245.3959 |  |  | 196.4311 |  |  | 262.3732
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 4.9357 |  |  | 28.6169 |  |  | 76.7311 |  |  | 241.4683 |  |  | #NUM! |  |  | 907.5587 |  |  | 336.7106 |  |  | 245.3959 |  |  | 196.4311 |  |  | 262.3732
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.20566 | 934.9632 |  | 17.0169 | 5334.8237 |  | 53.7311 | 13063.0237 |  | 202.0683 | 25443.4358 |  | 18000 | 42686.1704 |  | 18000 | 62301.6283 |  | 18000 | 82318.5787 |  | 18000 | 101448.7529 |  | 18000 | 117778.8527 |  | 18000 | 138104.9675
[13 empty] | Next iteration flow rate |  |  | 953.6624 | Abs Value of | Flow this | 5388.172 | Abs Value of | Flow this | 13193.6539 | Abs Value of | Flow this | 25697.8702 | Abs Value of | Flow this | 43113.0321 | Abs Value of | Flow this | 62924.6446 | Abs Value of | Flow this | 83141.7645 | Abs Value of | Flow this | 102463.2405 | Abs Value of | Flow this | 118956.6412 | Abs Value of | Flow this | 139486.0172 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2015 |  |  | 89.3135 |  |  | 84.7339 |  |  | 69.3789 |  |  | 31.5414 |  |  | -34.7899 |  |  | -128.0311 |  |  | -241.2628 |  |  | -356.5723 |  |  | -524.0968
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43511 |  |  | 0.43083 |  |  | 0.40874 |  |  | 0.33467 |  |  | 0.15215 |  |  | -0.16782 |  |  | -0.61759 |  |  | -1.1638 |  |  | -1.72 |  |  | -2.5281
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2015 |  |  | 29.3135 |  |  | 24.7339 |  |  | 9.3789 |  |  | -28.4586 |  |  | -94.7899 |  |  | -188.0311 |  |  | -301.2628 |  |  | -416.5723 |  |  | -584.0968
[13 empty] | Press drop ratio this iteration |  |  | 0.33482 |  |  | 0.32821 |  |  | 0.2919 |  |  | 0.13518 |  |  | -0.90226 |  |  | 2.7246 |  |  | 1.4686 |  |  | 1.2487 |  |  | 1.1683 |  |  | 1.1145
[13 empty] | Expansion factor | 12 |  | 0.82562 |  |  | 0.82911 |  |  | 0.84656 |  |  | 0.92794 |  |  | 1.4959 |  |  | -0.58729 |  |  | 0.079513 |  |  | 0.12495 |  |  | 0.34057 |  |  | 0.013793
[13 empty] | C Non choked w/ reducers | 5 |  | 5.0345 |  |  | 28.9125 |  |  | 77.6739 |  |  | 249.1733 |  |  | #NUM! |  |  | -443.2908 |  |  | 1659.0499 |  |  | 794.4736 |  |  | 269.4338 |  |  | 7277.9854
[13 empty] | C Choked w/ reducers | 5 |  | 4.5073 |  |  | 25.7332 |  |  | 66.8858 |  |  | 161.1777 |  |  | 611.4244 |  |  | 851.7296 |  |  | 328.6544 |  |  | 241.1398 |  |  | 193.497 |  |  | 258.8765
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.0345 |  |  | 28.9125 |  |  | 77.6739 |  |  | 249.1733 |  |  | #NUM! |  |  | 851.7296 |  |  | 328.6544 |  |  | 241.1398 |  |  | 193.497 |  |  | 258.8765
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.30447 | 953.6624 |  | 17.3125 | 5388.172 |  | 54.6739 | 13193.6539 |  | 209.7733 | 25697.8702 |  | 18000 | 43113.0321 |  | 18000 | 62924.6446 |  | 18000 | 83141.7645 |  | 18000 | 102463.2405 |  | 18000 | 118956.6412 |  | 18000 | 139486.0172
[13 empty] | Next iteration flow rate |  |  | 972.7357 | Abs Value of | Flow this | 5442.0537 | Abs Value of | Flow this | 13325.5904 | Abs Value of | Flow this | 25954.8489 | Abs Value of | Flow this | 43544.1624 | Abs Value of | Flow this | 63553.891 | Abs Value of | Flow this | 83973.1821 | Abs Value of | Flow this | 103487.8729 | Abs Value of | Flow this | 120146.2076 | Abs Value of | Flow this | 140880.8774 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.2003 |  |  | 89.2951 |  |  | 84.6234 |  |  | 68.9598 |  |  | 30.3617 |  |  | -37.3028 |  |  | -132.4182 |  |  | -247.9259 |  |  | -365.5531 |  |  | -536.4447
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4351 |  |  | 0.43074 |  |  | 0.4082 |  |  | 0.33264 |  |  | 0.14646 |  |  | -0.17994 |  |  | -0.63875 |  |  | -1.1959 |  |  | -1.7633 |  |  | -2.5877
[13 empty] | Delta P at this iteration flow rate |  |  | 30.2003 |  |  | 29.2951 |  |  | 24.6234 |  |  | 8.9598 |  |  | -29.6383 |  |  | -97.3028 |  |  | -192.4182 |  |  | -307.9259 |  |  | -425.5531 |  |  | -596.4447
[13 empty] | Press drop ratio this iteration |  |  | 0.33481 |  |  | 0.32807 |  |  | 0.29098 |  |  | 0.12993 |  |  | -0.97617 |  |  | 2.6085 |  |  | 1.4531 |  |  | 1.242 |  |  | 1.1641 |  |  | 1.1118
[13 empty] | Expansion factor | 12 |  | 0.82563 |  |  | 0.82918 |  |  | 0.84705 |  |  | 0.93074 |  |  | 1.5365 |  |  | -0.5196 |  |  | 0.089244 |  |  | 0.12963 |  |  | 0.3429 |  |  | 0.016125
[13 empty] | C Non choked w/ reducers | 5 |  | 5.1353 |  |  | 29.2112 |  |  | 78.6326 |  |  | 257.4876 |  |  | #NUM! |  |  | -482.3498 |  |  | 1451.1582 |  |  | 754.6635 |  |  | 264.104 |  |  | 6150.2966
[13 empty] | C Choked w/ reducers | 5 |  | 4.5975 |  |  | 25.9959 |  |  | 67.6429 |  |  | 163.7789 |  |  | 641.5319 |  |  | 802.2964 |  |  | 320.9436 |  |  | 237.0058 |  |  | 190.6307 |  |  | 255.4468
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.1353 |  |  | 29.2112 |  |  | 78.6326 |  |  | 257.4876 |  |  | #NUM! |  |  | 802.2964 |  |  | 320.9436 |  |  | 237.0058 |  |  | 190.6307 |  |  | 255.4468
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.40526 | 972.7357 |  | 17.6112 | 5442.0537 |  | 55.6326 | 13325.5904 |  | 218.0876 | 25954.8489 |  | 18000 | 43544.1624 |  | 18000 | 63553.891 |  | 18000 | 83973.1821 |  | 18000 | 103487.8729 |  | 18000 | 120146.2076 |  | 18000 | 140880.8774
[13 empty] | Next iteration flow rate |  |  | 992.1904 | Abs Value of | Flow this | 5496.4742 | Abs Value of | Flow this | 13458.8463 | Abs Value of | Flow this | 26214.3974 | Abs Value of | Flow this | 43979.604 | Abs Value of | Flow this | 64189.4299 | Abs Value of | Flow this | 84812.9139 | Abs Value of | Flow this | 104522.7516 | Abs Value of | Flow this | 121347.6697 | Abs Value of | Flow this | 142289.6861 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1991 |  |  | 89.2763 |  |  | 84.5107 |  |  | 68.5323 |  |  | 29.1584 |  |  | -39.8662 |  |  | -136.8934 |  |  | -254.7228 |  |  | -374.7143 |  |  | -549.0409
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4351 |  |  | 0.43065 |  |  | 0.40766 |  |  | 0.33058 |  |  | 0.14065 |  |  | -0.1923 |  |  | -0.66034 |  |  | -1.2287 |  |  | -1.8075 |  |  | -2.6484
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1991 |  |  | 29.2763 |  |  | 24.5107 |  |  | 8.5323 |  |  | -30.8416 |  |  | -99.8662 |  |  | -196.8934 |  |  | -314.7228 |  |  | -434.7143 |  |  | -609.0409
[13 empty] | Press drop ratio this iteration |  |  | 0.3348 |  |  | 0.32793 |  |  | 0.29003 |  |  | 0.1245 |  |  | -1.0577 |  |  | 2.505 |  |  | 1.4383 |  |  | 1.2356 |  |  | 1.1601 |  |  | 1.1093
[13 empty] | Expansion factor | 12 |  | 0.82563 |  |  | 0.82925 |  |  | 0.84755 |  |  | 0.93363 |  |  | 1.5813 |  |  | -0.45935 |  |  | 0.098528 |  |  | 0.13416 |  |  | 0.34516 |  |  | 0.018396
[13 empty] | C Non choked w/ reducers | 5 |  | 5.2381 |  |  | 29.5133 |  |  | 79.6076 |  |  | 266.5 |  |  | #NUM! |  |  | -526.1769 |  |  | 1290.7583 |  |  | 718.7183 |  |  | 258.9625 |  |  | 5326.2737
[13 empty] | C Choked w/ reducers | 5 |  | 4.6895 |  |  | 26.2614 |  |  | 68.4104 |  |  | 166.4486 |  |  | 674.6878 |  |  | 758.2155 |  |  | 313.5561 |  |  | 232.9884 |  |  | 187.8297 |  |  | 252.0822
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.2381 |  |  | 29.5133 |  |  | 79.6076 |  |  | 266.5 |  |  | #NUM! |  |  | 758.2155 |  |  | 313.5561 |  |  | 232.9884 |  |  | 187.8297 |  |  | 252.0822
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.50808 | 992.1904 |  | 17.9133 | 5496.4742 |  | 56.6076 | 13458.8463 |  | 227.1 | 26214.3974 |  | 18000 | 43979.604 |  | 18000 | 64189.4299 |  | 18000 | 84812.9139 |  | 18000 | 104522.7516 |  | 18000 | 121347.6697 |  | 18000 | 142289.6861
[13 empty] | Next iteration flow rate |  |  | 1012.0342 | Abs Value of | Flow this | 5551.439 | Abs Value of | Flow this | 13593.4348 | Abs Value of | Flow this | 26476.5413 | Abs Value of | Flow this | 44419.4001 | Abs Value of | Flow this | 64831.3242 | Abs Value of | Flow this | 85661.0431 | Abs Value of | Flow this | 105567.9791 | Abs Value of | Flow this | 122561.1464 | Abs Value of | Flow this | 143712.583 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1978 |  |  | 89.2571 |  |  | 84.3958 |  |  | 68.0961 |  |  | 27.9308 |  |  | -42.4812 |  |  | -141.4586 |  |  | -261.6563 |  |  | -384.0597 |  |  | -561.8903
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43509 |  |  | 0.43055 |  |  | 0.4071 |  |  | 0.32848 |  |  | 0.13473 |  |  | -0.20492 |  |  | -0.68236 |  |  | -1.2622 |  |  | -1.8526 |  |  | -2.7104
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1978 |  |  | 29.2571 |  |  | 24.3958 |  |  | 8.0961 |  |  | -32.0692 |  |  | -102.4812 |  |  | -201.4586 |  |  | -321.6563 |  |  | -444.0597 |  |  | -621.8903
[13 empty] | Press drop ratio this iteration |  |  | 0.3348 |  |  | 0.32778 |  |  | 0.28906 |  |  | 0.11889 |  |  | -1.1482 |  |  | 2.4124 |  |  | 1.4242 |  |  | 1.2293 |  |  | 1.1562 |  |  | 1.1068
[13 empty] | Expansion factor | 12 |  | 0.82564 |  |  | 0.82933 |  |  | 0.84805 |  |  | 0.93662 |  |  | 1.631 |  |  | -0.40538 |  |  | 0.10739 |  |  | 0.13853 |  |  | 0.34736 |  |  | 0.020607
[13 empty] | C Non choked w/ reducers | 5 |  | 5.343 |  |  | 29.8187 |  |  | 80.5995 |  |  | 276.3185 |  |  | #NUM! |  |  | -575.8729 |  |  | 1163.1812 |  |  | 686.0927 |  |  | 253.999 |  |  | 4697.7164
[13 empty] | C Choked w/ reducers | 5 |  | 4.7834 |  |  | 26.5297 |  |  | 69.1886 |  |  | 169.1898 |  |  | 711.3833 |  |  | 718.6588 |  |  | 306.4713 |  |  | 229.0827 |  |  | 185.0918 |  |  | 248.7807
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.343 |  |  | 29.8187 |  |  | 80.5995 |  |  | 276.3185 |  |  | #NUM! |  |  | 718.6588 |  |  | 306.4713 |  |  | 229.0827 |  |  | 185.0918 |  |  | 248.7807
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.61296 | 1012.0342 |  | 18.2187 | 5551.439 |  | 57.5995 | 13593.4348 |  | 236.9185 | 26476.5413 |  | 18000 | 44419.4001 |  | 18000 | 64831.3242 |  | 18000 | 85661.0431 |  | 18000 | 105567.9791 |  | 18000 | 122561.1464 |  | 18000 | 143712.583
[13 empty] | Next iteration flow rate |  |  | 1032.2749 | Abs Value of | Flow this | 5606.9533 | Abs Value of | Flow this | 13729.3692 | Abs Value of | Flow this | 26741.3068 | Abs Value of | Flow this | 44863.5941 | Abs Value of | Flow this | 65479.6375 | Abs Value of | Flow this | 86517.6535 | Abs Value of | Flow this | 106623.6589 | Abs Value of | Flow this | 123786.7579 | Abs Value of | Flow this | 145149.7088 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1965 |  |  | 89.2375 |  |  | 84.2785 |  |  | 67.6512 |  |  | 26.6786 |  |  | -45.1487 |  |  | -146.1155 |  |  | -268.7293 |  |  | -393.5929 |  |  | -574.9979
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43509 |  |  | 0.43046 |  |  | 0.40654 |  |  | 0.32633 |  |  | 0.12869 |  |  | -0.21779 |  |  | -0.70482 |  |  | -1.2963 |  |  | -1.8986 |  |  | -2.7736
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1965 |  |  | 29.2375 |  |  | 24.2785 |  |  | 7.6512 |  |  | -33.3214 |  |  | -105.1487 |  |  | -206.1155 |  |  | -328.7293 |  |  | -453.5929 |  |  | -634.9979
[13 empty] | Press drop ratio this iteration |  |  | 0.33479 |  |  | 0.32764 |  |  | 0.28807 |  |  | 0.1131 |  |  | -1.249 |  |  | 2.3289 |  |  | 1.4106 |  |  | 1.2233 |  |  | 1.1524 |  |  | 1.1043
[13 empty] | Expansion factor | 12 |  | 0.82564 |  |  | 0.8294 |  |  | 0.84857 |  |  | 0.93971 |  |  | 1.6864 |  |  | -0.35677 |  |  | 0.11587 |  |  | 0.14276 |  |  | 0.3495 |  |  | 0.022761
[13 empty] | C Non choked w/ reducers | 5 |  | 5.4499 |  |  | 30.1275 |  |  | 81.6085 |  |  | 287.0766 |  |  | #NUM! |  |  | -632.8815 |  |  | 1059.2375 |  |  | 656.3396 |  |  | 249.2036 |  |  | 4202.3725
[13 empty] | C Choked w/ reducers | 5 |  | 4.8791 |  |  | 26.8009 |  |  | 69.9778 |  |  | 172.0055 |  |  | 752.2214 |  |  | 682.9606 |  |  | 299.6706 |  |  | 225.2838 |  |  | 182.4148 |  |  | 245.5406
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.4499 |  |  | 30.1275 |  |  | 81.6085 |  |  | 287.0766 |  |  | #NUM! |  |  | 682.9606 |  |  | 299.6706 |  |  | 225.2838 |  |  | 182.4148 |  |  | 245.5406
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.71994 | 1032.2749 |  | 18.5275 | 5606.9533 |  | 58.6085 | 13729.3692 |  | 247.6766 | 26741.3068 |  | 18000 | 44863.5941 |  | 18000 | 65479.6375 |  | 18000 | 86517.6535 |  | 18000 | 106623.6589 |  | 18000 | 123786.7579 |  | 18000 | 145149.7088
[13 empty] | Next iteration flow rate |  |  | 1052.9204 | Abs Value of | Flow this | 5663.0229 | Abs Value of | Flow this | 13866.6628 | Abs Value of | Flow this | 27008.7198 | Abs Value of | Flow this | 45312.23 | Abs Value of | Flow this | 66134.4339 | Abs Value of | Flow this | 87382.8301 | Abs Value of | Flow this | 107689.8955 | Abs Value of | Flow this | 125024.6255 | Abs Value of | Flow this | 146601.2059 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1952 |  |  | 89.2176 |  |  | 84.1589 |  |  | 67.1974 |  |  | 25.4012 |  |  | -47.8698 |  |  | -150.8661 |  |  | -275.9444 |  |  | -403.3178 |  |  | -588.369
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43508 |  |  | 0.43036 |  |  | 0.40596 |  |  | 0.32414 |  |  | 0.12253 |  |  | -0.23091 |  |  | -0.72774 |  |  | -1.3311 |  |  | -1.9455 |  |  | -2.8381
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1952 |  |  | 29.2176 |  |  | 24.1589 |  |  | 7.1974 |  |  | -34.5988 |  |  | -107.8698 |  |  | -210.8661 |  |  | -335.9444 |  |  | -463.3178 |  |  | -648.369
[13 empty] | Press drop ratio this iteration |  |  | 0.33478 |  |  | 0.32749 |  |  | 0.28706 |  |  | 0.10711 |  |  | -1.3621 |  |  | 2.2534 |  |  | 1.3977 |  |  | 1.2174 |  |  | 1.1488 |  |  | 1.102
[13 empty] | Expansion factor | 12 |  | 0.82565 |  |  | 0.82948 |  |  | 0.84911 |  |  | 0.94291 |  |  | 1.7486 |  |  | -0.31276 |  |  | 0.12397 |  |  | 0.14685 |  |  | 0.35157 |  |  | 0.02486
[13 empty] | C Non choked w/ reducers | 5 |  | 5.5591 |  |  | 30.4397 |  |  | 82.6353 |  |  | 298.9411 |  |  | #NUM! |  |  | -699.1385 |  |  | 972.8768 |  |  | 629.0889 |  |  | 244.5676 |  |  | 3801.8885
[13 empty] | C Choked w/ reducers | 5 |  | 4.9768 |  |  | 27.0749 |  |  | 70.778 |  |  | 174.8988 |  |  | 797.9499 |  |  | 650.5797 |  |  | 293.1367 |  |  | 221.5872 |  |  | 179.7966 |  |  | 242.3601
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.5591 |  |  | 30.4397 |  |  | 82.6353 |  |  | 298.9411 |  |  | #NUM! |  |  | 650.5797 |  |  | 293.1367 |  |  | 221.5872 |  |  | 179.7966 |  |  | 242.3601
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.82907 | 1052.9204 |  | 18.8397 | 5663.0229 |  | 59.6353 | 13866.6628 |  | 259.5411 | 27008.7198 |  | 18000 | 45312.23 |  | 18000 | 66134.4339 |  | 18000 | 87382.8301 |  | 18000 | 107689.8955 |  | 18000 | 125024.6255 |  | 18000 | 146601.2059
[13 empty] | Next iteration flow rate |  |  | 1073.9788 | Abs Value of | Flow this | 5719.6531 | Abs Value of | Flow this | 14005.3295 | Abs Value of | Flow this | 27278.807 | Abs Value of | Flow this | 45765.3523 | Abs Value of | Flow this | 66795.7782 | Abs Value of | Flow this | 88256.6584 | Abs Value of | Flow this | 108766.7944 | Abs Value of | Flow this | 126274.8717 | Abs Value of | Flow this | 148067.218 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1938 |  |  | 89.1972 |  |  | 84.0368 |  |  | 66.7344 |  |  | 24.0982 |  |  | -50.6456 |  |  | -155.7121 |  |  | -283.3045 |  |  | -413.2381 |  |  | -602.0088
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43507 |  |  | 0.43027 |  |  | 0.40537 |  |  | 0.32191 |  |  | 0.11624 |  |  | -0.2443 |  |  | -0.75112 |  |  | -1.3666 |  |  | -1.9934 |  |  | -2.9039
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1938 |  |  | 29.1972 |  |  | 24.0368 |  |  | 6.7344 |  |  | -35.9018 |  |  | -110.6456 |  |  | -215.7121 |  |  | -343.3045 |  |  | -473.2381 |  |  | -662.0088
[13 empty] | Press drop ratio this iteration |  |  | 0.33477 |  |  | 0.32733 |  |  | 0.28603 |  |  | 0.10091 |  |  | -1.4898 |  |  | 2.1847 |  |  | 1.3853 |  |  | 1.2118 |  |  | 1.1452 |  |  | 1.0997
[13 empty] | Expansion factor | 12 |  | 0.82565 |  |  | 0.82956 |  |  | 0.84965 |  |  | 0.94621 |  |  | 1.8188 |  |  | -0.27274 |  |  | 0.13173 |  |  | 0.15081 |  |  | 0.35359 |  |  | 0.026904
[13 empty] | C Non choked w/ reducers | 5 |  | 5.6704 |  |  | 30.7553 |  |  | 83.6804 |  |  | 312.1239 |  |  | #NUM! |  |  | -777.3042 |  |  | 899.953 |  |  | 604.0316 |  |  | 240.0824 |  |  | 3471.3457
[13 empty] | C Choked w/ reducers | 5 |  | 5.0764 |  |  | 27.3519 |  |  | 71.5896 |  |  | 177.8733 |  |  | 849.5085 |  |  | 621.0716 |  |  | 286.8539 |  |  | 217.9888 |  |  | 177.2351 |  |  | 239.2376
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.6704 |  |  | 30.7553 |  |  | 83.6804 |  |  | 312.1239 |  |  | #NUM! |  |  | 621.0716 |  |  | 286.8539 |  |  | 217.9888 |  |  | 177.2351 |  |  | 239.2376
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 0.94039 | 1073.9788 |  | 19.1553 | 5719.6531 |  | 60.6804 | 14005.3295 |  | 272.7239 | 27278.807 |  | 18000 | 45765.3523 |  | 18000 | 66795.7782 |  | 18000 | 88256.6584 |  | 18000 | 108766.7944 |  | 18000 | 126274.8717 |  | 18000 | 148067.218
[13 empty] | Next iteration flow rate |  |  | 1095.4584 | Abs Value of | Flow this | 5776.8496 | Abs Value of | Flow this | 14145.3828 | Abs Value of | Flow this | 27551.5951 | Abs Value of | Flow this | 46223.0059 | Abs Value of | Flow this | 67463.736 | Abs Value of | Flow this | 89139.2249 | Abs Value of | Flow this | 109854.4624 | Abs Value of | Flow this | 127537.6204 | Abs Value of | Flow this | 149547.8901 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1923 |  |  | 89.1765 |  |  | 83.9124 |  |  | 66.2622 |  |  | 22.7689 |  |  | -53.4772 |  |  | -160.6555 |  |  | -290.8125 |  |  | -423.3578 |  |  | -615.9228
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43507 |  |  | 0.43017 |  |  | 0.40477 |  |  | 0.31963 |  |  | 0.10983 |  |  | -0.25796 |  |  | -0.77496 |  |  | -1.4028 |  |  | -2.0422 |  |  | -2.9711
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1923 |  |  | 29.1765 |  |  | 23.9124 |  |  | 6.2622 |  |  | -37.2311 |  |  | -113.4772 |  |  | -220.6555 |  |  | -350.8125 |  |  | -483.3578 |  |  | -675.9228
[13 empty] | Press drop ratio this iteration |  |  | 0.33475 |  |  | 0.32718 |  |  | 0.28497 |  |  | 0.094506 |  |  | -1.6352 |  |  | 2.122 |  |  | 1.3735 |  |  | 1.2063 |  |  | 1.1417 |  |  | 1.0974
[13 empty] | Expansion factor | 12 |  | 0.82566 |  |  | 0.82964 |  |  | 0.85021 |  |  | 0.94962 |  |  | 1.8987 |  |  | -0.23619 |  |  | 0.13916 |  |  | 0.15464 |  |  | 0.35555 |  |  | 0.028896
[13 empty] | C Non choked w/ reducers | 5 |  | 5.7839 |  |  | 31.0745 |  |  | 84.7442 |  |  | 326.8991 |  |  | #NUM! |  |  | -871.142 |  |  | 837.5296 |  |  | 580.9077 |  |  | 235.7404 |  |  | 3193.8509
[13 empty] | C Choked w/ reducers | 5 |  | 5.178 |  |  | 27.6319 |  |  | 72.4127 |  |  | 180.9324 |  |  | 908.0941 |  |  | 594.0679 |  |  | 280.8076 |  |  | 214.4845 |  |  | 174.7286 |  |  | 236.1715
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.7839 |  |  | 31.0745 |  |  | 84.7442 |  |  | 326.8991 |  |  | #NUM! |  |  | 594.0679 |  |  | 280.8076 |  |  | 214.4845 |  |  | 174.7286 |  |  | 236.1715
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.0539 | 1095.4584 |  | 19.4745 | 5776.8496 |  | 61.7442 | 14145.3828 |  | 287.4991 | 27551.5951 |  | 18000 | 46223.0059 |  | 18000 | 67463.736 |  | 18000 | 89139.2249 |  | 18000 | 109854.4624 |  | 18000 | 127537.6204 |  | 18000 | 149547.8901
[13 empty] | Next iteration flow rate |  |  | 1117.3676 | Abs Value of | Flow this | 5834.6181 | Abs Value of | Flow this | 14286.8366 | Abs Value of | Flow this | 27827.111 | Abs Value of | Flow this | 46685.2359 | Abs Value of | Flow this | 68138.3733 | Abs Value of | Flow this | 90030.6172 | Abs Value of | Flow this | 110953.007 | Abs Value of | Flow this | 128812.9966 | Abs Value of | Flow this | 151043.369 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1908 |  |  | 89.1553 |  |  | 83.7854 |  |  | 65.7804 |  |  | 21.4129 |  |  | -56.3657 |  |  | -165.6983 |  |  | -298.4715 |  |  | -433.6809 |  |  | -630.1165
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43506 |  |  | 0.43006 |  |  | 0.40416 |  |  | 0.31731 |  |  | 0.10329 |  |  | -0.27189 |  |  | -0.79929 |  |  | -1.4398 |  |  | -2.092 |  |  | -3.0395
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1908 |  |  | 29.1553 |  |  | 23.7854 |  |  | 5.7804 |  |  | -38.5871 |  |  | -116.3657 |  |  | -225.6983 |  |  | -358.4715 |  |  | -493.6809 |  |  | -690.1165
[13 empty] | Press drop ratio this iteration |  |  | 0.33474 |  |  | 0.32702 |  |  | 0.28388 |  |  | 0.087875 |  |  | -1.802 |  |  | 2.0645 |  |  | 1.3621 |  |  | 1.201 |  |  | 1.1384 |  |  | 1.0952
[13 empty] | Expansion factor | 12 |  | 0.82566 |  |  | 0.82973 |  |  | 0.85078 |  |  | 0.95316 |  |  | 1.9904 |  |  | -0.2027 |  |  | 0.14628 |  |  | 0.15835 |  |  | 0.35745 |  |  | 0.030838
[13 empty] | C Non choked w/ reducers | 5 |  | 5.8998 |  |  | 31.3972 |  |  | 85.8273 |  |  | 343.6282 |  |  | #NUM! |  |  | -986.1608 |  |  | 783.4685 |  |  | 559.497 |  |  | 231.5344 |  |  | 2957.5465
[13 empty] | C Choked w/ reducers | 5 |  | 5.2816 |  |  | 27.9148 |  |  | 73.2477 |  |  | 184.0801 |  |  | 975.255 |  |  | 569.2605 |  |  | 274.9842 |  |  | 211.0705 |  |  | 172.2751 |  |  | 233.1601
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 5.8998 |  |  | 31.3972 |  |  | 85.8273 |  |  | 343.6282 |  |  | #NUM! |  |  | 569.2605 |  |  | 274.9842 |  |  | 211.0705 |  |  | 172.2751 |  |  | 233.1601
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.1698 | 1117.3676 |  | 19.7972 | 5834.6181 |  | 62.8273 | 14286.8366 |  | 304.2282 | 27827.111 |  | 18000 | 46685.2359 |  | 18000 | 68138.3733 |  | 18000 | 90030.6172 |  | 18000 | 110953.007 |  | 18000 | 128812.9966 |  | 18000 | 151043.369
[13 empty] | Next iteration flow rate |  |  | 1139.7149 | Abs Value of | Flow this | 5892.9643 | Abs Value of | Flow this | 14429.705 | Abs Value of | Flow this | 28105.3822 | Abs Value of | Flow this | 47152.0883 | Abs Value of | Flow this | 68819.7571 | Abs Value of | Flow this | 90930.9234 | Abs Value of | Flow this | 112062.5371 | Abs Value of | Flow this | 130101.1266 | Abs Value of | Flow this | 152553.8027 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1892 |  |  | 89.1337 |  |  | 83.6558 |  |  | 65.289 |  |  | 20.0297 |  |  | -59.3123 |  |  | -170.8425 |  |  | -306.2844 |  |  | -444.2115 |  |  | -644.5955
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43505 |  |  | 0.42996 |  |  | 0.40353 |  |  | 0.31494 |  |  | 0.096618 |  |  | -0.28611 |  |  | -0.8241 |  |  | -1.4774 |  |  | -2.1428 |  |  | -3.1094
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1892 |  |  | 29.1337 |  |  | 23.6558 |  |  | 5.289 |  |  | -39.9703 |  |  | -119.3123 |  |  | -230.8425 |  |  | -366.2844 |  |  | -504.2115 |  |  | -704.5955
[13 empty] | Press drop ratio this iteration |  |  | 0.33473 |  |  | 0.32685 |  |  | 0.28278 |  |  | 0.081009 |  |  | -1.9956 |  |  | 2.0116 |  |  | 1.3512 |  |  | 1.1959 |  |  | 1.1351 |  |  | 1.0931
[13 empty] | Expansion factor | 12 |  | 0.82567 |  |  | 0.82981 |  |  | 0.85136 |  |  | 0.95682 |  |  | 2.0967 |  |  | -0.17189 |  |  | 0.15312 |  |  | 0.16195 |  |  | 0.35931 |  |  | 0.032731
[13 empty] | C Non choked w/ reducers | 5 |  | 6.0179 |  |  | 31.7235 |  |  | 86.9303 |  |  | 362.8006 |  |  | #NUM! |  |  | -1130.7631 |  |  | 736.1761 |  |  | 539.6114 |  |  | 227.4576 |  |  | 2753.8642
[13 empty] | C Choked w/ reducers | 5 |  | 5.3874 |  |  | 28.2008 |  |  | 74.0948 |  |  | 187.3204 |  |  | 1053.031 |  |  | 546.39 |  |  | 269.3713 |  |  | 207.7432 |  |  | 169.873 |  |  | 230.2021
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.0179 |  |  | 31.7235 |  |  | 86.9303 |  |  | 362.8006 |  |  | #NUM! |  |  | 546.39 |  |  | 269.3713 |  |  | 207.7432 |  |  | 169.873 |  |  | 230.2021
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.2879 | 1139.7149 |  | 20.1235 | 5892.9643 |  | 63.9303 | 14429.705 |  | 323.4006 | 28105.3822 |  | 18000 | 47152.0883 |  | 18000 | 68819.7571 |  | 18000 | 90930.9234 |  | 18000 | 112062.5371 |  | 18000 | 130101.1266 |  | 18000 | 152553.8027
[13 empty] | Next iteration flow rate |  |  | 1162.5092 | Abs Value of | Flow this | 5951.894 | Abs Value of | Flow this | 14574.002 | Abs Value of | Flow this | 28386.436 | Abs Value of | Flow this | 47623.6092 | Abs Value of | Flow this | 69507.9546 | Abs Value of | Flow this | 91840.2326 | Abs Value of | Flow this | 113183.1624 | Abs Value of | Flow this | 131402.1379 | Abs Value of | Flow this | 154079.3408 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1875 |  |  | 89.1116 |  |  | 83.5237 |  |  | 64.7877 |  |  | 18.6187 |  |  | -62.3181 |  |  | -176.0901 |  |  | -314.2543 |  |  | -454.9538 |  |  | -659.3655
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43504 |  |  | 0.42985 |  |  | 0.4029 |  |  | 0.31252 |  |  | 0.089812 |  |  | -0.30061 |  |  | -0.84941 |  |  | -1.5159 |  |  | -2.1946 |  |  | -3.1806
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1875 |  |  | 29.1116 |  |  | 23.5237 |  |  | 4.7877 |  |  | -41.3813 |  |  | -122.3181 |  |  | -236.0901 |  |  | -374.2543 |  |  | -514.9538 |  |  | -719.3655
[13 empty] | Press drop ratio this iteration |  |  | 0.33472 |  |  | 0.32669 |  |  | 0.28164 |  |  | 0.073898 |  |  | -2.2226 |  |  | 1.9628 |  |  | 1.3407 |  |  | 1.1909 |  |  | 1.1319 |  |  | 1.091
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.8299 |  |  | 0.85196 |  |  | 0.96061 |  |  | 2.2215 |  |  | -0.14347 |  |  | 0.15968 |  |  | 0.16543 |  |  | 0.36111 |  |  | 0.034576
[13 empty] | C Non choked w/ reducers | 5 |  | 6.1385 |  |  | 32.0535 |  |  | 88.0538 |  |  | 385.097 |  |  | #NUM! |  |  | -1318.4377 |  |  | 694.4398 |  |  | 521.0897 |  |  | 223.5038 |  |  | 2576.4584
[13 empty] | C Choked w/ reducers | 5 |  | 5.4952 |  |  | 28.4898 |  |  | 74.9541 |  |  | 190.6575 |  |  | 1144.1641 |  |  | 525.2362 |  |  | 263.9574 |  |  | 204.4993 |  |  | 167.5206 |  |  | 227.2959
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.1385 |  |  | 32.0535 |  |  | 88.0538 |  |  | 385.097 |  |  | #NUM! |  |  | 525.2362 |  |  | 263.9574 |  |  | 204.4993 |  |  | 167.5206 |  |  | 227.2959
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.4085 | 1162.5092 |  | 20.4535 | 5951.894 |  | 65.0538 | 14574.002 |  | 345.697 | 28386.436 |  | 18000 | 47623.6092 |  | 18000 | 69507.9546 |  | 18000 | 91840.2326 |  | 18000 | 113183.1624 |  | 18000 | 131402.1379 |  | 18000 | 154079.3408
[13 empty] | Next iteration flow rate |  |  | 1185.7594 | Abs Value of | Flow this | 6011.4129 | Abs Value of | Flow this | 14719.742 | Abs Value of | Flow this | 28670.3003 | Abs Value of | Flow this | 48099.8452 | Abs Value of | Flow this | 70203.0342 | Abs Value of | Flow this | 92758.6349 | Abs Value of | Flow this | 114314.9941 | Abs Value of | Flow this | 132716.1593 | Abs Value of | Flow this | 155620.1342 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1858 |  |  | 89.0892 |  |  | 83.3889 |  |  | 64.2763 |  |  | 17.1793 |  |  | -65.3843 |  |  | -181.4431 |  |  | -322.3844 |  |  | -465.912 |  |  | -674.4323
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43503 |  |  | 0.42974 |  |  | 0.40225 |  |  | 0.31005 |  |  | 0.082869 |  |  | -0.3154 |  |  | -0.87524 |  |  | -1.5551 |  |  | -2.2474 |  |  | -3.2533
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1858 |  |  | 29.0892 |  |  | 23.3889 |  |  | 4.2763 |  |  | -42.8207 |  |  | -125.3843 |  |  | -241.4431 |  |  | -382.3844 |  |  | -525.912 |  |  | -734.4323
[13 empty] | Press drop ratio this iteration |  |  | 0.33471 |  |  | 0.32652 |  |  | 0.28048 |  |  | 0.06653 |  |  | -2.4926 |  |  | 1.9177 |  |  | 1.3307 |  |  | 1.1861 |  |  | 1.1288 |  |  | 1.089
[13 empty] | Expansion factor | 12 |  | 0.82568 |  |  | 0.82999 |  |  | 0.85257 |  |  | 0.96454 |  |  | 2.3699 |  |  | -0.11716 |  |  | 0.16598 |  |  | 0.1688 |  |  | 0.36286 |  |  | 0.036375
[13 empty] | C Non choked w/ reducers | 5 |  | 6.2614 |  |  | 32.3872 |  |  | 89.1984 |  |  | 411.4997 |  |  | #NUM! |  |  | -1572.3003 |  |  | 657.321 |  |  | 503.7925 |  |  | 219.6671 |  |  | 2420.5295
[13 empty] | C Choked w/ reducers | 5 |  | 5.6052 |  |  | 28.782 |  |  | 75.826 |  |  | 194.0962 |  |  | 1252.4299 |  |  | 505.6111 |  |  | 258.7317 |  |  | 201.3355 |  |  | 165.2164 |  |  | 224.4403
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.2614 |  |  | 32.3872 |  |  | 89.1984 |  |  | 411.4997 |  |  | #NUM! |  |  | 505.6111 |  |  | 258.7317 |  |  | 201.3355 |  |  | 165.2164 |  |  | 224.4403
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.5314 | 1185.7594 |  | 20.7872 | 6011.4129 |  | 66.1984 | 14719.742 |  | 372.0997 | 28670.3003 |  | 18000 | 48099.8452 |  | 18000 | 70203.0342 |  | 18000 | 92758.6349 |  | 18000 | 114314.9941 |  | 18000 | 132716.1593 |  | 18000 | 155620.1342
[13 empty] | Next iteration flow rate |  |  | 1209.4746 | Abs Value of | Flow this | 6071.527 | Abs Value of | Flow this | 14866.9395 | Abs Value of | Flow this | 28957.0033 | Abs Value of | Flow this | 48580.8437 | Abs Value of | Flow this | 70905.0645 | Abs Value of | Flow this | 93686.2213 | Abs Value of | Flow this | 115458.144 | Abs Value of | Flow this | 134043.3208 | Abs Value of | Flow this | 157176.3355 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.184 |  |  | 89.0662 |  |  | 83.2514 |  |  | 63.7546 |  |  | 15.711 |  |  | -68.5121 |  |  | -186.9037 |  |  | -330.678 |  |  | -477.0905 |  |  | -689.802
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43503 |  |  | 0.42963 |  |  | 0.40158 |  |  | 0.30754 |  |  | 0.075786 |  |  | -0.33049 |  |  | -0.90158 |  |  | -1.5951 |  |  | -2.3014 |  |  | -3.3274
[13 empty] | Delta P at this iteration flow rate |  |  | 30.184 |  |  | 29.0662 |  |  | 23.2514 |  |  | 3.7546 |  |  | -44.289 |  |  | -128.5121 |  |  | -246.9037 |  |  | -390.678 |  |  | -537.0905 |  |  | -749.802
[13 empty] | Press drop ratio this iteration |  |  | 0.33469 |  |  | 0.32634 |  |  | 0.27929 |  |  | 0.058891 |  |  | -2.819 |  |  | 1.8758 |  |  | 1.321 |  |  | 1.1814 |  |  | 1.1258 |  |  | 1.087
[13 empty] | Expansion factor | 12 |  | 0.82569 |  |  | 0.83008 |  |  | 0.85319 |  |  | 0.96861 |  |  | 2.5493 |  |  | -0.092756 |  |  | 0.17203 |  |  | 0.17207 |  |  | 0.36456 |  |  | 0.038129
[13 empty] | C Non choked w/ reducers | 5 |  | 6.3869 |  |  | 32.7246 |  |  | 90.3648 |  |  | 443.4881 |  |  | #NUM! |  |  | -1935.5542 |  |  | 624.0818 |  |  | 487.5991 |  |  | 215.942 |  |  | 2282.3798
[13 empty] | C Choked w/ reducers | 5 |  | 5.7174 |  |  | 29.0773 |  |  | 76.7108 |  |  | 197.6412 |  |  | 1383.175 |  |  | 487.3532 |  |  | 253.6842 |  |  | 198.2488 |  |  | 162.9587 |  |  | 221.6339
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.3869 |  |  | 32.7246 |  |  | 90.3648 |  |  | 443.4881 |  |  | #NUM! |  |  | 487.3532 |  |  | 253.6842 |  |  | 198.2488 |  |  | 162.9587 |  |  | 221.6339
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.6569 | 1209.4746 |  | 21.1246 | 6071.527 |  | 67.3648 | 14866.9395 |  | 404.0881 | 28957.0033 |  | 18000 | 48580.8437 |  | 18000 | 70905.0645 |  | 18000 | 93686.2213 |  | 18000 | 115458.144 |  | 18000 | 134043.3208 |  | 18000 | 157176.3355
[13 empty] | Next iteration flow rate |  |  | 1233.6641 | Abs Value of | Flow this | 6132.2423 | Abs Value of | Flow this | 15015.6088 | Abs Value of | Flow this | 29246.5734 | Abs Value of | Flow this | 49066.6521 | Abs Value of | Flow this | 71614.1152 | Abs Value of | Flow this | 94623.0835 | Abs Value of | Flow this | 116612.7255 | Abs Value of | Flow this | 135383.7541 | Abs Value of | Flow this | 158748.0989 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1821 |  |  | 89.0428 |  |  | 83.1111 |  |  | 63.2224 |  |  | 14.2131 |  |  | -71.7029 |  |  | -192.4741 |  |  | -339.1383 |  |  | -488.4936 |  |  | -705.4807
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43502 |  |  | 0.42952 |  |  | 0.40091 |  |  | 0.30497 |  |  | 0.068561 |  |  | -0.34588 |  |  | -0.92845 |  |  | -1.6359 |  |  | -2.3564 |  |  | -3.4031
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1821 |  |  | 29.0428 |  |  | 23.1111 |  |  | 3.2224 |  |  | -45.7869 |  |  | -131.7029 |  |  | -252.4741 |  |  | -399.1383 |  |  | -548.4936 |  |  | -765.4807
[13 empty] | Press drop ratio this iteration |  |  | 0.33468 |  |  | 0.32617 |  |  | 0.27807 |  |  | 0.05097 |  |  | -3.2215 |  |  | 1.8368 |  |  | 1.3117 |  |  | 1.1769 |  |  | 1.1228 |  |  | 1.085
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.83017 |  |  | 0.85383 |  |  | 0.97283 |  |  | 2.7705 |  |  | -0.070053 |  |  | 0.17786 |  |  | 0.17525 |  |  | 0.36622 |  |  | 0.03984
[13 empty] | C Non choked w/ reducers | 5 |  | 6.5148 |  |  | 33.0658 |  |  | 91.5536 |  |  | 483.4189 |  |  | #NUM! |  |  | -2499.3768 |  |  | 594.1337 |  |  | 472.404 |  |  | 212.3233 |  |  | 2159.1148
[13 empty] | C Choked w/ reducers | 5 |  | 5.8319 |  |  | 29.3758 |  |  | 77.6087 |  |  | 201.2978 |  |  | 1544.229 |  |  | 470.323 |  |  | 248.8058 |  |  | 195.2363 |  |  | 160.7462 |  |  | 218.8753
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.5148 |  |  | 33.0658 |  |  | 91.5536 |  |  | 483.4189 |  |  | #NUM! |  |  | 470.323 |  |  | 248.8058 |  |  | 195.2363 |  |  | 160.7462 |  |  | 218.8753
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.7848 | 1233.6641 |  | 21.4658 | 6132.2423 |  | 68.5536 | 15015.6088 |  | 444.0189 | 29246.5734 |  | 18000 | 49066.6521 |  | 18000 | 71614.1152 |  | 18000 | 94623.0835 |  | 18000 | 116612.7255 |  | 18000 | 135383.7541 |  | 18000 | 158748.0989
[13 empty] | Next iteration flow rate |  |  | 1258.3373 | Abs Value of | Flow this | 6193.5647 | Abs Value of | Flow this | 15165.7649 | Abs Value of | Flow this | 29539.0391 | Abs Value of | Flow this | 49557.3187 | Abs Value of | Flow this | 72330.2563 | Abs Value of | Flow this | 95569.3143 | Abs Value of | Flow this | 117778.8527 | Abs Value of | Flow this | 136737.5916 | Abs Value of | Flow this | 160335.5799 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1802 |  |  | 89.019 |  |  | 82.968 |  |  | 62.6796 |  |  | 12.6852 |  |  | -74.9577 |  |  | -198.1565 |  |  | -347.7686 |  |  | -500.1259 |  |  | -721.4745
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43501 |  |  | 0.42941 |  |  | 0.40022 |  |  | 0.30235 |  |  | 0.06119 |  |  | -0.36158 |  |  | -0.95586 |  |  | -1.6775 |  |  | -2.4125 |  |  | -3.4802
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1802 |  |  | 29.019 |  |  | 22.968 |  |  | 2.6796 |  |  | -47.3148 |  |  | -134.9577 |  |  | -258.1565 |  |  | -407.7686 |  |  | -560.1259 |  |  | -781.4745
[13 empty] | Press drop ratio this iteration |  |  | 0.33467 |  |  | 0.32599 |  |  | 0.27683 |  |  | 0.042751 |  |  | -3.7299 |  |  | 1.8005 |  |  | 1.3028 |  |  | 1.1725 |  |  | 1.12 |  |  | 1.0832
[13 empty] | Expansion factor | 12 |  | 0.8257 |  |  | 0.83026 |  |  | 0.85449 |  |  | 0.97721 |  |  | 3.0499 |  |  | -0.048885 |  |  | 0.18346 |  |  | 0.17832 |  |  | 0.36783 |  |  | 0.041508
[13 empty] | C Non choked w/ reducers | 5 |  | 6.6453 |  |  | 33.4109 |  |  | 92.7656 |  |  | 535.3338 |  |  | #NUM! |  |  | -3495.115 |  |  | 567.0019 |  |  | 458.1149 |  |  | 208.8063 |  |  | 2048.436
[13 empty] | C Choked w/ reducers | 5 |  | 5.9487 |  |  | 29.6775 |  |  | 78.5199 |  |  | 205.0717 |  |  | 1747.5354 |  |  | 454.3994 |  |  | 244.0877 |  |  | 192.2951 |  |  | 158.5776 |  |  | 216.1635
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.6453 |  |  | 33.4109 |  |  | 92.7656 |  |  | 535.3338 |  |  | #NUM! |  |  | 454.3994 |  |  | 244.0877 |  |  | 192.2951 |  |  | 158.5776 |  |  | 216.1635
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 1.9153 | 1258.3373 |  | 21.8109 | 6193.5647 |  | 69.7656 | 15165.7649 |  | 495.9338 | 29539.0391 |  | 18000 | 49557.3187 |  | 18000 | 72330.2563 |  | 18000 | 95569.3143 |  | 18000 | 117778.8527 |  | 18000 | 136737.5916 |  | 18000 | 160335.5799
[13 empty] | Next iteration flow rate |  |  | 1283.5041 | Abs Value of | Flow this | 6255.5004 | Abs Value of | Flow this | 15317.4226 | Abs Value of | Flow this | 29834.4295 | Abs Value of | Flow this | 50052.8918 | Abs Value of | Flow this | 73053.5589 | Abs Value of | Flow this | 96525.0075 | Abs Value of | Flow this | 118956.6412 | Abs Value of | Flow this | 138104.9675 | Abs Value of | Flow this | 161938.9357 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1782 |  |  | 88.9946 |  |  | 82.822 |  |  | 62.1258 |  |  | 11.1265 |  |  | -78.278 |  |  | -203.9531 |  |  | -356.5723 |  |  | -511.9921 |  |  | -737.7897
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.435 |  |  | 0.42929 |  |  | 0.39951 |  |  | 0.29968 |  |  | 0.053672 |  |  | -0.37759 |  |  | -0.98382 |  |  | -1.72 |  |  | -2.4697 |  |  | -3.5589
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1782 |  |  | 28.9946 |  |  | 22.822 |  |  | 2.1258 |  |  | -48.8735 |  |  | -138.278 |  |  | -263.9531 |  |  | -416.5723 |  |  | -571.9921 |  |  | -797.7897
[13 empty] | Press drop ratio this iteration |  |  | 0.33465 |  |  | 0.3258 |  |  | 0.27556 |  |  | 0.034218 |  |  | -4.3925 |  |  | 1.7665 |  |  | 1.2942 |  |  | 1.1683 |  |  | 1.1172 |  |  | 1.0813
[13 empty] | Expansion factor | 12 |  | 0.82571 |  |  | 0.83036 |  |  | 0.85516 |  |  | 0.98176 |  |  | 3.4141 |  |  | -0.029106 |  |  | 0.18885 |  |  | 0.18131 |  |  | 0.3694 |  |  | 0.043135
[13 empty] | C Non choked w/ reducers | 5 |  | 6.7785 |  |  | 33.7599 |  |  | 94.0015 |  |  | 606.9139 |  |  | #NUM! |  |  | -5731.8296 |  |  | 542.2991 |  |  | 444.6507 |  |  | 205.3865 |  |  | 1948.4953
[13 empty] | C Choked w/ reducers | 5 |  | 6.0678 |  |  | 29.9825 |  |  | 79.4449 |  |  | 208.9686 |  |  | 2012.2617 |  |  | 439.4767 |  |  | 239.522 |  |  | 189.4228 |  |  | 156.4513 |  |  | 213.4972
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.7785 |  |  | 33.7599 |  |  | 94.0015 |  |  | 606.9139 |  |  | #NUM! |  |  | 439.4767 |  |  | 239.522 |  |  | 189.4228 |  |  | 156.4513 |  |  | 213.4972
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.0485 | 1283.5041 |  | 22.1599 | 6255.5004 |  | 71.0015 | 15317.4226 |  | 567.5139 | 29834.4295 |  | 18000 | 50052.8918 |  | 18000 | 73053.5589 |  | 18000 | 96525.0075 |  | 18000 | 118956.6412 |  | 18000 | 138104.9675 |  | 18000 | 161938.9357
[13 empty] | Next iteration flow rate |  |  | 1309.1742 | Abs Value of | Flow this | 6318.0554 | Abs Value of | Flow this | 15470.5968 | Abs Value of | Flow this | 30132.7738 | Abs Value of | Flow this | 50553.4208 | Abs Value of | Flow this | 73784.0945 | Abs Value of | Flow this | 97490.2575 | Abs Value of | Flow this | 120146.2076 | Abs Value of | Flow this | 139486.0172 | Abs Value of | Flow this | 163558.325 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1761 |  |  | 88.9698 |  |  | 82.6731 |  |  | 61.5609 |  |  | 9.5365 |  |  | -81.665 |  |  | -209.8661 |  |  | -365.5531 |  |  | -524.0968 |  |  | -754.4329
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43499 |  |  | 0.42917 |  |  | 0.39879 |  |  | 0.29695 |  |  | 0.046002 |  |  | -0.39393 |  |  | -1.0123 |  |  | -1.7633 |  |  | -2.5281 |  |  | -3.6392
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1761 |  |  | 28.9698 |  |  | 22.6731 |  |  | 1.5609 |  |  | -50.4635 |  |  | -141.665 |  |  | -269.8661 |  |  | -425.5531 |  |  | -584.0968 |  |  | -814.4329
[13 empty] | Press drop ratio this iteration |  |  | 0.33463 |  |  | 0.32561 |  |  | 0.27425 |  |  | 0.025356 |  |  | -5.2916 |  |  | 1.7347 |  |  | 1.2859 |  |  | 1.1641 |  |  | 1.1145 |  |  | 1.0795
[13 empty] | Expansion factor | 12 |  | 0.82572 |  |  | 0.83046 |  |  | 0.85584 |  |  | 0.98648 |  |  | 3.9082 |  |  | -0.010586 |  |  | 0.19405 |  |  | 0.18421 |  |  | 0.37093 |  |  | 0.044723
[13 empty] | C Non choked w/ reducers | 5 |  | 6.9143 |  |  | 34.1129 |  |  | 95.2621 |  |  | 715.1874 |  |  | #NUM! |  |  | -15396.3395 |  |  | 519.7059 |  |  | 431.9396 |  |  | 202.0595 |  |  | 1857.7897
[13 empty] | C Choked w/ reducers | 5 |  | 6.1893 |  |  | 30.2908 |  |  | 80.3839 |  |  | 212.995 |  |  | 2371.2345 |  |  | 425.4621 |  |  | 235.101 |  |  | 186.6169 |  |  | 154.3663 |  |  | 210.8752
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 6.9143 |  |  | 34.1129 |  |  | 95.2621 |  |  | 715.1874 |  |  | #NUM! |  |  | 425.4621 |  |  | 235.101 |  |  | 186.6169 |  |  | 154.3663 |  |  | 210.8752
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.1843 | 1309.1742 |  | 22.5129 | 6318.0554 |  | 72.2621 | 15470.5968 |  | 675.7874 | 30132.7738 |  | 18000 | 50553.4208 |  | 18000 | 73784.0945 |  | 18000 | 97490.2575 |  | 18000 | 120146.2076 |  | 18000 | 139486.0172 |  | 18000 | 163558.325
[13 empty] | Next iteration flow rate |  |  | 1335.3577 | Abs Value of | Flow this | 6381.2359 | Abs Value of | Flow this | 15625.3028 | Abs Value of | Flow this | 30434.1015 | Abs Value of | Flow this | 51058.955 | Abs Value of | Flow this | 74521.9354 | Abs Value of | Flow this | 98465.1601 | Abs Value of | Flow this | 121347.6697 | Abs Value of | Flow this | 140880.8774 | Abs Value of | Flow this | 165193.9083 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1739 |  |  | 88.9445 |  |  | 82.5212 |  |  | 60.9847 |  |  | 7.9146 |  |  | -85.1201 |  |  | -215.8981 |  |  | -374.7143 |  |  | -536.4447 |  |  | -771.4107
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43498 |  |  | 0.42905 |  |  | 0.39806 |  |  | 0.29417 |  |  | 0.038178 |  |  | -0.4106 |  |  | -1.0414 |  |  | -1.8075 |  |  | -2.5877 |  |  | -3.7211
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1739 |  |  | 28.9445 |  |  | 22.5212 |  |  | 0.98467 |  |  | -52.0854 |  |  | -145.1201 |  |  | -275.8981 |  |  | -434.7143 |  |  | -596.4447 |  |  | -831.4107
[13 empty] | Press drop ratio this iteration |  |  | 0.33462 |  |  | 0.32542 |  |  | 0.27291 |  |  | 0.016146 |  |  | -6.5809 |  |  | 1.7049 |  |  | 1.2779 |  |  | 1.1601 |  |  | 1.1118 |  |  | 1.0778
[13 empty] | Expansion factor | 12 |  | 0.82573 |  |  | 0.83056 |  |  | 0.85654 |  |  | 0.99139 |  |  | 4.6168 |  |  | 0.0067878 |  |  | 0.19905 |  |  | 0.18702 |  |  | 0.37241 |  |  | 0.046272
[13 empty] | C Non choked w/ reducers | 5 |  | 7.0529 |  |  | 34.4698 |  |  | 96.5483 |  |  | 909.2281 |  |  | #NUM! |  |  | 23469.2707 |  |  | 498.9571 |  |  | 419.9179 |  |  | 198.8214 |  |  | 1775.0843
[13 empty] | C Choked w/ reducers | 5 |  | 6.3132 |  |  | 30.6024 |  |  | 81.3372 |  |  | 217.1577 |  |  | 2885.7446 |  |  | 412.2742 |  |  | 230.8179 |  |  | 183.8749 |  |  | 152.3212 |  |  | 208.2964
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.0529 |  |  | 34.4698 |  |  | 96.5483 |  |  | 909.2281 |  |  | #NUM! |  |  | 412.2742 |  |  | 230.8179 |  |  | 183.8749 |  |  | 152.3212 |  |  | 208.2964
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.3229 | 1335.3577 |  | 22.8698 | 6381.2359 |  | 73.5483 | 15625.3028 |  | 869.8281 | 30434.1015 |  | 18000 | 51058.955 |  | 18000 | 74521.9354 |  | 18000 | 98465.1601 |  | 18000 | 121347.6697 |  | 18000 | 140880.8774 |  | 18000 | 165193.9083
[13 empty] | Next iteration flow rate |  |  | 1362.0648 | Abs Value of | Flow this | 6445.0483 | Abs Value of | Flow this | 15781.5558 | Abs Value of | Flow this | 30738.4425 | Abs Value of | Flow this | 51569.5445 | Abs Value of | Flow this | 75267.1548 | Abs Value of | Flow this | 99449.8117 | Abs Value of | Flow this | 122561.1464 | Abs Value of | Flow this | 142289.6861 | Abs Value of | Flow this | 166845.8473 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1716 |  |  | 88.9186 |  |  | 82.3663 |  |  | 60.3968 |  |  | 6.2601 |  |  | -88.6446 |  |  | -222.0512 |  |  | -384.0597 |  |  | -549.0409 |  |  | -788.7297
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43497 |  |  | 0.42892 |  |  | 0.39731 |  |  | 0.29134 |  |  | 0.030197 |  |  | -0.4276 |  |  | -1.0711 |  |  | -1.8526 |  |  | -2.6484 |  |  | -3.8046
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1716 |  |  | 28.9186 |  |  | 22.3663 |  |  | 0.39683 |  |  | -53.7399 |  |  | -148.6446 |  |  | -282.0512 |  |  | -444.0597 |  |  | -609.0409 |  |  | -848.7297
[13 empty] | Press drop ratio this iteration |  |  | 0.3346 |  |  | 0.32523 |  |  | 0.27155 |  |  | 0.0065705 |  |  | -8.5846 |  |  | 1.6769 |  |  | 1.2702 |  |  | 1.1562 |  |  | 1.1093 |  |  | 1.0761
[13 empty] | Expansion factor | 12 |  | 0.82574 |  |  | 0.83066 |  |  | 0.85726 |  |  | 0.9965 |  |  | 5.718 |  |  | 0.023115 |  |  | 0.20388 |  |  | 0.18975 |  |  | 0.37386 |  |  | 0.047783
[13 empty] | C Non choked w/ reducers | 5 |  | 7.1942 |  |  | 34.8308 |  |  | 97.8608 |  |  | 1446.1308 |  |  | #NUM! |  |  | 6739.5894 |  |  | 479.83 |  |  | 408.5292 |  |  | 195.6684 |  |  | 1699.3551
[13 empty] | C Choked w/ reducers | 5 |  | 6.4397 |  |  | 30.9174 |  |  | 82.3051 |  |  | 221.464 |  |  | 3684.9369 |  |  | 399.8408 |  |  | 226.666 |  |  | 181.1947 |  |  | 150.3148 |  |  | 205.7599
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.1942 |  |  | 34.8308 |  |  | 97.8608 |  |  | 1446.1308 |  |  | #NUM! |  |  | 399.8408 |  |  | 226.666 |  |  | 181.1947 |  |  | 150.3148 |  |  | 205.7599
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.4642 | 1362.0648 |  | 23.2308 | 6445.0483 |  | 74.8608 | 15781.5558 |  | 1406.7308 | 30738.4425 |  | 18000 | 51569.5445 |  | 18000 | 75267.1548 |  | 18000 | 99449.8117 |  | 18000 | 122561.1464 |  | 18000 | 142289.6861 |  | 18000 | 166845.8473
[13 empty] | Next iteration flow rate |  |  | 1389.3061 | Abs Value of | Flow this | 6509.4988 | Abs Value of | Flow this | 15939.3714 | Abs Value of | Flow this | 31045.827 | Abs Value of | Flow this | 52085.24 | Abs Value of | Flow this | 76019.8263 | Abs Value of | Flow this | 100444.3098 | Abs Value of | Flow this | 123786.7579 | Abs Value of | Flow this | 143712.583 | Abs Value of | Flow this | 168514.3058 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1692 |  |  | 88.8922 |  |  | 82.2082 |  |  | 59.7972 |  |  | 4.5723 |  |  | -92.24 |  |  | -228.3281 |  |  | -393.5929 |  |  | -561.8903 |  |  | -806.3967
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43495 |  |  | 0.42879 |  |  | 0.39655 |  |  | 0.28845 |  |  | 0.022055 |  |  | -0.44494 |  |  | -1.1014 |  |  | -1.8986 |  |  | -2.7104 |  |  | -3.8899
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1692 |  |  | 28.8922 |  |  | 22.2082 |  |  | -0.20282 |  |  | -55.4277 |  |  | -152.24 |  |  | -288.3281 |  |  | -453.5929 |  |  | -621.8903 |  |  | -866.3967
[13 empty] | Press drop ratio this iteration |  |  | 0.33458 |  |  | 0.32503 |  |  | 0.27015 |  |  | -0.0033917 |  |  | -12.1226 |  |  | 1.6505 |  |  | 1.2628 |  |  | 1.1524 |  |  | 1.1068 |  |  | 1.0744
[13 empty] | Expansion factor | 12 |  | 0.82575 |  |  | 0.83076 |  |  | 0.858 |  |  | 1.0018 |  |  | 7.6625 |  |  | 0.038485 |  |  | 0.20854 |  |  | 0.1924 |  |  | 0.37527 |  |  | 0.049258
[13 empty] | C Non choked w/ reducers | 5 |  | 7.3384 |  |  | 35.196 |  |  | 99.2006 |  |  | #NUM! |  |  | #NUM! |  |  | 3960.3755 |  |  | 462.1367 |  |  | 397.7229 |  |  | 192.597 |  |  | 1629.7458
[13 empty] | C Choked w/ reducers | 5 |  | 6.5686 |  |  | 31.2358 |  |  | 83.288 |  |  | 225.9217 |  |  | 5095.6453 |  |  | 388.0982 |  |  | 222.6392 |  |  | 178.574 |  |  | 148.3462 |  |  | 203.2644
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.3384 |  |  | 35.196 |  |  | 99.2006 |  |  | #NUM! |  |  | #NUM! |  |  | 388.0982 |  |  | 222.6392 |  |  | 178.574 |  |  | 148.3462 |  |  | 203.2644
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.6084 | 1389.3061 |  | 23.596 | 6509.4988 |  | 76.2006 | 15939.3714 |  | 18000 | 31045.827 |  | 18000 | 52085.24 |  | 18000 | 76019.8263 |  | 18000 | 100444.3098 |  | 18000 | 123786.7579 |  | 18000 | 143712.583 |  | 18000 | 168514.3058
[13 empty] | Next iteration flow rate |  |  | 1417.0922 | Abs Value of | Flow this | 6574.5937 | Abs Value of | Flow this | 16098.7651 | Abs Value of | Flow this | 31356.2852 | Abs Value of | Flow this | 52606.0924 | Abs Value of | Flow this | 76780.0246 | Abs Value of | Flow this | 101448.7529 | Abs Value of | Flow this | 125024.6255 | Abs Value of | Flow this | 145149.7088 | Abs Value of | Flow this | 170199.4489 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1668 |  |  | 88.8654 |  |  | 82.047 |  |  | 59.1855 |  |  | 2.8505 |  |  | -95.9077 |  |  | -234.7311 |  |  | -403.3178 |  |  | -574.9979 |  |  | -824.4189
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43494 |  |  | 0.42866 |  |  | 0.39577 |  |  | 0.2855 |  |  | 0.01375 |  |  | -0.46263 |  |  | -1.1323 |  |  | -1.9455 |  |  | -2.7736 |  |  | -3.9768
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1668 |  |  | 28.8654 |  |  | 22.047 |  |  | -0.81452 |  |  | -57.1495 |  |  | -155.9077 |  |  | -294.7311 |  |  | -463.3178 |  |  | -634.9979 |  |  | -884.4189
[13 empty] | Press drop ratio this iteration |  |  | 0.33457 |  |  | 0.32482 |  |  | 0.26871 |  |  | -0.013762 |  |  | -20.0487 |  |  | 1.6256 |  |  | 1.2556 |  |  | 1.1488 |  |  | 1.1043 |  |  | 1.0728
[13 empty] | Expansion factor | 12 |  | 0.82575 |  |  | 0.83087 |  |  | 0.85875 |  |  | 1.0073 |  |  | 12.0186 |  |  | 0.052977 |  |  | 0.21303 |  |  | 0.19498 |  |  | 0.37665 |  |  | 0.050697
[13 empty] | C Non choked w/ reducers | 5 |  | 7.4855 |  |  | 35.5653 |  |  | 100.5687 |  |  | #NUM! |  |  | #NUM! |  |  | 2815.9828 |  |  | 445.7173 |  |  | 387.4538 |  |  | 189.6038 |  |  | 1565.535
[13 empty] | C Choked w/ reducers | 5 |  | 6.7002 |  |  | 31.5577 |  |  | 84.2862 |  |  | 230.5392 |  |  | 8255.1599 |  |  | 376.9893 |  |  | 218.7317 |  |  | 176.0109 |  |  | 146.4142 |  |  | 200.8092
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.4855 |  |  | 35.5653 |  |  | 100.5687 |  |  | #NUM! |  |  | #NUM! |  |  | 376.9893 |  |  | 218.7317 |  |  | 176.0109 |  |  | 146.4142 |  |  | 200.8092
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.7555 | 1417.0922 |  | 23.9653 | 6574.5937 |  | 77.5687 | 16098.7651 |  | 18000 | 31356.2852 |  | 18000 | 52606.0924 |  | 18000 | 76780.0246 |  | 18000 | 101448.7529 |  | 18000 | 125024.6255 |  | 18000 | 145149.7088 |  | 18000 | 170199.4489
[13 empty] | Next iteration flow rate |  |  | 1445.4341 | Abs Value of | Flow this | 6640.3397 | Abs Value of | Flow this | 16259.7527 | Abs Value of | Flow this | 31669.8481 | Abs Value of | Flow this | 53132.1533 | Abs Value of | Flow this | 77547.8248 | Abs Value of | Flow this | 102463.2405 | Abs Value of | Flow this | 126274.8717 | Abs Value of | Flow this | 146601.2059 | Abs Value of | Flow this | 171901.4434 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1642 |  |  | 88.8379 |  |  | 81.8825 |  |  | 58.5615 |  |  | 1.0942 |  |  | -99.6491 |  |  | -241.2628 |  |  | -413.2381 |  |  | -588.369 |  |  | -842.8034
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43493 |  |  | 0.42853 |  |  | 0.39498 |  |  | 0.28249 |  |  | 0.0052781 |  |  | -0.48068 |  |  | -1.1638 |  |  | -1.9934 |  |  | -2.8381 |  |  | -4.0655
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1642 |  |  | 28.8379 |  |  | 21.8825 |  |  | -1.4385 |  |  | -58.9058 |  |  | -159.6491 |  |  | -301.2628 |  |  | -473.2381 |  |  | -648.369 |  |  | -902.8034
[13 empty] | Press drop ratio this iteration |  |  | 0.33455 |  |  | 0.32461 |  |  | 0.26724 |  |  | -0.024564 |  |  | -53.8348 |  |  | 1.6021 |  |  | 1.2487 |  |  | 1.1452 |  |  | 1.102 |  |  | 1.0712
[13 empty] | Expansion factor | 12 |  | 0.82576 |  |  | 0.83098 |  |  | 0.85952 |  |  | 1.0131 |  |  | 30.587 |  |  | 0.06666 |  |  | 0.21737 |  |  | 0.19748 |  |  | 0.37799 |  |  | 0.052102
[13 empty] | C Non choked w/ reducers | 5 |  | 7.6355 |  |  | 35.9389 |  |  | 101.9661 |  |  | #NUM! |  |  | #NUM! |  |  | 2191.3368 |  |  | 430.4351 |  |  | 377.6812 |  |  | 186.6857 |  |  | 1506.1103
[13 empty] | C Choked w/ reducers | 5 |  | 6.8344 |  |  | 31.8831 |  |  | 85.3 |  |  | 235.3257 |  |  | 21720.852 |  |  | 366.4634 |  |  | 214.9381 |  |  | 173.5034 |  |  | 144.5177 |  |  | 198.3931
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.6355 |  |  | 35.9389 |  |  | 101.9661 |  |  | #NUM! |  |  | #NUM! |  |  | 366.4634 |  |  | 214.9381 |  |  | 173.5034 |  |  | 144.5177 |  |  | 198.3931
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 2.9055 | 1445.4341 |  | 24.3389 | 6640.3397 |  | 78.9661 | 16259.7527 |  | 18000 | 31669.8481 |  | 18000 | 53132.1533 |  | 18000 | 77547.8248 |  | 18000 | 102463.2405 |  | 18000 | 126274.8717 |  | 18000 | 146601.2059 |  | 18000 | 171901.4434
[13 empty] | Next iteration flow rate |  |  | 1474.3428 | Abs Value of | Flow this | 6706.7431 | Abs Value of | Flow this | 16422.3503 | Abs Value of | Flow this | 31986.5466 | Abs Value of | Flow this | 53663.4748 | Abs Value of | Flow this | 78323.3031 | Abs Value of | Flow this | 103487.8729 | Abs Value of | Flow this | 127537.6204 | Abs Value of | Flow this | 148067.218 | Abs Value of | Flow this | 173620.4578 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1615 |  |  | 88.8099 |  |  | 81.7147 |  |  | 57.9249 |  |  | -0.69744 |  |  | -103.4656 |  |  | -247.9259 |  |  | -423.3578 |  |  | -602.0088 |  |  | -861.5574
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43492 |  |  | 0.4284 |  |  | 0.39417 |  |  | 0.27942 |  |  | -0.0033643 |  |  | -0.49909 |  |  | -1.1959 |  |  | -2.0422 |  |  | -2.9039 |  |  | -4.1559
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1615 |  |  | 28.8099 |  |  | 21.7147 |  |  | -2.0751 |  |  | -60.6974 |  |  | -163.4656 |  |  | -307.9259 |  |  | -483.3578 |  |  | -662.0088 |  |  | -921.5574
[13 empty] | Press drop ratio this iteration |  |  | 0.33453 |  |  | 0.3244 |  |  | 0.26574 |  |  | -0.035823 |  |  | 87.0293 |  |  | 1.5799 |  |  | 1.242 |  |  | 1.1417 |  |  | 1.0997 |  |  | 1.0696
[13 empty] | Expansion factor | 12 |  | 0.82577 |  |  | 0.83109 |  |  | 0.86032 |  |  | 1.0191 |  |  | -46.8303 |  |  | 0.079599 |  |  | 0.22155 |  |  | 0.19991 |  |  | 0.37929 |  |  | 0.053473
[13 empty] | C Non choked w/ reducers | 5 |  | 7.7886 |  |  | 36.3168 |  |  | 103.3938 |  |  | #NUM! |  |  | -40.9237 |  |  | 1797.6151 |  |  | 416.1722 |  |  | 368.3685 |  |  | 183.8397 |  |  | 1450.9488
[13 empty] | C Choked w/ reducers | 5 |  | 6.9713 |  |  | 32.2121 |  |  | 86.3299 |  |  | 240.2908 |  |  | 34418.2194 |  |  | 356.475 |  |  | 211.2532 |  |  | 171.0496 |  |  | 142.6557 |  |  | 196.0154
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.7886 |  |  | 36.3168 |  |  | 103.3938 |  |  | #NUM! |  |  | 34418.2194 |  |  | 356.475 |  |  | 211.2532 |  |  | 171.0496 |  |  | 142.6557 |  |  | 196.0154
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.0586 | 1474.3428 |  | 24.7168 | 6706.7431 |  | 80.3938 | 16422.3503 |  | 18000 | 31986.5466 |  | 18000 | 53663.4748 |  | 18000 | 78323.3031 |  | 18000 | 103487.8729 |  | 18000 | 127537.6204 |  | 18000 | 148067.218 |  | 18000 | 173620.4578
[13 empty] | Next iteration flow rate |  |  | 1503.8296 | Abs Value of | Flow this | 6773.8105 | Abs Value of | Flow this | 16586.5738 | Abs Value of | Flow this | 32306.412 | Abs Value of | Flow this | 54200.1096 | Abs Value of | Flow this | 79106.5361 | Abs Value of | Flow this | 104522.7516 | Abs Value of | Flow this | 128812.9966 | Abs Value of | Flow this | 149547.8901 | Abs Value of | Flow this | 175356.6624 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1588 |  |  | 88.7814 |  |  | 81.5435 |  |  | 57.2756 |  |  | -2.5251 |  |  | -107.3589 |  |  | -254.7228 |  |  | -433.6809 |  |  | -615.9228 |  |  | -880.6883
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4349 |  |  | 0.42826 |  |  | 0.39335 |  |  | 0.27628 |  |  | -0.01218 |  |  | -0.51787 |  |  | -1.2287 |  |  | -2.092 |  |  | -2.9711 |  |  | -4.2482
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1588 |  |  | 28.7814 |  |  | 21.5435 |  |  | -2.7244 |  |  | -62.5251 |  |  | -167.3589 |  |  | -314.7228 |  |  | -493.6809 |  |  | -675.9228 |  |  | -940.6883
[13 empty] | Press drop ratio this iteration |  |  | 0.33451 |  |  | 0.32418 |  |  | 0.2642 |  |  | -0.047566 |  |  | 24.7616 |  |  | 1.5589 |  |  | 1.2356 |  |  | 1.1384 |  |  | 1.0974 |  |  | 1.0681
[13 empty] | Expansion factor | 12 |  | 0.82579 |  |  | 0.8312 |  |  | 0.86113 |  |  | 1.0254 |  |  | -12.6087 |  |  | 0.091851 |  |  | 0.2256 |  |  | 0.20227 |  |  | 0.38056 |  |  | 0.054812
[13 empty] | C Non choked w/ reducers | 5 |  | 7.9448 |  |  | 36.6991 |  |  | 104.853 |  |  | #NUM! |  |  | -79.4924 |  |  | 1526.5583 |  |  | 402.8267 |  |  | 359.4827 |  |  | 181.0629 |  |  | 1399.6011
[13 empty] | C Choked w/ reducers | 5 |  | 7.1109 |  |  | 32.5447 |  |  | 87.3762 |  |  | 245.4451 |  |  | 9601.5044 |  |  | 346.9832 |  |  | 207.6724 |  |  | 168.6478 |  |  | 140.8274 |  |  | 193.675
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 7.9448 |  |  | 36.6991 |  |  | 104.853 |  |  | #NUM! |  |  | 9601.5044 |  |  | 346.9832 |  |  | 207.6724 |  |  | 168.6478 |  |  | 140.8274 |  |  | 193.675
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.2148 | 1503.8296 |  | 25.0991 | 6773.8105 |  | 81.853 | 16586.5738 |  | 18000 | 32306.412 |  | 18000 | 54200.1096 |  | 18000 | 79106.5361 |  | 18000 | 104522.7516 |  | 18000 | 128812.9966 |  | 18000 | 149547.8901 |  | 18000 | 175356.6624
[13 empty] | Next iteration flow rate |  |  | 1533.9062 | Abs Value of | Flow this | 6841.5486 | Abs Value of | Flow this | 16752.4395 | Abs Value of | Flow this | 32629.4762 | Abs Value of | Flow this | 54742.1107 | Abs Value of | Flow this | 79897.6015 | Abs Value of | Flow this | 105567.9791 | Abs Value of | Flow this | 130101.1266 | Abs Value of | Flow this | 151043.369 | Abs Value of | Flow this | 177110.229 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1559 |  |  | 88.7523 |  |  | 81.3689 |  |  | 56.6132 |  |  | -4.3895 |  |  | -111.3305 |  |  | -261.6563 |  |  | -444.2115 |  |  | -630.1165 |  |  | -900.2038
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43489 |  |  | 0.42812 |  |  | 0.3925 |  |  | 0.27309 |  |  | -0.021174 |  |  | -0.53703 |  |  | -1.2622 |  |  | -2.1428 |  |  | -3.0395 |  |  | -4.3424
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1559 |  |  | 28.7523 |  |  | 21.3689 |  |  | -3.3868 |  |  | -64.3895 |  |  | -171.3305 |  |  | -321.6563 |  |  | -504.2115 |  |  | -690.1165 |  |  | -960.2038
[13 empty] | Press drop ratio this iteration |  |  | 0.33449 |  |  | 0.32396 |  |  | 0.26262 |  |  | -0.059823 |  |  | 14.6691 |  |  | 1.5389 |  |  | 1.2293 |  |  | 1.1351 |  |  | 1.0952 |  |  | 1.0667
[13 empty] | Expansion factor | 12 |  | 0.8258 |  |  | 0.83132 |  |  | 0.86196 |  |  | 1.0319 |  |  | -7.062 |  |  | 0.10347 |  |  | 0.22951 |  |  | 0.20457 |  |  | 0.3818 |  |  | 0.056119
[13 empty] | C Non choked w/ reducers | 5 |  | 8.1041 |  |  | 37.0858 |  |  | 106.3449 |  |  | #NUM! |  |  | -107.1378 |  |  | 1328.4389 |  |  | 390.3098 |  |  | 350.9938 |  |  | 178.3527 |  |  | 1351.679
[13 empty] | C Choked w/ reducers | 5 |  | 7.2534 |  |  | 32.8809 |  |  | 88.4394 |  |  | 250.8001 |  |  | 5578.5945 |  |  | 337.9511 |  |  | 204.191 |  |  | 166.2963 |  |  | 139.0318 |  |  | 191.371
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.1041 |  |  | 37.0858 |  |  | 106.3449 |  |  | #NUM! |  |  | 5578.5945 |  |  | 337.9511 |  |  | 204.191 |  |  | 166.2963 |  |  | 139.0318 |  |  | 191.371
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.3741 | 1533.9062 |  | 25.4858 | 6841.5486 |  | 83.3449 | 16752.4395 |  | 18000 | 32629.4762 |  | 18000 | 54742.1107 |  | 18000 | 79897.6015 |  | 18000 | 105567.9791 |  | 18000 | 130101.1266 |  | 18000 | 151043.369 |  | 18000 | 177110.229
[13 empty] | Next iteration flow rate |  |  | 1564.5843 | Abs Value of | Flow this | 6909.9641 | Abs Value of | Flow this | 16919.9639 | Abs Value of | Flow this | 32955.7709 | Abs Value of | Flow this | 55289.5318 | Abs Value of | Flow this | 80696.5775 | Abs Value of | Flow this | 106623.6589 | Abs Value of | Flow this | 131402.1379 | Abs Value of | Flow this | 152553.8027 | Abs Value of | Flow this | 178881.3313 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1529 |  |  | 88.7226 |  |  | 81.1908 |  |  | 55.9375 |  |  | -6.2913 |  |  | -115.3818 |  |  | -268.7293 |  |  | -454.9538 |  |  | -644.5955 |  |  | -920.1115
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43487 |  |  | 0.42798 |  |  | 0.39164 |  |  | 0.26983 |  |  | -0.030348 |  |  | -0.55657 |  |  | -1.2963 |  |  | -2.1946 |  |  | -3.1094 |  |  | -4.4384
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1529 |  |  | 28.7226 |  |  | 21.1908 |  |  | -4.0625 |  |  | -66.2913 |  |  | -175.3818 |  |  | -328.7293 |  |  | -514.9538 |  |  | -704.5955 |  |  | -980.1115
[13 empty] | Press drop ratio this iteration |  |  | 0.33446 |  |  | 0.32373 |  |  | 0.261 |  |  | -0.072625 |  |  | 10.537 |  |  | 1.52 |  |  | 1.2233 |  |  | 1.1319 |  |  | 1.0931 |  |  | 1.0652
[13 empty] | Expansion factor | 12 |  | 0.82581 |  |  | 0.83144 |  |  | 0.86281 |  |  | 1.0387 |  |  | -4.791 |  |  | 0.11449 |  |  | 0.2333 |  |  | 0.20681 |  |  | 0.38301 |  |  | 0.057395
[13 empty] | C Non choked w/ reducers | 5 |  | 8.2666 |  |  | 37.477 |  |  | 107.8706 |  |  | #NUM! |  |  | -131.3042 |  |  | 1177.2131 |  |  | 378.544 |  |  | 342.8747 |  |  | 175.7066 |  |  | 1306.8452
[13 empty] | C Choked w/ reducers | 5 |  | 7.3987 |  |  | 33.2209 |  |  | 89.5197 |  |  | 256.3679 |  |  | 3931.1166 |  |  | 329.3456 |  |  | 200.8049 |  |  | 163.9934 |  |  | 137.2679 |  |  | 189.1028
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.2666 |  |  | 37.477 |  |  | 107.8706 |  |  | #NUM! |  |  | 3931.1166 |  |  | 329.3456 |  |  | 200.8049 |  |  | 163.9934 |  |  | 137.2679 |  |  | 189.1028
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.5366 | 1564.5843 |  | 25.877 | 6909.9641 |  | 84.8706 | 16919.9639 |  | 18000 | 32955.7709 |  | 18000 | 55289.5318 |  | 18000 | 80696.5775 |  | 18000 | 106623.6589 |  | 18000 | 131402.1379 |  | 18000 | 152553.8027 |  | 18000 | 178881.3313
[13 empty] | Next iteration flow rate |  |  | 1595.876 | Abs Value of | Flow this | 6979.0637 | Abs Value of | Flow this | 17089.1635 | Abs Value of | Flow this | 33285.3286 | Abs Value of | Flow this | 55842.4271 | Abs Value of | Flow this | 81503.5433 | Abs Value of | Flow this | 107689.8955 | Abs Value of | Flow this | 132716.1593 | Abs Value of | Flow this | 154079.3408 | Abs Value of | Flow this | 180670.1446 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1498 |  |  | 88.6923 |  |  | 81.0091 |  |  | 55.2482 |  |  | -8.2314 |  |  | -119.5146 |  |  | -275.9444 |  |  | -465.912 |  |  | -659.3655 |  |  | -940.4193
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43486 |  |  | 0.42783 |  |  | 0.39077 |  |  | 0.2665 |  |  | -0.039706 |  |  | -0.57651 |  |  | -1.3311 |  |  | -2.2474 |  |  | -3.1806 |  |  | -4.5363
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1498 |  |  | 28.6923 |  |  | 21.0091 |  |  | -4.7518 |  |  | -68.2314 |  |  | -179.5146 |  |  | -335.9444 |  |  | -525.912 |  |  | -719.3655 |  |  | -1000.4193
[13 empty] | Press drop ratio this iteration |  |  | 0.33444 |  |  | 0.3235 |  |  | 0.25934 |  |  | -0.086008 |  |  | 8.2892 |  |  | 1.502 |  |  | 1.2174 |  |  | 1.1288 |  |  | 1.091 |  |  | 1.0638
[13 empty] | Expansion factor | 12 |  | 0.82582 |  |  | 0.83156 |  |  | 0.86368 |  |  | 1.0458 |  |  | -3.5556 |  |  | 0.12497 |  |  | 0.23696 |  |  | 0.20898 |  |  | 0.38418 |  |  | 0.058641
[13 empty] | C Non choked w/ reducers | 5 |  | 8.4324 |  |  | 37.8727 |  |  | 109.4315 |  |  | #NUM! |  |  | -153.9852 |  |  | 1057.9216 |  |  | 367.4612 |  |  | 335.1006 |  |  | 173.1221 |  |  | 1264.8054
[13 empty] | C Choked w/ reducers | 5 |  | 7.5469 |  |  | 33.5645 |  |  | 90.6177 |  |  | 262.1621 |  |  | 3034.6264 |  |  | 321.1364 |  |  | 197.51 |  |  | 161.7377 |  |  | 135.535 |  |  | 186.8694
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.4324 |  |  | 37.8727 |  |  | 109.4315 |  |  | #NUM! |  |  | 3034.6264 |  |  | 321.1364 |  |  | 197.51 |  |  | 161.7377 |  |  | 135.535 |  |  | 186.8694
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.7024 | 1595.876 |  | 26.2727 | 6979.0637 |  | 86.4315 | 17089.1635 |  | 18000 | 33285.3286 |  | 18000 | 55842.4271 |  | 18000 | 81503.5433 |  | 18000 | 107689.8955 |  | 18000 | 132716.1593 |  | 18000 | 154079.3408 |  | 18000 | 180670.1446
[13 empty] | Next iteration flow rate |  |  | 1627.7935 | Abs Value of | Flow this | 7048.8544 | Abs Value of | Flow this | 17260.0552 | Abs Value of | Flow this | 33618.1819 | Abs Value of | Flow this | 56400.8514 | Abs Value of | Flow this | 82318.5787 | Abs Value of | Flow this | 108766.7944 | Abs Value of | Flow this | 134043.3208 | Abs Value of | Flow this | 155620.1342 | Abs Value of | Flow this | 182476.8461 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1465 |  |  | 88.6614 |  |  | 80.8238 |  |  | 54.5451 |  |  | -10.2105 |  |  | -123.7305 |  |  | -283.3045 |  |  | -477.0905 |  |  | -674.4323 |  |  | -961.1354
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43484 |  |  | 0.42768 |  |  | 0.38987 |  |  | 0.26311 |  |  | -0.049253 |  |  | -0.59684 |  |  | -1.3666 |  |  | -2.3014 |  |  | -3.2533 |  |  | -4.6363
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1465 |  |  | 28.6614 |  |  | 20.8238 |  |  | -5.4549 |  |  | -70.2105 |  |  | -183.7305 |  |  | -343.3045 |  |  | -537.0905 |  |  | -734.4323 |  |  | -1021.1354
[13 empty] | Press drop ratio this iteration |  |  | 0.33442 |  |  | 0.32327 |  |  | 0.25764 |  |  | -0.10001 |  |  | 6.8763 |  |  | 1.4849 |  |  | 1.2118 |  |  | 1.1258 |  |  | 1.089 |  |  | 1.0624
[13 empty] | Expansion factor | 12 |  | 0.82583 |  |  | 0.83168 |  |  | 0.86457 |  |  | 1.0533 |  |  | -2.7791 |  |  | 0.13493 |  |  | 0.2405 |  |  | 0.2111 |  |  | 0.38533 |  |  | 0.059858
[13 empty] | C Non choked w/ reducers | 5 |  | 8.6015 |  |  | 38.2731 |  |  | 111.0291 |  |  | #NUM! |  |  | -176.1207 |  |  | 961.3587 |  |  | 357.0013 |  |  | 327.649 |  |  | 170.5971 |  |  | 1225.3017
[13 empty] | C Choked w/ reducers | 5 |  | 7.6981 |  |  | 33.912 |  |  | 91.7338 |  |  | 268.197 |  |  | 2470.8947 |  |  | 313.2963 |  |  | 194.3026 |  |  | 159.5276 |  |  | 133.8322 |  |  | 184.6701
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.6015 |  |  | 38.2731 |  |  | 111.0291 |  |  | #NUM! |  |  | 2470.8947 |  |  | 313.2963 |  |  | 194.3026 |  |  | 159.5276 |  |  | 133.8322 |  |  | 184.6701
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 3.8715 | 1627.7935 |  | 26.6731 | 7048.8544 |  | 88.0291 | 17260.0552 |  | 18000 | 33618.1819 |  | 18000 | 56400.8514 |  | 18000 | 82318.5787 |  | 18000 | 108766.7944 |  | 18000 | 134043.3208 |  | 18000 | 155620.1342 |  | 18000 | 182476.8461
[13 empty] | Next iteration flow rate |  |  | 1660.3494 | Abs Value of | Flow this | 7119.3429 | Abs Value of | Flow this | 17432.6557 | Abs Value of | Flow this | 33954.3637 | Abs Value of | Flow this | 56964.8599 | Abs Value of | Flow this | 83141.7645 | Abs Value of | Flow this | 109854.4624 | Abs Value of | Flow this | 135383.7541 | Abs Value of | Flow this | 157176.3355 | Abs Value of | Flow this | 184301.6145 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1431 |  |  | 88.6298 |  |  | 80.6347 |  |  | 53.8278 |  |  | -12.2293 |  |  | -128.0311 |  |  | -290.8125 |  |  | -488.4936 |  |  | -689.802 |  |  | -982.2679
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43483 |  |  | 0.42753 |  |  | 0.38896 |  |  | 0.25965 |  |  | -0.058991 |  |  | -0.61759 |  |  | -1.4028 |  |  | -2.3564 |  |  | -3.3274 |  |  | -4.7382
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1431 |  |  | 28.6298 |  |  | 20.6347 |  |  | -6.1722 |  |  | -72.2293 |  |  | -188.0311 |  |  | -350.8125 |  |  | -548.4936 |  |  | -749.802 |  |  | -1042.2679
[13 empty] | Press drop ratio this iteration |  |  | 0.33439 |  |  | 0.32303 |  |  | 0.2559 |  |  | -0.11467 |  |  | 5.9062 |  |  | 1.4686 |  |  | 1.2063 |  |  | 1.1228 |  |  | 1.087 |  |  | 1.0611
[13 empty] | Expansion factor | 12 |  | 0.82585 |  |  | 0.8318 |  |  | 0.86548 |  |  | 1.0611 |  |  | -2.246 |  |  | 0.14442 |  |  | 0.24392 |  |  | 0.21315 |  |  | 0.38645 |  |  | 0.061046
[13 empty] | C Non choked w/ reducers | 5 |  | 8.7741 |  |  | 38.6781 |  |  | 112.6647 |  |  | #NUM! |  |  | -198.2892 |  |  | 881.549 |  |  | 347.1112 |  |  | 320.4993 |  |  | 168.1292 |  |  | 1188.1069
[13 empty] | C Choked w/ reducers | 5 |  | 7.8524 |  |  | 34.2633 |  |  | 92.8683 |  |  | 274.4885 |  |  | 2083.6215 |  |  | 305.8003 |  |  | 191.1791 |  |  | 157.3617 |  |  | 132.1587 |  |  | 182.5041
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.7741 |  |  | 38.6781 |  |  | 112.6647 |  |  | #NUM! |  |  | 2083.6215 |  |  | 305.8003 |  |  | 191.1791 |  |  | 157.3617 |  |  | 132.1587 |  |  | 182.5041
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.0441 | 1660.3494 |  | 27.0781 | 7119.3429 |  | 89.6647 | 17432.6557 |  | 18000 | 33954.3637 |  | 18000 | 56964.8599 |  | 18000 | 83141.7645 |  | 18000 | 109854.4624 |  | 18000 | 135383.7541 |  | 18000 | 157176.3355 |  | 18000 | 184301.6145
[13 empty] | Next iteration flow rate |  |  | 1693.5564 | Abs Value of | Flow this | 7190.5364 | Abs Value of | Flow this | 17606.9823 | Abs Value of | Flow this | 34293.9074 | Abs Value of | Flow this | 57534.5085 | Abs Value of | Flow this | 83973.1821 | Abs Value of | Flow this | 110953.007 | Abs Value of | Flow this | 136737.5916 | Abs Value of | Flow this | 158748.0989 | Abs Value of | Flow this | 186144.6307 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1396 |  |  | 88.5977 |  |  | 80.4419 |  |  | 53.0961 |  |  | -14.2888 |  |  | -132.4182 |  |  | -298.4715 |  |  | -500.1259 |  |  | -705.4807 |  |  | -1003.8251
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43481 |  |  | 0.42737 |  |  | 0.38803 |  |  | 0.25612 |  |  | -0.068925 |  |  | -0.63875 |  |  | -1.4398 |  |  | -2.4125 |  |  | -3.4031 |  |  | -4.8422
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1396 |  |  | 28.5977 |  |  | 20.4419 |  |  | -6.9039 |  |  | -74.2888 |  |  | -192.4182 |  |  | -358.4715 |  |  | -560.1259 |  |  | -765.4807 |  |  | -1063.8251
[13 empty] | Press drop ratio this iteration |  |  | 0.33437 |  |  | 0.32278 |  |  | 0.25412 |  |  | -0.13003 |  |  | 5.1991 |  |  | 1.4531 |  |  | 1.201 |  |  | 1.12 |  |  | 1.085 |  |  | 1.0598
[13 empty] | Expansion factor | 12 |  | 0.82586 |  |  | 0.83193 |  |  | 0.86642 |  |  | 1.0693 |  |  | -1.8574 |  |  | 0.15346 |  |  | 0.24724 |  |  | 0.21516 |  |  | 0.38754 |  |  | 0.062207
[13 empty] | C Non choked w/ reducers | 5 |  | 8.9501 |  |  | 39.088 |  |  | 114.34 |  |  | #NUM! |  |  | -220.9183 |  |  | 814.4448 |  |  | 337.7437 |  |  | 313.6326 |  |  | 165.7166 |  |  | 1153.0202
[13 empty] | C Choked w/ reducers | 5 |  | 8.0097 |  |  | 34.6185 |  |  | 94.0219 |  |  | 281.0538 |  |  | 1801.1429 |  |  | 298.6257 |  |  | 188.136 |  |  | 155.2386 |  |  | 130.5138 |  |  | 180.3707
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 8.9501 |  |  | 39.088 |  |  | 114.34 |  |  | #NUM! |  |  | 1801.1429 |  |  | 298.6257 |  |  | 188.136 |  |  | 155.2386 |  |  | 130.5138 |  |  | 180.3707
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.2201 | 1693.5564 |  | 27.488 | 7190.5364 |  | 91.34 | 17606.9823 |  | 18000 | 34293.9074 |  | 18000 | 57534.5085 |  | 18000 | 83973.1821 |  | 18000 | 110953.007 |  | 18000 | 136737.5916 |  | 18000 | 158748.0989 |  | 18000 | 186144.6307
[13 empty] | Next iteration flow rate |  |  | 1727.4275 | Abs Value of | Flow this | 7262.4417 | Abs Value of | Flow this | 17783.0521 | Abs Value of | Flow this | 34636.8464 | Abs Value of | Flow this | 58109.8536 | Abs Value of | Flow this | 84812.9139 | Abs Value of | Flow this | 112062.5371 | Abs Value of | Flow this | 138104.9675 | Abs Value of | Flow this | 160335.5799 | Abs Value of | Flow this | 188006.077 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.136 |  |  | 88.5648 |  |  | 80.2451 |  |  | 52.3497 |  |  | -16.3896 |  |  | -136.8934 |  |  | -306.2844 |  |  | -511.9921 |  |  | -721.4745 |  |  | -1025.8156
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43479 |  |  | 0.42721 |  |  | 0.38708 |  |  | 0.25252 |  |  | -0.079059 |  |  | -0.66034 |  |  | -1.4774 |  |  | -2.4697 |  |  | -3.4802 |  |  | -4.9483
[13 empty] | Delta P at this iteration flow rate |  |  | 30.136 |  |  | 28.5648 |  |  | 20.2451 |  |  | -7.6503 |  |  | -76.3896 |  |  | -196.8934 |  |  | -366.2844 |  |  | -571.9921 |  |  | -781.4745 |  |  | -1085.8156
[13 empty] | Press drop ratio this iteration |  |  | 0.33434 |  |  | 0.32253 |  |  | 0.25229 |  |  | -0.14614 |  |  | 4.6609 |  |  | 1.4383 |  |  | 1.1959 |  |  | 1.1172 |  |  | 1.0832 |  |  | 1.0585
[13 empty] | Expansion factor | 12 |  | 0.82587 |  |  | 0.83206 |  |  | 0.86738 |  |  | 1.0779 |  |  | -1.5616 |  |  | 0.16209 |  |  | 0.25046 |  |  | 0.2171 |  |  | 0.3886 |  |  | 0.063341
[13 empty] | C Non choked w/ reducers | 5 |  | 9.1297 |  |  | 39.5026 |  |  | 116.0566 |  |  | #NUM! |  |  | -244.3719 |  |  | 757.2061 |  |  | 328.8566 |  |  | 307.0316 |  |  | 163.3572 |  |  | 1119.8637
[13 empty] | C Choked w/ reducers | 5 |  | 8.1703 |  |  | 34.9776 |  |  | 95.195 |  |  | 287.9116 |  |  | 1585.9738 |  |  | 291.7519 |  |  | 185.1703 |  |  | 153.1572 |  |  | 128.8968 |  |  | 178.2691
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9.1297 |  |  | 39.5026 |  |  | 116.0566 |  |  | #NUM! |  |  | 1585.9738 |  |  | 291.7519 |  |  | 185.1703 |  |  | 153.1572 |  |  | 128.8968 |  |  | 178.2691
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.3997 | 1727.4275 |  | 27.9026 | 7262.4417 |  | 93.0566 | 17783.0521 |  | 18000 | 34636.8464 |  | 18000 | 58109.8536 |  | 18000 | 84812.9139 |  | 18000 | 112062.5371 |  | 18000 | 138104.9675 |  | 18000 | 160335.5799 |  | 18000 | 188006.077
[13 empty] | Next iteration flow rate |  |  | 1761.9761 | Abs Value of | Flow this | 7335.0661 | Abs Value of | Flow this | 17960.8826 | Abs Value of | Flow this | 34983.2149 | Abs Value of | Flow this | 58690.9521 | Abs Value of | Flow this | 85661.0431 | Abs Value of | Flow this | 113183.1624 | Abs Value of | Flow this | 139486.0172 | Abs Value of | Flow this | 161938.9357 | Abs Value of | Flow this | 189886.1377 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1322 |  |  | 88.5314 |  |  | 80.0444 |  |  | 51.5884 |  |  | -18.5327 |  |  | -141.4586 |  |  | -314.2543 |  |  | -524.0968 |  |  | -737.7897 |  |  | -1048.2481
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43477 |  |  | 0.42705 |  |  | 0.38611 |  |  | 0.24885 |  |  | -0.089397 |  |  | -0.68236 |  |  | -1.5159 |  |  | -2.5281 |  |  | -3.5589 |  |  | -5.0565
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1322 |  |  | 28.5314 |  |  | 20.0444 |  |  | -8.4116 |  |  | -78.5327 |  |  | -201.4586 |  |  | -374.2543 |  |  | -584.0968 |  |  | -797.7897 |  |  | -1108.2481
[13 empty] | Press drop ratio this iteration |  |  | 0.33431 |  |  | 0.32227 |  |  | 0.25042 |  |  | -0.16305 |  |  | 4.2375 |  |  | 1.4242 |  |  | 1.1909 |  |  | 1.1145 |  |  | 1.0813 |  |  | 1.0572
[13 empty] | Expansion factor | 12 |  | 0.82589 |  |  | 0.8322 |  |  | 0.86837 |  |  | 1.0869 |  |  | -1.3289 |  |  | 0.17033 |  |  | 0.25357 |  |  | 0.219 |  |  | 0.38964 |  |  | 0.064449
[13 empty] | C Non choked w/ reducers | 5 |  | 9.3129 |  |  | 39.9222 |  |  | 117.8162 |  |  | #NUM! |  |  | -268.9959 |  |  | 707.7821 |  |  | 320.4124 |  |  | 300.6805 |  |  | 161.0491 |  |  | 1088.4788
[13 empty] | C Choked w/ reducers | 5 |  | 8.334 |  |  | 35.3408 |  |  | 96.388 |  |  | 295.0825 |  |  | 1416.6026 |  |  | 285.1598 |  |  | 182.2788 |  |  | 151.116 |  |  | 127.3069 |  |  | 176.1987
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9.3129 |  |  | 39.9222 |  |  | 117.8162 |  |  | #NUM! |  |  | 1416.6026 |  |  | 285.1598 |  |  | 182.2788 |  |  | 151.116 |  |  | 127.3069 |  |  | 176.1987
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.5829 | 1761.9761 |  | 28.3222 | 7335.0661 |  | 94.8162 | 17960.8826 |  | 18000 | 34983.2149 |  | 18000 | 58690.9521 |  | 18000 | 85661.0431 |  | 18000 | 113183.1624 |  | 18000 | 139486.0172 |  | 18000 | 161938.9357 |  | 18000 | 189886.1377
[13 empty] | Next iteration flow rate |  |  | 1797.2156 | Abs Value of | Flow this | 7408.4168 | Abs Value of | Flow this | 18140.4914 | Abs Value of | Flow this | 35333.0471 | Abs Value of | Flow this | 59277.8616 | Abs Value of | Flow this | 86517.6535 | Abs Value of | Flow this | 114314.9941 | Abs Value of | Flow this | 140880.8774 | Abs Value of | Flow this | 163558.325 | Abs Value of | Flow this | 191784.9991 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1282 |  |  | 88.4972 |  |  | 79.8397 |  |  | 50.8117 |  |  | -20.7188 |  |  | -146.1155 |  |  | -322.3844 |  |  | -536.4447 |  |  | -754.4329 |  |  | -1071.1315
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43476 |  |  | 0.42689 |  |  | 0.38513 |  |  | 0.2451 |  |  | -0.099942 |  |  | -0.70482 |  |  | -1.5551 |  |  | -2.5877 |  |  | -3.6392 |  |  | -5.1669
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1282 |  |  | 28.4972 |  |  | 19.8397 |  |  | -9.1883 |  |  | -80.7188 |  |  | -206.1155 |  |  | -382.3844 |  |  | -596.4447 |  |  | -814.4329 |  |  | -1131.1315
[13 empty] | Press drop ratio this iteration |  |  | 0.33428 |  |  | 0.32201 |  |  | 0.24849 |  |  | -0.18083 |  |  | 3.8959 |  |  | 1.4106 |  |  | 1.1861 |  |  | 1.1118 |  |  | 1.0795 |  |  | 1.056
[13 empty] | Expansion factor | 12 |  | 0.8259 |  |  | 0.83233 |  |  | 0.86938 |  |  | 1.0964 |  |  | -1.1412 |  |  | 0.17821 |  |  | 0.25659 |  |  | 0.22085 |  |  | 0.39066 |  |  | 0.065531
[13 empty] | C Non choked w/ reducers | 5 |  | 9.4998 |  |  | 40.3467 |  |  | 119.6209 |  |  | #NUM! |  |  | -295.1471 |  |  | 664.6541 |  |  | 312.3772 |  |  | 294.5645 |  |  | 158.7907 |  |  | 1058.724
[13 empty] | C Choked w/ reducers | 5 |  | 8.5011 |  |  | 35.708 |  |  | 97.6015 |  |  | 302.589 |  |  | 1279.8018 |  |  | 278.832 |  |  | 179.4588 |  |  | 149.114 |  |  | 125.7434 |  |  | 174.1587
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9.4998 |  |  | 40.3467 |  |  | 119.6209 |  |  | #NUM! |  |  | 1279.8018 |  |  | 278.832 |  |  | 179.4588 |  |  | 149.114 |  |  | 125.7434 |  |  | 174.1587
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.7698 | 1797.2156 |  | 28.7467 | 7408.4168 |  | 96.6209 | 18140.4914 |  | 18000 | 35333.0471 |  | 18000 | 59277.8616 |  | 18000 | 86517.6535 |  | 18000 | 114314.9941 |  | 18000 | 140880.8774 |  | 18000 | 163558.325 |  | 18000 | 191784.9991
[13 empty] | Next iteration flow rate |  |  | 1833.1599 | Abs Value of | Flow this | 7482.501 | Abs Value of | Flow this | 18321.8964 | Abs Value of | Flow this | 35686.3775 | Abs Value of | Flow this | 59870.6402 | Abs Value of | Flow this | 87382.8301 | Abs Value of | Flow this | 115458.144 | Abs Value of | Flow this | 142289.6861 | Abs Value of | Flow this | 165193.9083 | Abs Value of | Flow this | 193702.8491 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1241 |  |  | 88.4624 |  |  | 79.6308 |  |  | 50.0193 |  |  | -22.9489 |  |  | -150.8661 |  |  | -330.678 |  |  | -549.0409 |  |  | -771.4107 |  |  | -1094.4749
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43474 |  |  | 0.42672 |  |  | 0.38412 |  |  | 0.24128 |  |  | -0.1107 |  |  | -0.72774 |  |  | -1.5951 |  |  | -2.6484 |  |  | -3.7211 |  |  | -5.2795
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1241 |  |  | 28.4624 |  |  | 19.6308 |  |  | -9.9807 |  |  | -82.9489 |  |  | -210.8661 |  |  | -390.678 |  |  | -609.0409 |  |  | -831.4107 |  |  | -1154.4749
[13 empty] | Press drop ratio this iteration |  |  | 0.33425 |  |  | 0.32175 |  |  | 0.24652 |  |  | -0.19954 |  |  | 3.6145 |  |  | 1.3977 |  |  | 1.1814 |  |  | 1.1093 |  |  | 1.0778 |  |  | 1.0548
[13 empty] | Expansion factor | 12 |  | 0.82592 |  |  | 0.83247 |  |  | 0.87042 |  |  | 1.1064 |  |  | -0.98649 |  |  | 0.18574 |  |  | 0.25951 |  |  | 0.22265 |  |  | 0.39164 |  |  | 0.066588
[13 empty] | C Non choked w/ reducers | 5 |  | 9.6905 |  |  | 40.7764 |  |  | 121.4725 |  |  | #NUM! |  |  | -323.2169 |  |  | 626.6739 |  |  | 304.7207 |  |  | 288.6702 |  |  | 156.5802 |  |  | 1030.4724
[13 empty] | C Choked w/ reducers | 5 |  | 8.6715 |  |  | 36.0792 |  |  | 98.8361 |  |  | 310.4559 |  |  | 1166.9904 |  |  | 272.7525 |  |  | 176.7075 |  |  | 147.1499 |  |  | 124.2057 |  |  | 172.1487
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9.6905 |  |  | 40.7764 |  |  | 121.4725 |  |  | #NUM! |  |  | 1166.9904 |  |  | 272.7525 |  |  | 176.7075 |  |  | 147.1499 |  |  | 124.2057 |  |  | 172.1487
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 4.9605 | 1833.1599 |  | 29.1764 | 7482.501 |  | 98.4725 | 18321.8964 |  | 18000 | 35686.3775 |  | 18000 | 59870.6402 |  | 18000 | 87382.8301 |  | 18000 | 115458.144 |  | 18000 | 142289.6861 |  | 18000 | 165193.9083 |  | 18000 | 193702.8491
[13 empty] | Next iteration flow rate |  |  | 1869.8231 | Abs Value of | Flow this | 7557.326 | Abs Value of | Flow this | 18505.1153 | Abs Value of | Flow this | 36043.2413 | Abs Value of | Flow this | 60469.3466 | Abs Value of | Flow this | 88256.6584 | Abs Value of | Flow this | 116612.7255 | Abs Value of | Flow this | 143712.583 | Abs Value of | Flow this | 166845.8473 | Abs Value of | Flow this | 195639.8776 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1198 |  |  | 88.4269 |  |  | 79.4178 |  |  | 49.2111 |  |  | -25.2238 |  |  | -155.7121 |  |  | -339.1383 |  |  | -561.8903 |  |  | -788.7297 |  |  | -1118.2874
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43472 |  |  | 0.42655 |  |  | 0.38309 |  |  | 0.23738 |  |  | -0.12167 |  |  | -0.75112 |  |  | -1.6359 |  |  | -2.7104 |  |  | -3.8046 |  |  | -5.3943
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1198 |  |  | 28.4269 |  |  | 19.4178 |  |  | -10.7889 |  |  | -85.2238 |  |  | -215.7121 |  |  | -399.1383 |  |  | -621.8903 |  |  | -848.7297 |  |  | -1178.2874
[13 empty] | Press drop ratio this iteration |  |  | 0.33422 |  |  | 0.32147 |  |  | 0.2445 |  |  | -0.21924 |  |  | 3.3787 |  |  | 1.3853 |  |  | 1.1769 |  |  | 1.1068 |  |  | 1.0761 |  |  | 1.0537
[13 empty] | Expansion factor | 12 |  | 0.82594 |  |  | 0.83261 |  |  | 0.87148 |  |  | 1.1169 |  |  | -0.8569 |  |  | 0.19295 |  |  | 0.26235 |  |  | 0.2244 |  |  | 0.39261 |  |  | 0.067621
[13 empty] | C Non choked w/ reducers | 5 |  | 9.8851 |  |  | 41.2111 |  |  | 123.3732 |  |  | #NUM! |  |  | -353.6548 |  |  | 592.9571 |  |  | 297.4154 |  |  | 282.9851 |  |  | 154.416 |  |  | 1003.6101
[13 empty] | C Choked w/ reducers | 5 |  | 8.8454 |  |  | 36.4547 |  |  | 100.0922 |  |  | 318.7104 |  |  | 1072.3585 |  |  | 266.9066 |  |  | 174.0223 |  |  | 145.2227 |  |  | 122.6932 |  |  | 170.1678
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9.8851 |  |  | 41.2111 |  |  | 123.3732 |  |  | #NUM! |  |  | 1072.3585 |  |  | 266.9066 |  |  | 174.0223 |  |  | 145.2227 |  |  | 122.6932 |  |  | 170.1678
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.1551 | 1869.8231 |  | 29.6111 | 7557.326 |  | 100.3732 | 18505.1153 |  | 18000 | 36043.2413 |  | 18000 | 60469.3466 |  | 18000 | 88256.6584 |  | 18000 | 116612.7255 |  | 18000 | 143712.583 |  | 18000 | 166845.8473 |  | 18000 | 195639.8776
[13 empty] | Next iteration flow rate |  |  | 1907.2196 | Abs Value of | Flow this | 7632.8992 | Abs Value of | Flow this | 18690.1665 | Abs Value of | Flow this | 36403.6737 | Abs Value of | Flow this | 61074.0401 | Abs Value of | Flow this | 89139.2249 | Abs Value of | Flow this | 117778.8527 | Abs Value of | Flow this | 145149.7088 | Abs Value of | Flow this | 168514.3058 | Abs Value of | Flow this | 197596.2764 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1153 |  |  | 88.3906 |  |  | 79.2005 |  |  | 48.3866 |  |  | -27.5444 |  |  | -160.6555 |  |  | -347.7686 |  |  | -574.9979 |  |  | -806.3967 |  |  | -1142.5787
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43469 |  |  | 0.42637 |  |  | 0.38204 |  |  | 0.2334 |  |  | -0.13287 |  |  | -0.77496 |  |  | -1.6775 |  |  | -2.7736 |  |  | -3.8899 |  |  | -5.5115
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1153 |  |  | 28.3906 |  |  | 19.2005 |  |  | -11.6134 |  |  | -87.5444 |  |  | -220.6555 |  |  | -407.7686 |  |  | -634.9979 |  |  | -866.3967 |  |  | -1202.5787
[13 empty] | Press drop ratio this iteration |  |  | 0.33419 |  |  | 0.32119 |  |  | 0.24243 |  |  | -0.24001 |  |  | 3.1783 |  |  | 1.3735 |  |  | 1.1725 |  |  | 1.1043 |  |  | 1.0744 |  |  | 1.0525
[13 empty] | Expansion factor | 12 |  | 0.82595 |  |  | 0.83276 |  |  | 0.87257 |  |  | 1.1279 |  |  | -0.74676 |  |  | 0.19986 |  |  | 0.2651 |  |  | 0.2261 |  |  | 0.39355 |  |  | 0.06863
[13 empty] | C Non choked w/ reducers | 5 |  | 10.0835 |  |  | 41.6511 |  |  | 125.3252 |  |  | #NUM! |  |  | -386.995 |  |  | 562.8113 |  |  | 290.4366 |  |  | 277.4977 |  |  | 152.2966 |  |  | 978.0344
[13 empty] | C Choked w/ reducers | 5 |  | 9.0227 |  |  | 36.8343 |  |  | 101.3705 |  |  | 327.3824 |  |  | 991.832 |  |  | 261.2807 |  |  | 171.4007 |  |  | 143.3314 |  |  | 121.2052 |  |  | 168.2155
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 10.0835 |  |  | 41.6511 |  |  | 125.3252 |  |  | #NUM! |  |  | 991.832 |  |  | 261.2807 |  |  | 171.4007 |  |  | 143.3314 |  |  | 121.2052 |  |  | 168.2155
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.3535 | 1907.2196 |  | 30.0511 | 7632.8992 |  | 102.3252 | 18690.1665 |  | 18000 | 36403.6737 |  | 18000 | 61074.0401 |  | 18000 | 89139.2249 |  | 18000 | 117778.8527 |  | 18000 | 145149.7088 |  | 18000 | 168514.3058 |  | 18000 | 197596.2764
[13 empty] | Next iteration flow rate |  |  | 1945.364 | Abs Value of | Flow this | 7709.2282 | Abs Value of | Flow this | 18877.0681 | Abs Value of | Flow this | 36767.7105 | Abs Value of | Flow this | 61684.7805 | Abs Value of | Flow this | 90030.6172 | Abs Value of | Flow this | 118956.6412 | Abs Value of | Flow this | 146601.2059 | Abs Value of | Flow this | 170199.4489 | Abs Value of | Flow this | 199572.2391 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1107 |  |  | 88.3536 |  |  | 78.9788 |  |  | 47.5456 |  |  | -29.9117 |  |  | -165.6983 |  |  | -356.5723 |  |  | -588.369 |  |  | -824.4189 |  |  | -1167.3581
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43467 |  |  | 0.4262 |  |  | 0.38097 |  |  | 0.22935 |  |  | -0.14429 |  |  | -0.79929 |  |  | -1.72 |  |  | -2.8381 |  |  | -3.9768 |  |  | -5.631
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1107 |  |  | 28.3536 |  |  | 18.9788 |  |  | -12.4544 |  |  | -89.9117 |  |  | -225.6983 |  |  | -416.5723 |  |  | -648.369 |  |  | -884.4189 |  |  | -1227.3581
[13 empty] | Press drop ratio this iteration |  |  | 0.33415 |  |  | 0.32091 |  |  | 0.2403 |  |  | -0.26195 |  |  | 3.0059 |  |  | 1.3621 |  |  | 1.1683 |  |  | 1.102 |  |  | 1.0728 |  |  | 1.0514
[13 empty] | Expansion factor | 12 |  | 0.82597 |  |  | 0.83291 |  |  | 0.87369 |  |  | 1.1396 |  |  | -0.65201 |  |  | 0.20648 |  |  | 0.26777 |  |  | 0.22776 |  |  | 0.39447 |  |  | 0.069617
[13 empty] | C Non choked w/ reducers | 5 |  | 10.286 |  |  | 42.0963 |  |  | 127.3311 |  |  | #NUM! |  |  | -423.8904 |  |  | 535.6868 |  |  | 283.7617 |  |  | 272.1973 |  |  | 150.2206 |  |  | 953.6525
[13 empty] | C Choked w/ reducers | 5 |  | 9.2036 |  |  | 37.2182 |  |  | 102.6716 |  |  | 336.5054 |  |  | 922.4698 |  |  | 255.8623 |  |  | 168.8405 |  |  | 141.4748 |  |  | 119.7411 |  |  | 166.2913
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 10.286 |  |  | 42.0963 |  |  | 127.3311 |  |  | #NUM! |  |  | 922.4698 |  |  | 255.8623 |  |  | 168.8405 |  |  | 141.4748 |  |  | 119.7411 |  |  | 166.2913
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.556 | 1945.364 |  | 30.4963 | 7709.2282 |  | 104.3311 | 18877.0681 |  | 18000 | 36767.7105 |  | 18000 | 61684.7805 |  | 18000 | 90030.6172 |  | 18000 | 118956.6412 |  | 18000 | 146601.2059 |  | 18000 | 170199.4489 |  | 18000 | 199572.2391
[13 empty] | Next iteration flow rate |  |  | 1984.2712 | Abs Value of | Flow this | 7786.3205 | Abs Value of | Flow this | 19065.8388 | Abs Value of | Flow this | 37135.3876 | Abs Value of | Flow this | 62301.6283 | Abs Value of | Flow this | 90930.9234 | Abs Value of | Flow this | 120146.2076 | Abs Value of | Flow this | 148067.218 | Abs Value of | Flow this | 171901.4434 | Abs Value of | Flow this | 201567.9615 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1059 |  |  | 88.3159 |  |  | 78.7526 |  |  | 46.6876 |  |  | -32.3265 |  |  | -170.8425 |  |  | -365.5531 |  |  | -602.0088 |  |  | -842.8034 |  |  | -1192.6356
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43465 |  |  | 0.42601 |  |  | 0.37988 |  |  | 0.22521 |  |  | -0.15594 |  |  | -0.8241 |  |  | -1.7633 |  |  | -2.9039 |  |  | -4.0655 |  |  | -5.753
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1059 |  |  | 28.3159 |  |  | 18.7526 |  |  | -13.3124 |  |  | -92.3265 |  |  | -230.8425 |  |  | -425.5531 |  |  | -662.0088 |  |  | -902.8034 |  |  | -1252.6356
[13 empty] | Press drop ratio this iteration |  |  | 0.33412 |  |  | 0.32062 |  |  | 0.23812 |  |  | -0.28514 |  |  | 2.8561 |  |  | 1.3512 |  |  | 1.1641 |  |  | 1.0997 |  |  | 1.0712 |  |  | 1.0503
[13 empty] | Expansion factor | 12 |  | 0.82599 |  |  | 0.83306 |  |  | 0.87483 |  |  | 1.152 |  |  | -0.56966 |  |  | 0.21283 |  |  | 0.27036 |  |  | 0.22938 |  |  | 0.39536 |  |  | 0.070581
[13 empty] | C Non choked w/ reducers | 5 |  | 10.4927 |  |  | 42.547 |  |  | 129.3933 |  |  | #NUM! |  |  | -465.1588 |  |  | 511.1416 |  |  | 277.3703 |  |  | 267.0739 |  |  | 148.1865 |  |  | 930.3804
[13 empty] | C Choked w/ reducers | 5 |  | 9.3882 |  |  | 37.6065 |  |  | 103.9961 |  |  | 346.1161 |  |  | 862.0952 |  |  | 250.6397 |  |  | 166.3395 |  |  | 139.6521 |  |  | 118.3005 |  |  | 164.3944
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 10.4927 |  |  | 42.547 |  |  | 129.3933 |  |  | #NUM! |  |  | 862.0952 |  |  | 250.6397 |  |  | 166.3395 |  |  | 139.6521 |  |  | 118.3005 |  |  | 164.3944
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.7627 | 1984.2712 |  | 30.947 | 7786.3205 |  | 106.3933 | 19065.8388 |  | 18000 | 37135.3876 |  | 18000 | 62301.6283 |  | 18000 | 90930.9234 |  | 18000 | 120146.2076 |  | 18000 | 148067.218 |  | 18000 | 171901.4434 |  | 18000 | 201567.9615
[13 empty] | Next iteration flow rate |  |  | 2023.9567 | Abs Value of | Flow this | 7864.1837 | Abs Value of | Flow this | 19256.4972 | Abs Value of | Flow this | 37506.7414 | Abs Value of | Flow this | 62924.6446 | Abs Value of | Flow this | 91840.2326 | Abs Value of | Flow this | 121347.6697 | Abs Value of | Flow this | 149547.8901 | Abs Value of | Flow this | 173620.4578 | Abs Value of | Flow this | 203583.6411 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.1008 |  |  | 88.2774 |  |  | 78.5219 |  |  | 45.8124 |  |  | -34.7899 |  |  | -176.0901 |  |  | -374.7143 |  |  | -615.9228 |  |  | -861.5574 |  |  | -1218.4212
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43462 |  |  | 0.42583 |  |  | 0.37877 |  |  | 0.22099 |  |  | -0.16782 |  |  | -0.84941 |  |  | -1.8075 |  |  | -2.9711 |  |  | -4.1559 |  |  | -5.8774
[13 empty] | Delta P at this iteration flow rate |  |  | 30.1008 |  |  | 28.2774 |  |  | 18.5219 |  |  | -14.1876 |  |  | -94.7899 |  |  | -236.0901 |  |  | -434.7143 |  |  | -675.9228 |  |  | -921.5574 |  |  | -1278.4212
[13 empty] | Press drop ratio this iteration |  |  | 0.33408 |  |  | 0.32032 |  |  | 0.23588 |  |  | -0.30969 |  |  | 2.7246 |  |  | 1.3407 |  |  | 1.1601 |  |  | 1.0974 |  |  | 1.0696 |  |  | 1.0492
[13 empty] | Expansion factor | 12 |  | 0.82601 |  |  | 0.83321 |  |  | 0.87601 |  |  | 1.1651 |  |  | -0.49743 |  |  | 0.21893 |  |  | 0.27288 |  |  | 0.23096 |  |  | 0.39624 |  |  | 0.071523
[13 empty] | C Non choked w/ reducers | 5 |  | 10.7035 |  |  | 43.0031 |  |  | 131.5148 |  |  | #NUM! |  |  | -511.8471 |  |  | 488.8163 |  |  | 271.2438 |  |  | 262.1183 |  |  | 146.1931 |  |  | 908.1418
[13 empty] | C Choked w/ reducers | 5 |  | 9.5765 |  |  | 37.9991 |  |  | 105.3447 |  |  | 356.2556 |  |  | 809.0628 |  |  | 245.6022 |  |  | 163.8954 |  |  | 137.8622 |  |  | 116.8826 |  |  | 162.5245
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 10.7035 |  |  | 43.0031 |  |  | 131.5148 |  |  | #NUM! |  |  | 809.0628 |  |  | 245.6022 |  |  | 163.8954 |  |  | 137.8622 |  |  | 116.8826 |  |  | 162.5245
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 5.9735 | 2023.9567 |  | 31.4031 | 7864.1837 |  | 108.5148 | 19256.4972 |  | 18000 | 37506.7414 |  | 18000 | 62924.6446 |  | 18000 | 91840.2326 |  | 18000 | 121347.6697 |  | 18000 | 149547.8901 |  | 18000 | 173620.4578 |  | 18000 | 203583.6411
[13 empty] | Next iteration flow rate |  |  | 2064.4358 | Abs Value of | Flow this | 7942.8256 | Abs Value of | Flow this | 19449.0622 | Abs Value of | Flow this | 37881.8088 | Abs Value of | Flow this | 63553.891 | Abs Value of | Flow this | 92758.6349 | Abs Value of | Flow this | 122561.1464 | Abs Value of | Flow this | 151043.369 | Abs Value of | Flow this | 175356.6624 | Abs Value of | Flow this | 205619.4776 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0956 |  |  | 88.2382 |  |  | 78.2866 |  |  | 44.9196 |  |  | -37.3028 |  |  | -181.4431 |  |  | -384.0597 |  |  | -630.1165 |  |  | -880.6883 |  |  | -1244.7251
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4346 |  |  | 0.42564 |  |  | 0.37763 |  |  | 0.21668 |  |  | -0.17994 |  |  | -0.87524 |  |  | -1.8526 |  |  | -3.0395 |  |  | -4.2482 |  |  | -6.0042
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0956 |  |  | 28.2382 |  |  | 18.2866 |  |  | -15.0804 |  |  | -97.3028 |  |  | -241.4431 |  |  | -444.0597 |  |  | -690.1165 |  |  | -940.6883 |  |  | -1304.7251
[13 empty] | Press drop ratio this iteration |  |  | 0.33404 |  |  | 0.32002 |  |  | 0.23359 |  |  | -0.33572 |  |  | 2.6085 |  |  | 1.3307 |  |  | 1.1562 |  |  | 1.0952 |  |  | 1.0681 |  |  | 1.0482
[13 empty] | Expansion factor | 12 |  | 0.82603 |  |  | 0.83337 |  |  | 0.87722 |  |  | 1.179 |  |  | -0.43358 |  |  | 0.22479 |  |  | 0.27532 |  |  | 0.2325 |  |  | 0.39709 |  |  | 0.072444
[13 empty] | C Non choked w/ reducers | 5 |  | 10.9185 |  |  | 43.4647 |  |  | 133.6984 |  |  | #NUM! |  |  | -565.327 |  |  | 468.4155 |  |  | 265.3652 |  |  | 257.322 |  |  | 144.2389 |  |  | 886.8672
[13 empty] | C Choked w/ reducers | 5 |  | 9.7686 |  |  | 38.3962 |  |  | 106.718 |  |  | 366.9697 |  |  | 762.1059 |  |  | 240.7399 |  |  | 161.5064 |  |  | 136.1044 |  |  | 115.487 |  |  | 160.6809
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 10.9185 |  |  | 43.4647 |  |  | 133.6984 |  |  | #NUM! |  |  | 762.1059 |  |  | 240.7399 |  |  | 161.5064 |  |  | 136.1044 |  |  | 115.487 |  |  | 160.6809
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.1885 | 2064.4358 |  | 31.8647 | 7942.8256 |  | 110.6984 | 19449.0622 |  | 18000 | 37881.8088 |  | 18000 | 63553.891 |  | 18000 | 92758.6349 |  | 18000 | 122561.1464 |  | 18000 | 151043.369 |  | 18000 | 175356.6624 |  | 18000 | 205619.4776
[13 empty] | Next iteration flow rate |  |  | 2105.7245 | Abs Value of | Flow this | 8022.2538 | Abs Value of | Flow this | 19643.5528 | Abs Value of | Flow this | 38260.6269 | Abs Value of | Flow this | 64189.4299 | Abs Value of | Flow this | 93686.2213 | Abs Value of | Flow this | 123786.7579 | Abs Value of | Flow this | 152553.8027 | Abs Value of | Flow this | 177110.229 | Abs Value of | Flow this | 207675.6723 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0902 |  |  | 88.1981 |  |  | 78.0465 |  |  | 44.0089 |  |  | -39.8662 |  |  | -186.9037 |  |  | -393.5929 |  |  | -644.5955 |  |  | -900.2038 |  |  | -1271.5577
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43457 |  |  | 0.42545 |  |  | 0.37648 |  |  | 0.21229 |  |  | -0.1923 |  |  | -0.90158 |  |  | -1.8986 |  |  | -3.1094 |  |  | -4.3424 |  |  | -6.1337
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0902 |  |  | 28.1981 |  |  | 18.0465 |  |  | -15.9911 |  |  | -99.8662 |  |  | -246.9037 |  |  | -453.5929 |  |  | -704.5955 |  |  | -960.2038 |  |  | -1331.5577
[13 empty] | Press drop ratio this iteration |  |  | 0.334 |  |  | 0.31971 |  |  | 0.23123 |  |  | -0.36336 |  |  | 2.505 |  |  | 1.321 |  |  | 1.1524 |  |  | 1.0931 |  |  | 1.0667 |  |  | 1.0472
[13 empty] | Expansion factor | 12 |  | 0.82605 |  |  | 0.83353 |  |  | 0.87846 |  |  | 1.1937 |  |  | -0.37674 |  |  | 0.23042 |  |  | 0.27769 |  |  | 0.234 |  |  | 0.39792 |  |  | 0.073344
[13 empty] | C Non choked w/ reducers | 5 |  | 11.1379 |  |  | 43.932 |  |  | 135.9474 |  |  | #NUM! |  |  | -627.4386 |  |  | 449.6941 |  |  | 259.7189 |  |  | 252.6769 |  |  | 142.3229 |  |  | 866.4935
[13 empty] | C Choked w/ reducers | 5 |  | 9.9646 |  |  | 38.7977 |  |  | 108.1167 |  |  | 378.3097 |  |  | 720.2332 |  |  | 236.0434 |  |  | 159.1705 |  |  | 134.3777 |  |  | 114.1132 |  |  | 158.8631
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 11.1379 |  |  | 43.932 |  |  | 135.9474 |  |  | #NUM! |  |  | 720.2332 |  |  | 236.0434 |  |  | 159.1705 |  |  | 134.3777 |  |  | 114.1132 |  |  | 158.8631
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.4079 | 2105.7245 |  | 32.332 | 8022.2538 |  | 112.9474 | 19643.5528 |  | 18000 | 38260.6269 |  | 18000 | 64189.4299 |  | 18000 | 93686.2213 |  | 18000 | 123786.7579 |  | 18000 | 152553.8027 |  | 18000 | 177110.229 |  | 18000 | 207675.6723
[13 empty] | Next iteration flow rate |  |  | 2147.839 | Abs Value of | Flow this | 8102.4763 | Abs Value of | Flow this | 19839.9883 | Abs Value of | Flow this | 38643.2332 | Abs Value of | Flow this | 64831.3242 | Abs Value of | Flow this | 94623.0835 | Abs Value of | Flow this | 125024.6255 | Abs Value of | Flow this | 154079.3408 | Abs Value of | Flow this | 178881.3313 | Abs Value of | Flow this | 209752.4291 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0845 |  |  | 88.1573 |  |  | 77.8016 |  |  | 43.0798 |  |  | -42.4812 |  |  | -192.4741 |  |  | -403.3178 |  |  | -659.3655 |  |  | -920.1115 |  |  | -1298.9297
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43455 |  |  | 0.42525 |  |  | 0.3753 |  |  | 0.20781 |  |  | -0.20492 |  |  | -0.92845 |  |  | -1.9455 |  |  | -3.1806 |  |  | -4.4384 |  |  | -6.2657
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0845 |  |  | 28.1573 |  |  | 17.8016 |  |  | -16.9202 |  |  | -102.4812 |  |  | -252.4741 |  |  | -463.3178 |  |  | -719.3655 |  |  | -980.1115 |  |  | -1358.9297
[13 empty] | Press drop ratio this iteration |  |  | 0.33396 |  |  | 0.3194 |  |  | 0.22881 |  |  | -0.39276 |  |  | 2.4124 |  |  | 1.3117 |  |  | 1.1488 |  |  | 1.091 |  |  | 1.0652 |  |  | 1.0462
[13 empty] | Expansion factor | 12 |  | 0.82607 |  |  | 0.83369 |  |  | 0.87973 |  |  | 1.2094 |  |  | -0.32582 |  |  | 0.23583 |  |  | 0.28 |  |  | 0.23546 |  |  | 0.39874 |  |  | 0.074224
[13 empty] | C Non choked w/ reducers | 5 |  | 11.3618 |  |  | 44.4051 |  |  | 138.2653 |  |  | #NUM! |  |  | -700.7164 |  |  | 432.4473 |  |  | 254.2907 |  |  | 248.1756 |  |  | 140.4439 |  |  | 846.9626
[13 empty] | C Choked w/ reducers | 5 |  | 10.1645 |  |  | 39.2039 |  |  | 109.5416 |  |  | 390.3329 |  |  | 682.6581 |  |  | 231.5042 |  |  | 156.8859 |  |  | 132.6812 |  |  | 112.7607 |  |  | 157.0706
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 11.3618 |  |  | 44.4051 |  |  | 138.2653 |  |  | #NUM! |  |  | 682.6581 |  |  | 231.5042 |  |  | 156.8859 |  |  | 132.6812 |  |  | 112.7607 |  |  | 157.0706
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.6318 | 2147.839 |  | 32.8051 | 8102.4763 |  | 115.2653 | 19839.9883 |  | 18000 | 38643.2332 |  | 18000 | 64831.3242 |  | 18000 | 94623.0835 |  | 18000 | 125024.6255 |  | 18000 | 154079.3408 |  | 18000 | 178881.3313 |  | 18000 | 209752.4291
[13 empty] | Next iteration flow rate |  |  | 2190.7958 | Abs Value of | Flow this | 8183.5011 | Abs Value of | Flow this | 20038.3882 | Abs Value of | Flow this | 39029.6655 | Abs Value of | Flow this | 65479.6375 | Abs Value of | Flow this | 95569.3143 | Abs Value of | Flow this | 126274.8717 | Abs Value of | Flow this | 155620.1342 | Abs Value of | Flow this | 180670.1446 | Abs Value of | Flow this | 211849.9533 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0786 |  |  | 88.1156 |  |  | 77.5518 |  |  | 42.1321 |  |  | -45.1487 |  |  | -198.1565 |  |  | -413.2381 |  |  | -674.4323 |  |  | -940.4193 |  |  | -1326.8518
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43452 |  |  | 0.42505 |  |  | 0.37409 |  |  | 0.20323 |  |  | -0.21779 |  |  | -0.95586 |  |  | -1.9934 |  |  | -3.2533 |  |  | -4.5363 |  |  | -6.4004
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0786 |  |  | 28.1156 |  |  | 17.5518 |  |  | -17.8679 |  |  | -105.1487 |  |  | -258.1565 |  |  | -473.2381 |  |  | -734.4323 |  |  | -1000.4193 |  |  | -1386.8518
[13 empty] | Press drop ratio this iteration |  |  | 0.33392 |  |  | 0.31908 |  |  | 0.22632 |  |  | -0.42409 |  |  | 2.3289 |  |  | 1.3028 |  |  | 1.1452 |  |  | 1.089 |  |  | 1.0638 |  |  | 1.0452
[13 empty] | Expansion factor | 12 |  | 0.82609 |  |  | 0.83386 |  |  | 0.88103 |  |  | 1.2261 |  |  | -0.27996 |  |  | 0.24104 |  |  | 0.28223 |  |  | 0.23688 |  |  | 0.39953 |  |  | 0.075084
[13 empty] | C Non choked w/ reducers | 5 |  | 11.5903 |  |  | 44.8839 |  |  | 140.6558 |  |  | #NUM! |  |  | -788.7574 |  |  | 416.5024 |  |  | 249.0674 |  |  | 243.8112 |  |  | 138.6008 |  |  | 828.2217
[13 empty] | C Choked w/ reducers | 5 |  | 10.3685 |  |  | 39.6146 |  |  | 110.9934 |  |  | 403.1042 |  |  | 648.7481 |  |  | 227.1142 |  |  | 154.6508 |  |  | 131.0143 |  |  | 111.4289 |  |  | 155.3028
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 11.5903 |  |  | 44.8839 |  |  | 140.6558 |  |  | #NUM! |  |  | 648.7481 |  |  | 227.1142 |  |  | 154.6508 |  |  | 131.0143 |  |  | 111.4289 |  |  | 155.3028
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 6.8603 | 2190.7958 |  | 33.2839 | 8183.5011 |  | 117.6558 | 20038.3882 |  | 18000 | 39029.6655 |  | 18000 | 65479.6375 |  | 18000 | 95569.3143 |  | 18000 | 126274.8717 |  | 18000 | 155620.1342 |  | 18000 | 180670.1446 |  | 18000 | 211849.9533
[13 empty] | Next iteration flow rate |  |  | 2234.6117 | Abs Value of | Flow this | 8265.3361 | Abs Value of | Flow this | 20238.7721 | Abs Value of | Flow this | 39419.9622 | Abs Value of | Flow this | 66134.4339 | Abs Value of | Flow this | 96525.0075 | Abs Value of | Flow this | 127537.6204 | Abs Value of | Flow this | 157176.3355 | Abs Value of | Flow this | 182476.8461 | Abs Value of | Flow this | 213968.4529 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0725 |  |  | 88.0731 |  |  | 77.297 |  |  | 41.1653 |  |  | -47.8698 |  |  | -203.9531 |  |  | -423.3578 |  |  | -689.802 |  |  | -961.1354 |  |  | -1355.3351
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43449 |  |  | 0.42484 |  |  | 0.37286 |  |  | 0.19857 |  |  | -0.23091 |  |  | -0.98382 |  |  | -2.0422 |  |  | -3.3274 |  |  | -4.6363 |  |  | -6.5378
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0725 |  |  | 28.0731 |  |  | 17.297 |  |  | -18.8347 |  |  | -107.8698 |  |  | -263.9531 |  |  | -483.3578 |  |  | -749.802 |  |  | -1021.1354 |  |  | -1415.3351
[13 empty] | Press drop ratio this iteration |  |  | 0.33387 |  |  | 0.31875 |  |  | 0.22377 |  |  | -0.45754 |  |  | 2.2534 |  |  | 1.2942 |  |  | 1.1417 |  |  | 1.087 |  |  | 1.0624 |  |  | 1.0443
[13 empty] | Expansion factor | 12 |  | 0.82612 |  |  | 0.83403 |  |  | 0.88237 |  |  | 1.2439 |  |  | -0.23844 |  |  | 0.24605 |  |  | 0.28441 |  |  | 0.23827 |  |  | 0.40031 |  |  | 0.075925
[13 empty] | C Non choked w/ reducers | 5 |  | 11.8233 |  |  | 45.3687 |  |  | 143.123 |  |  | #NUM! |  |  | -896.8506 |  |  | 401.7129 |  |  | 244.037 |  |  | 239.5771 |  |  | 136.7924 |  |  | 810.2222
[13 empty] | C Choked w/ reducers | 5 |  | 10.5766 |  |  | 40.0301 |  |  | 112.4729 |  |  | 416.6968 |  |  | 617.9893 |  |  | 222.866 |  |  | 152.4637 |  |  | 129.3761 |  |  | 110.1175 |  |  | 153.5594
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 11.8233 |  |  | 45.3687 |  |  | 143.123 |  |  | #NUM! |  |  | 617.9893 |  |  | 222.866 |  |  | 152.4637 |  |  | 129.3761 |  |  | 110.1175 |  |  | 153.5594
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.0933 | 2234.6117 |  | 33.7687 | 8265.3361 |  | 120.123 | 20238.7721 |  | 18000 | 39419.9622 |  | 18000 | 66134.4339 |  | 18000 | 96525.0075 |  | 18000 | 127537.6204 |  | 18000 | 157176.3355 |  | 18000 | 182476.8461 |  | 18000 | 213968.4529
[13 empty] | Next iteration flow rate |  |  | 2279.3039 | Abs Value of | Flow this | 8347.9895 | Abs Value of | Flow this | 20441.1598 | Abs Value of | Flow this | 39814.1618 | Abs Value of | Flow this | 66795.7782 | Abs Value of | Flow this | 97490.2575 | Abs Value of | Flow this | 128812.9966 | Abs Value of | Flow this | 158748.0989 | Abs Value of | Flow this | 184301.6145 | Abs Value of | Flow this | 216108.1374 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0661 |  |  | 88.0298 |  |  | 77.037 |  |  | 40.1791 |  |  | -50.6456 |  |  | -209.8661 |  |  | -433.6809 |  |  | -705.4807 |  |  | -982.2679 |  |  | -1384.391
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43446 |  |  | 0.42463 |  |  | 0.37161 |  |  | 0.19381 |  |  | -0.2443 |  |  | -1.0123 |  |  | -2.092 |  |  | -3.4031 |  |  | -4.7382 |  |  | -6.678
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0661 |  |  | 28.0298 |  |  | 17.037 |  |  | -19.8209 |  |  | -110.6456 |  |  | -269.8661 |  |  | -493.6809 |  |  | -765.4807 |  |  | -1042.2679 |  |  | -1444.391
[13 empty] | Press drop ratio this iteration |  |  | 0.33382 |  |  | 0.31841 |  |  | 0.22115 |  |  | -0.49331 |  |  | 2.1847 |  |  | 1.2859 |  |  | 1.1384 |  |  | 1.085 |  |  | 1.0611 |  |  | 1.0433
[13 empty] | Expansion factor | 12 |  | 0.82614 |  |  | 0.83421 |  |  | 0.88375 |  |  | 1.263 |  |  | -0.20069 |  |  | 0.25088 |  |  | 0.28652 |  |  | 0.23963 |  |  | 0.40107 |  |  | 0.076747
[13 empty] | C Non choked w/ reducers | 5 |  | 12.0611 |  |  | 45.8595 |  |  | 145.6711 |  |  | #NUM! |  |  | -1033.1113 |  |  | 387.9534 |  |  | 239.1884 |  |  | 235.4672 |  |  | 135.0178 |  |  | 792.9194
[13 empty] | C Choked w/ reducers | 5 |  | 10.7889 |  |  | 40.4503 |  |  | 113.981 |  |  | 431.194 |  |  | 589.9594 |  |  | 218.7525 |  |  | 150.3229 |  |  | 127.7658 |  |  | 108.8259 |  |  | 151.8399
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 12.0611 |  |  | 45.8595 |  |  | 145.6711 |  |  | #NUM! |  |  | 589.9594 |  |  | 218.7525 |  |  | 150.3229 |  |  | 127.7658 |  |  | 108.8259 |  |  | 151.8399
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.3311 | 2279.3039 |  | 34.2595 | 8347.9895 |  | 122.6711 | 20441.1598 |  | 18000 | 39814.1618 |  | 18000 | 66795.7782 |  | 18000 | 97490.2575 |  | 18000 | 128812.9966 |  | 18000 | 158748.0989 |  | 18000 | 184301.6145 |  | 18000 | 216108.1374
[13 empty] | Next iteration flow rate |  |  | 2324.89 | Abs Value of | Flow this | 8431.4694 | Abs Value of | Flow this | 20645.5714 | Abs Value of | Flow this | 40212.3034 | Abs Value of | Flow this | 67463.736 | Abs Value of | Flow this | 98465.1601 | Abs Value of | Flow this | 130101.1266 | Abs Value of | Flow this | 160335.5799 | Abs Value of | Flow this | 186144.6307 | Abs Value of | Flow this | 218269.2188 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0595 |  |  | 87.9855 |  |  | 76.7718 |  |  | 39.1731 |  |  | -53.4772 |  |  | -215.8981 |  |  | -444.2115 |  |  | -721.4745 |  |  | -1003.8251 |  |  | -1414.0309
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43442 |  |  | 0.42442 |  |  | 0.37033 |  |  | 0.18896 |  |  | -0.25796 |  |  | -1.0414 |  |  | -2.1428 |  |  | -3.4802 |  |  | -4.8422 |  |  | -6.8209
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0595 |  |  | 27.9855 |  |  | 16.7718 |  |  | -20.8269 |  |  | -113.4772 |  |  | -275.8981 |  |  | -504.2115 |  |  | -781.4745 |  |  | -1063.8251 |  |  | -1474.0309
[13 empty] | Press drop ratio this iteration |  |  | 0.33377 |  |  | 0.31807 |  |  | 0.21846 |  |  | -0.53166 |  |  | 2.122 |  |  | 1.2779 |  |  | 1.1351 |  |  | 1.0832 |  |  | 1.0598 |  |  | 1.0424
[13 empty] | Expansion factor | 12 |  | 0.82617 |  |  | 0.83438 |  |  | 0.88517 |  |  | 1.2834 |  |  | -0.16621 |  |  | 0.25553 |  |  | 0.28858 |  |  | 0.24095 |  |  | 0.40181 |  |  | 0.077551
[13 empty] | C Non choked w/ reducers | 5 |  | 12.3038 |  |  | 46.3564 |  |  | 148.305 |  |  | #NUM! |  |  | -1210.6678 |  |  | 375.1164 |  |  | 234.5113 |  |  | 231.4758 |  |  | 133.276 |  |  | 776.2721
[13 empty] | C Choked w/ reducers | 5 |  | 11.0054 |  |  | 40.8753 |  |  | 115.5184 |  |  | 446.6904 |  |  | 564.3084 |  |  | 214.7672 |  |  | 148.2269 |  |  | 126.1828 |  |  | 107.5538 |  |  | 150.1437
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 12.3038 |  |  | 46.3564 |  |  | 148.305 |  |  | #NUM! |  |  | 564.3084 |  |  | 214.7672 |  |  | 148.2269 |  |  | 126.1828 |  |  | 107.5538 |  |  | 150.1437
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.5738 | 2324.89 |  | 34.7564 | 8431.4694 |  | 125.305 | 20645.5714 |  | 18000 | 40212.3034 |  | 18000 | 67463.736 |  | 18000 | 98465.1601 |  | 18000 | 130101.1266 |  | 18000 | 160335.5799 |  | 18000 | 186144.6307 |  | 18000 | 218269.2188
[13 empty] | Next iteration flow rate |  |  | 2371.3878 | Abs Value of | Flow this | 8515.7841 | Abs Value of | Flow this | 20852.0271 | Abs Value of | Flow this | 40614.4265 | Abs Value of | Flow this | 68138.3733 | Abs Value of | Flow this | 99449.8117 | Abs Value of | Flow this | 131402.1379 | Abs Value of | Flow this | 161938.9357 | Abs Value of | Flow this | 188006.077 | Abs Value of | Flow this | 220451.911 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0526 |  |  | 87.9404 |  |  | 76.5013 |  |  | 38.1468 |  |  | -56.3657 |  |  | -222.0512 |  |  | -454.9538 |  |  | -737.7897 |  |  | -1025.8156 |  |  | -1444.2665
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43439 |  |  | 0.4242 |  |  | 0.36902 |  |  | 0.18401 |  |  | -0.27189 |  |  | -1.0711 |  |  | -2.1946 |  |  | -3.5589 |  |  | -4.9483 |  |  | -6.9668
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0526 |  |  | 27.9404 |  |  | 16.5013 |  |  | -21.8532 |  |  | -116.3657 |  |  | -282.0512 |  |  | -514.9538 |  |  | -797.7897 |  |  | -1085.8156 |  |  | -1504.2665
[13 empty] | Press drop ratio this iteration |  |  | 0.33372 |  |  | 0.31772 |  |  | 0.2157 |  |  | -0.57287 |  |  | 2.0645 |  |  | 1.2702 |  |  | 1.1319 |  |  | 1.0813 |  |  | 1.0585 |  |  | 1.0415
[13 empty] | Expansion factor | 12 |  | 0.82619 |  |  | 0.83457 |  |  | 0.88662 |  |  | 1.3054 |  |  | -0.13461 |  |  | 0.26002 |  |  | 0.29058 |  |  | 0.24224 |  |  | 0.40253 |  |  | 0.078337
[13 empty] | C Non choked w/ reducers | 5 |  | 12.5514 |  |  | 46.8596 |  |  | 151.0297 |  |  | #NUM! |  |  | -1452.2485 |  |  | 363.1087 |  |  | 229.9963 |  |  | 227.5976 |  |  | 131.566 |  |  | 760.2424
[13 empty] | C Choked w/ reducers | 5 |  | 11.2264 |  |  | 41.3053 |  |  | 117.0862 |  |  | 463.2946 |  |  | 540.7438 |  |  | 210.904 |  |  | 146.1742 |  |  | 124.6264 |  |  | 106.3006 |  |  | 148.4704
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 12.5514 |  |  | 46.8596 |  |  | 151.0297 |  |  | #NUM! |  |  | 540.7438 |  |  | 210.904 |  |  | 146.1742 |  |  | 124.6264 |  |  | 106.3006 |  |  | 148.4704
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 7.8214 | 2371.3878 |  | 35.2596 | 8515.7841 |  | 128.0297 | 20852.0271 |  | 18000 | 40614.4265 |  | 18000 | 68138.3733 |  | 18000 | 99449.8117 |  | 18000 | 131402.1379 |  | 18000 | 161938.9357 |  | 18000 | 188006.077 |  | 18000 | 220451.911
[13 empty] | Next iteration flow rate |  |  | 2418.8156 | Abs Value of | Flow this | 8600.9419 | Abs Value of | Flow this | 21060.5474 | Abs Value of | Flow this | 41020.5707 | Abs Value of | Flow this | 68819.7571 | Abs Value of | Flow this | 100444.3098 | Abs Value of | Flow this | 132716.1593 | Abs Value of | Flow this | 163558.325 | Abs Value of | Flow this | 189886.1377 | Abs Value of | Flow this | 222656.4301 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0454 |  |  | 87.8944 |  |  | 76.2254 |  |  | 37.1 |  |  | -59.3123 |  |  | -228.3281 |  |  | -465.912 |  |  | -754.4329 |  |  | -1048.2481 |  |  | -1475.1099
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43436 |  |  | 0.42398 |  |  | 0.36769 |  |  | 0.17896 |  |  | -0.28611 |  |  | -1.1014 |  |  | -2.2474 |  |  | -3.6392 |  |  | -5.0565 |  |  | -7.1156
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0454 |  |  | 27.8944 |  |  | 16.2254 |  |  | -22.9 |  |  | -119.3123 |  |  | -288.3281 |  |  | -525.912 |  |  | -814.4329 |  |  | -1108.2481 |  |  | -1535.1099
[13 empty] | Press drop ratio this iteration |  |  | 0.33367 |  |  | 0.31736 |  |  | 0.21286 |  |  | -0.61725 |  |  | 2.0116 |  |  | 1.2628 |  |  | 1.1288 |  |  | 1.0795 |  |  | 1.0572 |  |  | 1.0407
[13 empty] | Expansion factor | 12 |  | 0.82622 |  |  | 0.83475 |  |  | 0.88811 |  |  | 1.329 |  |  | -0.10555 |  |  | 0.26434 |  |  | 0.29252 |  |  | 0.24349 |  |  | 0.40324 |  |  | 0.079106
[13 empty] | C Non choked w/ reducers | 5 |  | 12.804 |  |  | 47.369 |  |  | 153.8509 |  |  | #NUM! |  |  | -1800.9303 |  |  | 351.8497 |  |  | 225.6345 |  |  | 223.8275 |  |  | 129.887 |  |  | 744.7954
[13 empty] | C Choked w/ reducers | 5 |  | 11.4519 |  |  | 41.7402 |  |  | 118.6852 |  |  | 481.1314 |  |  | 519.0189 |  |  | 207.1572 |  |  | 144.1636 |  |  | 123.0958 |  |  | 105.066 |  |  | 146.8197
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 12.804 |  |  | 47.369 |  |  | 153.8509 |  |  | #NUM! |  |  | 519.0189 |  |  | 207.1572 |  |  | 144.1636 |  |  | 123.0958 |  |  | 105.066 |  |  | 146.8197
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.074 | 2418.8156 |  | 35.769 | 8600.9419 |  | 130.8509 | 21060.5474 |  | 18000 | 41020.5707 |  | 18000 | 68819.7571 |  | 18000 | 100444.3098 |  | 18000 | 132716.1593 |  | 18000 | 163558.325 |  | 18000 | 189886.1377 |  | 18000 | 222656.4301
[13 empty] | Next iteration flow rate |  |  | 2467.1919 | Abs Value of | Flow this | 8686.9513 | Abs Value of | Flow this | 21271.1529 | Abs Value of | Flow this | 41430.7764 | Abs Value of | Flow this | 69507.9546 | Abs Value of | Flow this | 101448.7529 | Abs Value of | Flow this | 134043.3208 | Abs Value of | Flow this | 165193.9083 | Abs Value of | Flow this | 191784.9991 | Abs Value of | Flow this | 224882.9944 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.038 |  |  | 87.8475 |  |  | 75.9439 |  |  | 36.032 |  |  | -62.3181 |  |  | -234.7311 |  |  | -477.0905 |  |  | -771.4107 |  |  | -1071.1315 |  |  | -1506.5732
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43432 |  |  | 0.42375 |  |  | 0.36633 |  |  | 0.17381 |  |  | -0.30061 |  |  | -1.1323 |  |  | -2.3014 |  |  | -3.7211 |  |  | -5.1669 |  |  | -7.2673
[13 empty] | Delta P at this iteration flow rate |  |  | 30.038 |  |  | 27.8475 |  |  | 15.9439 |  |  | -23.968 |  |  | -122.3181 |  |  | -294.7311 |  |  | -537.0905 |  |  | -831.4107 |  |  | -1131.1315 |  |  | -1566.5732
[13 empty] | Press drop ratio this iteration |  |  | 0.33361 |  |  | 0.317 |  |  | 0.20994 |  |  | -0.66518 |  |  | 1.9628 |  |  | 1.2556 |  |  | 1.1258 |  |  | 1.0778 |  |  | 1.056 |  |  | 1.0398
[13 empty] | Expansion factor | 12 |  | 0.82625 |  |  | 0.83494 |  |  | 0.88964 |  |  | 1.3546 |  |  | -0.078735 |  |  | 0.26852 |  |  | 0.29441 |  |  | 0.24472 |  |  | 0.40393 |  |  | 0.079857
[13 empty] | C Non choked w/ reducers | 5 |  | 13.0618 |  |  | 47.8849 |  |  | 156.7746 |  |  | #NUM! |  |  | -2349.4948 |  |  | 341.2686 |  |  | 221.4178 |  |  | 220.1607 |  |  | 128.238 |  |  | 729.8985
[13 empty] | C Choked w/ reducers | 5 |  | 11.6819 |  |  | 42.1801 |  |  | 120.3163 |  |  | 500.3451 |  |  | 498.9248 |  |  | 203.5214 |  |  | 142.1936 |  |  | 121.5905 |  |  | 103.8496 |  |  | 145.191
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 13.0618 |  |  | 47.8849 |  |  | 156.7746 |  |  | #NUM! |  |  | 498.9248 |  |  | 203.5214 |  |  | 142.1936 |  |  | 121.5905 |  |  | 103.8496 |  |  | 145.191
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.3318 | 2467.1919 |  | 36.2849 | 8686.9513 |  | 133.7746 | 21271.1529 |  | 18000 | 41430.7764 |  | 18000 | 69507.9546 |  | 18000 | 101448.7529 |  | 18000 | 134043.3208 |  | 18000 | 165193.9083 |  | 18000 | 191784.9991 |  | 18000 | 224882.9944
[13 empty] | Next iteration flow rate |  |  | 2516.5357 | Abs Value of | Flow this | 8773.8208 | Abs Value of | Flow this | 21483.8644 | Abs Value of | Flow this | 41845.0842 | Abs Value of | Flow this | 70203.0342 | Abs Value of | Flow this | 102463.2405 | Abs Value of | Flow this | 135383.7541 | Abs Value of | Flow this | 166845.8473 | Abs Value of | Flow this | 193702.8491 | Abs Value of | Flow this | 227131.8243 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0302 |  |  | 87.7996 |  |  | 75.6567 |  |  | 34.9427 |  |  | -65.3843 |  |  | -241.2628 |  |  | -488.4936 |  |  | -788.7297 |  |  | -1094.4749 |  |  | -1538.669
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43428 |  |  | 0.42352 |  |  | 0.36495 |  |  | 0.16855 |  |  | -0.3154 |  |  | -1.1638 |  |  | -2.3564 |  |  | -3.8046 |  |  | -5.2795 |  |  | -7.4222
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0302 |  |  | 27.7996 |  |  | 15.6567 |  |  | -25.0573 |  |  | -125.3843 |  |  | -301.2628 |  |  | -548.4936 |  |  | -848.7297 |  |  | -1154.4749 |  |  | -1598.669
[13 empty] | Press drop ratio this iteration |  |  | 0.33356 |  |  | 0.31663 |  |  | 0.20694 |  |  | -0.7171 |  |  | 1.9177 |  |  | 1.2487 |  |  | 1.1228 |  |  | 1.0761 |  |  | 1.0548 |  |  | 1.039
[13 empty] | Expansion factor | 12 |  | 0.82628 |  |  | 0.83514 |  |  | 0.89122 |  |  | 1.3823 |  |  | -0.053921 |  |  | 0.27255 |  |  | 0.29625 |  |  | 0.24592 |  |  | 0.4046 |  |  | 0.080592
[13 empty] | C Non choked w/ reducers | 5 |  | 13.3249 |  |  | 48.4074 |  |  | 159.8076 |  |  | #NUM! |  |  | -3341.2075 |  |  | 331.3036 |  |  | 217.3387 |  |  | 216.5929 |  |  | 126.6183 |  |  | 715.5219
[13 empty] | C Choked w/ reducers | 5 |  | 11.9165 |  |  | 42.6251 |  |  | 121.9807 |  |  | 521.1034 |  |  | 480.2828 |  |  | 199.9916 |  |  | 140.2631 |  |  | 120.1098 |  |  | 102.651 |  |  | 143.5841
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 13.3249 |  |  | 48.4074 |  |  | 159.8076 |  |  | #NUM! |  |  | 480.2828 |  |  | 199.9916 |  |  | 140.2631 |  |  | 120.1098 |  |  | 102.651 |  |  | 143.5841
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.5949 | 2516.5357 |  | 36.8074 | 8773.8208 |  | 136.8076 | 21483.8644 |  | 18000 | 41845.0842 |  | 18000 | 70203.0342 |  | 18000 | 102463.2405 |  | 18000 | 135383.7541 |  | 18000 | 166845.8473 |  | 18000 | 193702.8491 |  | 18000 | 227131.8243
[13 empty] | Next iteration flow rate |  |  | 2566.8664 | Abs Value of | Flow this | 8861.5591 | Abs Value of | Flow this | 21698.703 | Abs Value of | Flow this | 42263.535 | Abs Value of | Flow this | 70905.0645 | Abs Value of | Flow this | 103487.8729 | Abs Value of | Flow this | 136737.5916 | Abs Value of | Flow this | 168514.3058 | Abs Value of | Flow this | 195639.8776 | Abs Value of | Flow this | 229403.1426 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0221 |  |  | 87.7507 |  |  | 75.3638 |  |  | 33.8314 |  |  | -68.5121 |  |  | -247.9259 |  |  | -500.1259 |  |  | -806.3967 |  |  | -1118.2874 |  |  | -1571.4099
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43424 |  |  | 0.42329 |  |  | 0.36354 |  |  | 0.16319 |  |  | -0.33049 |  |  | -1.1959 |  |  | -2.4125 |  |  | -3.8899 |  |  | -5.3943 |  |  | -7.5801
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0221 |  |  | 27.7507 |  |  | 15.3638 |  |  | -26.1686 |  |  | -128.5121 |  |  | -307.9259 |  |  | -560.1259 |  |  | -866.3967 |  |  | -1178.2874 |  |  | -1631.4099
[13 empty] | Press drop ratio this iteration |  |  | 0.3335 |  |  | 0.31624 |  |  | 0.20386 |  |  | -0.7735 |  |  | 1.8758 |  |  | 1.242 |  |  | 1.12 |  |  | 1.0744 |  |  | 1.0537 |  |  | 1.0382
[13 empty] | Expansion factor | 12 |  | 0.82631 |  |  | 0.83534 |  |  | 0.89284 |  |  | 1.4123 |  |  | -0.030896 |  |  | 0.27645 |  |  | 0.29804 |  |  | 0.24709 |  |  | 0.40526 |  |  | 0.081311
[13 empty] | C Non choked w/ reducers | 5 |  | 13.5933 |  |  | 48.9365 |  |  | 162.9572 |  |  | #NUM! |  |  | -5683.0484 |  |  | 321.9002 |  |  | 213.39 |  |  | 213.1199 |  |  | 125.027 |  |  | 701.6375
[13 empty] | C Choked w/ reducers | 5 |  | 12.1559 |  |  | 43.0753 |  |  | 123.6794 |  |  | 543.6026 |  |  | 462.9396 |  |  | 196.563 |  |  | 138.3707 |  |  | 118.6532 |  |  | 101.4699 |  |  | 141.9984
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 13.5933 |  |  | 48.9365 |  |  | 162.9572 |  |  | #NUM! |  |  | 462.9396 |  |  | 196.563 |  |  | 138.3707 |  |  | 118.6532 |  |  | 101.4699 |  |  | 141.9984
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 8.8633 | 2566.8664 |  | 37.3365 | 8861.5591 |  | 139.9572 | 21698.703 |  | 18000 | 42263.535 |  | 18000 | 70905.0645 |  | 18000 | 103487.8729 |  | 18000 | 136737.5916 |  | 18000 | 168514.3058 |  | 18000 | 195639.8776 |  | 18000 | 229403.1426
[13 empty] | Next iteration flow rate |  |  | 2618.2038 | Abs Value of | Flow this | 8950.1746 | Abs Value of | Flow this | 21915.6901 | Abs Value of | Flow this | 42686.1704 | Abs Value of | Flow this | 71614.1152 | Abs Value of | Flow this | 104522.7516 | Abs Value of | Flow this | 138104.9675 | Abs Value of | Flow this | 170199.4489 | Abs Value of | Flow this | 197596.2764 | Abs Value of | Flow this | 231697.174 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.0137 |  |  | 87.7009 |  |  | 75.065 |  |  | 32.6978 |  |  | -71.7029 |  |  | -254.7228 |  |  | -511.9921 |  |  | -824.4189 |  |  | -1142.5787 |  |  | -1604.8088
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4342 |  |  | 0.42305 |  |  | 0.36209 |  |  | 0.15773 |  |  | -0.34588 |  |  | -1.2287 |  |  | -2.4697 |  |  | -3.9768 |  |  | -5.5115 |  |  | -7.7412
[13 empty] | Delta P at this iteration flow rate |  |  | 30.0137 |  |  | 27.7009 |  |  | 15.065 |  |  | -27.3022 |  |  | -131.7029 |  |  | -314.7228 |  |  | -571.9921 |  |  | -884.4189 |  |  | -1202.5787 |  |  | -1664.8088
[13 empty] | Press drop ratio this iteration |  |  | 0.33344 |  |  | 0.31586 |  |  | 0.20069 |  |  | -0.83499 |  |  | 1.8368 |  |  | 1.2356 |  |  | 1.1172 |  |  | 1.0728 |  |  | 1.0525 |  |  | 1.0374
[13 empty] | Expansion factor | 12 |  | 0.82634 |  |  | 0.83554 |  |  | 0.89451 |  |  | 1.4451 |  |  | -0.0094781 |  |  | 0.28021 |  |  | 0.29979 |  |  | 0.24823 |  |  | 0.40591 |  |  | 0.082015
[13 empty] | C Non choked w/ reducers | 5 |  | 13.8672 |  |  | 49.4724 |  |  | 166.2314 |  |  | #NUM! |  |  | -18066.3697 |  |  | 313.0101 |  |  | 209.5653 |  |  | 209.7376 |  |  | 123.4635 |  |  | 688.2195
[13 empty] | C Choked w/ reducers | 5 |  | 12.4002 |  |  | 43.5308 |  |  | 125.4134 |  |  | 568.0735 |  |  | 446.7625 |  |  | 193.2312 |  |  | 136.5154 |  |  | 117.2199 |  |  | 100.3057 |  |  | 140.4335
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 13.8672 |  |  | 49.4724 |  |  | 166.2314 |  |  | #NUM! |  |  | 446.7625 |  |  | 193.2312 |  |  | 136.5154 |  |  | 117.2199 |  |  | 100.3057 |  |  | 140.4335
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.1372 | 2618.2038 |  | 37.8724 | 8950.1746 |  | 143.2314 | 21915.6901 |  | 18000 | 42686.1704 |  | 18000 | 71614.1152 |  | 18000 | 104522.7516 |  | 18000 | 138104.9675 |  | 18000 | 170199.4489 |  | 18000 | 197596.2764 |  | 18000 | 231697.174
[13 empty] | Next iteration flow rate |  |  | 2670.5678 | Abs Value of | Flow this | 9039.6764 | Abs Value of | Flow this | 22134.847 | Abs Value of | Flow this | 43113.0321 | Abs Value of | Flow this | 72330.2563 | Abs Value of | Flow this | 105567.9791 | Abs Value of | Flow this | 139486.0172 | Abs Value of | Flow this | 171901.4434 | Abs Value of | Flow this | 199572.2391 | Abs Value of | Flow this | 234014.1457 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 90.005 |  |  | 87.65 |  |  | 74.7601 |  |  | 31.5414 |  |  | -74.9577 |  |  | -261.6563 |  |  | -524.0968 |  |  | -842.8034 |  |  | -1167.3581 |  |  | -1638.8791
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43416 |  |  | 0.4228 |  |  | 0.36062 |  |  | 0.15215 |  |  | -0.36158 |  |  | -1.2622 |  |  | -2.5281 |  |  | -4.0655 |  |  | -5.631 |  |  | -7.9055
[13 empty] | Delta P at this iteration flow rate |  |  | 30.005 |  |  | 27.65 |  |  | 14.7601 |  |  | -28.4586 |  |  | -134.9577 |  |  | -321.6563 |  |  | -584.0968 |  |  | -902.8034 |  |  | -1227.3581 |  |  | -1698.8791
[13 empty] | Press drop ratio this iteration |  |  | 0.33337 |  |  | 0.31546 |  |  | 0.19743 |  |  | -0.90226 |  |  | 1.8005 |  |  | 1.2293 |  |  | 1.1145 |  |  | 1.0712 |  |  | 1.0514 |  |  | 1.0366
[13 empty] | Expansion factor | 12 |  | 0.82638 |  |  | 0.83574 |  |  | 0.89622 |  |  | 1.481 |  |  | 0.010491 |  |  | 0.28384 |  |  | 0.30148 |  |  | 0.24934 |  |  | 0.40653 |  |  | 0.082702
[13 empty] | C Non choked w/ reducers | 5 |  | 14.1467 |  |  | 50.0151 |  |  | 169.6391 |  |  | #NUM! |  |  | 15927.2096 |  |  | 304.5905 |  |  | 205.8584 |  |  | 206.4424 |  |  | 121.9268 |  |  | 675.2438
[13 empty] | C Choked w/ reducers | 5 |  | 12.6495 |  |  | 43.9916 |  |  | 127.184 |  |  | 594.7898 |  |  | 431.6366 |  |  | 189.9919 |  |  | 134.6961 |  |  | 115.8096 |  |  | 99.1583 |  |  | 138.8892
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 14.1467 |  |  | 50.0151 |  |  | 169.6391 |  |  | #NUM! |  |  | 431.6366 |  |  | 189.9919 |  |  | 134.6961 |  |  | 115.8096 |  |  | 99.1583 |  |  | 138.8892
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.4167 | 2670.5678 |  | 38.4151 | 9039.6764 |  | 146.6391 | 22134.847 |  | 18000 | 43113.0321 |  | 18000 | 72330.2563 |  | 18000 | 105567.9791 |  | 18000 | 139486.0172 |  | 18000 | 171901.4434 |  | 18000 | 199572.2391 |  | 18000 | 234014.1457
[13 empty] | Next iteration flow rate |  |  | 2723.9792 | Abs Value of | Flow this | 9130.0732 | Abs Value of | Flow this | 22356.1955 | Abs Value of | Flow this | 43544.1624 | Abs Value of | Flow this | 73053.5589 | Abs Value of | Flow this | 106623.6589 | Abs Value of | Flow this | 140880.8774 | Abs Value of | Flow this | 173620.4578 | Abs Value of | Flow this | 201567.9615 | Abs Value of | Flow this | 236354.2872 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9959 |  |  | 87.5982 |  |  | 74.4492 |  |  | 30.3617 |  |  | -78.278 |  |  | -268.7293 |  |  | -536.4447 |  |  | -861.5574 |  |  | -1192.6356 |  |  | -1673.6342
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43412 |  |  | 0.42255 |  |  | 0.35912 |  |  | 0.14646 |  |  | -0.37759 |  |  | -1.2963 |  |  | -2.5877 |  |  | -4.1559 |  |  | -5.753 |  |  | -8.0732
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9959 |  |  | 27.5982 |  |  | 14.4492 |  |  | -29.6383 |  |  | -138.278 |  |  | -328.7293 |  |  | -596.4447 |  |  | -921.5574 |  |  | -1252.6356 |  |  | -1733.6342
[13 empty] | Press drop ratio this iteration |  |  | 0.3333 |  |  | 0.31505 |  |  | 0.19408 |  |  | -0.97617 |  |  | 1.7665 |  |  | 1.2233 |  |  | 1.1118 |  |  | 1.0696 |  |  | 1.0503 |  |  | 1.0359
[13 empty] | Expansion factor | 12 |  | 0.82641 |  |  | 0.83595 |  |  | 0.89798 |  |  | 1.5204 |  |  | 0.029151 |  |  | 0.28736 |  |  | 0.30313 |  |  | 0.25042 |  |  | 0.40715 |  |  | 0.083375
[13 empty] | C Non choked w/ reducers | 5 |  | 14.432 |  |  | 50.5649 |  |  | 173.19 |  |  | #NUM! |  |  | 5596.9142 |  |  | 296.6034 |  |  | 202.2637 |  |  | 203.2307 |  |  | 120.4164 |  |  | 662.6881
[13 empty] | C Choked w/ reducers | 5 |  | 12.9038 |  |  | 44.4579 |  |  | 128.9924 |  |  | 624.0782 |  |  | 417.4614 |  |  | 186.8412 |  |  | 132.9116 |  |  | 114.4216 |  |  | 98.0273 |  |  | 137.3651
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 14.432 |  |  | 50.5649 |  |  | 173.19 |  |  | #NUM! |  |  | 417.4614 |  |  | 186.8412 |  |  | 132.9116 |  |  | 114.4216 |  |  | 98.0273 |  |  | 137.3651
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.702 | 2723.9792 |  | 38.9649 | 9130.0732 |  | 150.19 | 22356.1955 |  | 18000 | 43544.1624 |  | 18000 | 73053.5589 |  | 18000 | 106623.6589 |  | 18000 | 140880.8774 |  | 18000 | 173620.4578 |  | 18000 | 201567.9615 |  | 18000 | 236354.2872
[13 empty] | Next iteration flow rate |  |  | 2778.4588 | Abs Value of | Flow this | 9221.3739 | Abs Value of | Flow this | 22579.7574 | Abs Value of | Flow this | 43979.604 | Abs Value of | Flow this | 73784.0945 | Abs Value of | Flow this | 107689.8955 | Abs Value of | Flow this | 142289.6861 | Abs Value of | Flow this | 175356.6624 | Abs Value of | Flow this | 203583.6411 | Abs Value of | Flow this | 238717.8301 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9864 |  |  | 87.5453 |  |  | 74.132 |  |  | 29.1584 |  |  | -81.665 |  |  | -275.9444 |  |  | -549.0409 |  |  | -880.6883 |  |  | -1218.4212 |  |  | -1709.0879
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43407 |  |  | 0.4223 |  |  | 0.35759 |  |  | 0.14065 |  |  | -0.39393 |  |  | -1.3311 |  |  | -2.6484 |  |  | -4.2482 |  |  | -5.8774 |  |  | -8.2442
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9864 |  |  | 27.5453 |  |  | 14.132 |  |  | -30.8416 |  |  | -141.665 |  |  | -335.9444 |  |  | -609.0409 |  |  | -940.6883 |  |  | -1278.4212 |  |  | -1769.0879
[13 empty] | Press drop ratio this iteration |  |  | 0.33323 |  |  | 0.31464 |  |  | 0.19063 |  |  | -1.0577 |  |  | 1.7347 |  |  | 1.2174 |  |  | 1.1093 |  |  | 1.0681 |  |  | 1.0492 |  |  | 1.0351
[13 empty] | Expansion factor | 12 |  | 0.82645 |  |  | 0.83617 |  |  | 0.89979 |  |  | 1.5638 |  |  | 0.046623 |  |  | 0.29076 |  |  | 0.30474 |  |  | 0.25148 |  |  | 0.40775 |  |  | 0.084033
[13 empty] | C Non choked w/ reducers | 5 |  | 14.723 |  |  | 51.1218 |  |  | 176.895 |  |  | #NUM! |  |  | 3418.8193 |  |  | 289.0147 |  |  | 198.7757 |  |  | 200.0992 |  |  | 118.9315 |  |  | 650.5313
[13 empty] | C Choked w/ reducers | 5 |  | 13.1632 |  |  | 44.9296 |  |  | 130.8398 |  |  | 656.3321 |  |  | 404.1489 |  |  | 183.7755 |  |  | 131.1609 |  |  | 113.0554 |  |  | 96.9122 |  |  | 135.8607
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 14.723 |  |  | 51.1218 |  |  | 176.895 |  |  | #NUM! |  |  | 404.1489 |  |  | 183.7755 |  |  | 131.1609 |  |  | 113.0554 |  |  | 96.9122 |  |  | 135.8607
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 9.993 | 2778.4588 |  | 39.5218 | 9221.3739 |  | 153.895 | 22579.7574 |  | 18000 | 43979.604 |  | 18000 | 73784.0945 |  | 18000 | 107689.8955 |  | 18000 | 142289.6861 |  | 18000 | 175356.6624 |  | 18000 | 203583.6411 |  | 18000 | 238717.8301
[13 empty] | Next iteration flow rate |  |  | 2834.0279 | Abs Value of | Flow this | 9313.5876 | Abs Value of | Flow this | 22805.555 | Abs Value of | Flow this | 44419.4001 | Abs Value of | Flow this | 74521.9354 | Abs Value of | Flow this | 108766.7944 | Abs Value of | Flow this | 143712.583 | Abs Value of | Flow this | 177110.229 | Abs Value of | Flow this | 205619.4776 | Abs Value of | Flow this | 241105.0084 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9766 |  |  | 87.4913 |  |  | 73.8084 |  |  | 27.9308 |  |  | -85.1201 |  |  | -283.3045 |  |  | -561.8903 |  |  | -900.2038 |  |  | -1244.7251 |  |  | -1745.2542
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43402 |  |  | 0.42204 |  |  | 0.35603 |  |  | 0.13473 |  |  | -0.4106 |  |  | -1.3666 |  |  | -2.7104 |  |  | -4.3424 |  |  | -6.0042 |  |  | -8.4187
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9766 |  |  | 27.4913 |  |  | 13.8084 |  |  | -32.0692 |  |  | -145.1201 |  |  | -343.3045 |  |  | -621.8903 |  |  | -960.2038 |  |  | -1304.7251 |  |  | -1805.2542
[13 empty] | Press drop ratio this iteration |  |  | 0.33316 |  |  | 0.31422 |  |  | 0.18708 |  |  | -1.1482 |  |  | 1.7049 |  |  | 1.2118 |  |  | 1.1068 |  |  | 1.0667 |  |  | 1.0482 |  |  | 1.0344
[13 empty] | Expansion factor | 12 |  | 0.82649 |  |  | 0.83639 |  |  | 0.90166 |  |  | 1.612 |  |  | 0.063013 |  |  | 0.29405 |  |  | 0.30631 |  |  | 0.25252 |  |  | 0.40834 |  |  | 0.084677
[13 empty] | C Non choked w/ reducers | 5 |  | 15.0201 |  |  | 51.686 |  |  | 180.7662 |  |  | #NUM! |  |  | 2472.4978 |  |  | 281.7939 |  |  | 195.3894 |  |  | 197.0447 |  |  | 117.4715 |  |  | 638.7539
[13 empty] | C Choked w/ reducers | 5 |  | 13.4279 |  |  | 45.4069 |  |  | 132.7275 |  |  | 692.0293 |  |  | 391.6216 |  |  | 180.7911 |  |  | 129.4431 |  |  | 111.7105 |  |  | 95.8129 |  |  | 134.3758
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 15.0201 |  |  | 51.686 |  |  | 180.7662 |  |  | #NUM! |  |  | 391.6216 |  |  | 180.7911 |  |  | 129.4431 |  |  | 111.7105 |  |  | 95.8129 |  |  | 134.3758
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 10.2901 | 2834.0279 |  | 40.086 | 9313.5876 |  | 157.7662 | 22805.555 |  | 18000 | 44419.4001 |  | 18000 | 74521.9354 |  | 18000 | 108766.7944 |  | 18000 | 143712.583 |  | 18000 | 177110.229 |  | 18000 | 205619.4776 |  | 18000 | 241105.0084
[13 empty] | Next iteration flow rate |  |  | 2890.7085 | Abs Value of | Flow this | 9406.7235 | Abs Value of | Flow this | 23033.6105 | Abs Value of | Flow this | 44863.5941 | Abs Value of | Flow this | 75267.1548 | Abs Value of | Flow this | 109854.4624 | Abs Value of | Flow this | 145149.7088 | Abs Value of | Flow this | 178881.3313 | Abs Value of | Flow this | 207675.6723 | Abs Value of | Flow this | 243516.0584 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9663 |  |  | 87.4363 |  |  | 73.4783 |  |  | 26.6786 |  |  | -88.6446 |  |  | -290.8125 |  |  | -574.9979 |  |  | -920.1115 |  |  | -1271.5577 |  |  | -1782.1474
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43398 |  |  | 0.42177 |  |  | 0.35444 |  |  | 0.12869 |  |  | -0.4276 |  |  | -1.4028 |  |  | -2.7736 |  |  | -4.4384 |  |  | -6.1337 |  |  | -8.5966
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9663 |  |  | 27.4363 |  |  | 13.4783 |  |  | -33.3214 |  |  | -148.6446 |  |  | -350.8125 |  |  | -634.9979 |  |  | -980.1115 |  |  | -1331.5577 |  |  | -1842.1474
[13 empty] | Press drop ratio this iteration |  |  | 0.33308 |  |  | 0.31379 |  |  | 0.18343 |  |  | -1.249 |  |  | 1.6769 |  |  | 1.2063 |  |  | 1.1043 |  |  | 1.0652 |  |  | 1.0472 |  |  | 1.0337
[13 empty] | Expansion factor | 12 |  | 0.82653 |  |  | 0.83662 |  |  | 0.90358 |  |  | 1.6658 |  |  | 0.078416 |  |  | 0.29724 |  |  | 0.30783 |  |  | 0.25353 |  |  | 0.40891 |  |  | 0.085307
[13 empty] | C Non choked w/ reducers | 5 |  | 15.3233 |  |  | 52.2577 |  |  | 184.8171 |  |  | #NUM! |  |  | 1942.9478 |  |  | 274.9135 |  |  | 192.1003 |  |  | 194.0644 |  |  | 116.0358 |  |  | 627.3376
[13 empty] | C Choked w/ reducers | 5 |  | 13.6981 |  |  | 45.8898 |  |  | 134.657 |  |  | 731.7563 |  |  | 379.8111 |  |  | 177.8848 |  |  | 127.7573 |  |  | 110.3865 |  |  | 94.7289 |  |  | 132.9099
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 15.3233 |  |  | 52.2577 |  |  | 184.8171 |  |  | #NUM! |  |  | 379.8111 |  |  | 177.8848 |  |  | 127.7573 |  |  | 110.3865 |  |  | 94.7289 |  |  | 132.9099
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 10.5933 | 2890.7085 |  | 40.6577 | 9406.7235 |  | 161.8171 | 23033.6105 |  | 18000 | 44863.5941 |  | 18000 | 75267.1548 |  | 18000 | 109854.4624 |  | 18000 | 145149.7088 |  | 18000 | 178881.3313 |  | 18000 | 207675.6723 |  | 18000 | 243516.0584
[13 empty] | Next iteration flow rate |  |  | 2948.5227 | Abs Value of | Flow this | 9500.7907 | Abs Value of | Flow this | 23263.9466 | Abs Value of | Flow this | 45312.23 | Abs Value of | Flow this | 76019.8263 | Abs Value of | Flow this | 110953.007 | Abs Value of | Flow this | 146601.2059 | Abs Value of | Flow this | 180670.1446 | Abs Value of | Flow this | 209752.4291 | Abs Value of | Flow this | 245951.219 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9557 |  |  | 87.3801 |  |  | 73.1416 |  |  | 25.4012 |  |  | -92.24 |  |  | -298.4715 |  |  | -588.369 |  |  | -940.4193 |  |  | -1298.9297 |  |  | -1819.7822
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43392 |  |  | 0.4215 |  |  | 0.35282 |  |  | 0.12253 |  |  | -0.44494 |  |  | -1.4398 |  |  | -2.8381 |  |  | -4.5363 |  |  | -6.2657 |  |  | -8.7782
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9557 |  |  | 27.3801 |  |  | 13.1416 |  |  | -34.5988 |  |  | -152.24 |  |  | -358.4715 |  |  | -648.369 |  |  | -1000.4193 |  |  | -1358.9297 |  |  | -1879.7822
[13 empty] | Press drop ratio this iteration |  |  | 0.333 |  |  | 0.31334 |  |  | 0.17967 |  |  | -1.3621 |  |  | 1.6505 |  |  | 1.201 |  |  | 1.102 |  |  | 1.0638 |  |  | 1.0462 |  |  | 1.033
[13 empty] | Expansion factor | 12 |  | 0.82657 |  |  | 0.83685 |  |  | 0.90555 |  |  | 1.7261 |  |  | 0.092916 |  |  | 0.30032 |  |  | 0.30932 |  |  | 0.25452 |  |  | 0.40947 |  |  | 0.085923
[13 empty] | C Non choked w/ reducers | 5 |  | 15.6327 |  |  | 52.8368 |  |  | 189.0626 |  |  | #NUM! |  |  | 1604.2578 |  |  | 268.3488 |  |  | 188.9039 |  |  | 191.1552 |  |  | 114.6237 |  |  | 616.2654
[13 empty] | C Choked w/ reducers | 5 |  | 13.9737 |  |  | 46.3785 |  |  | 136.6296 |  |  | 776.2407 |  |  | 368.6567 |  |  | 175.0533 |  |  | 126.1024 |  |  | 109.0828 |  |  | 93.6601 |  |  | 131.4628
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 15.6327 |  |  | 52.8368 |  |  | 189.0626 |  |  | #NUM! |  |  | 368.6567 |  |  | 175.0533 |  |  | 126.1024 |  |  | 109.0828 |  |  | 93.6601 |  |  | 131.4628
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 10.9027 | 2948.5227 |  | 41.2368 | 9500.7907 |  | 166.0626 | 23263.9466 |  | 18000 | 45312.23 |  | 18000 | 76019.8263 |  | 18000 | 110953.007 |  | 18000 | 146601.2059 |  | 18000 | 180670.1446 |  | 18000 | 209752.4291 |  | 18000 | 245951.219
[13 empty] | Next iteration flow rate |  |  | 3007.4931 | Abs Value of | Flow this | 9595.7986 | Abs Value of | Flow this | 23496.5861 | Abs Value of | Flow this | 45765.3523 | Abs Value of | Flow this | 76780.0246 | Abs Value of | Flow this | 112062.5371 | Abs Value of | Flow this | 148067.218 | Abs Value of | Flow this | 182476.8461 | Abs Value of | Flow this | 211849.9533 | Abs Value of | Flow this | 248410.7312 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9446 |  |  | 87.3228 |  |  | 72.7982 |  |  | 24.0982 |  |  | -95.9077 |  |  | -306.2844 |  |  | -602.0088 |  |  | -961.1354 |  |  | -1326.8518 |  |  | -1858.1735
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43387 |  |  | 0.42122 |  |  | 0.35116 |  |  | 0.11624 |  |  | -0.46263 |  |  | -1.4774 |  |  | -2.9039 |  |  | -4.6363 |  |  | -6.4004 |  |  | -8.9634
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9446 |  |  | 27.3228 |  |  | 12.7982 |  |  | -35.9018 |  |  | -155.9077 |  |  | -366.2844 |  |  | -662.0088 |  |  | -1021.1354 |  |  | -1386.8518 |  |  | -1918.1735
[13 empty] | Press drop ratio this iteration |  |  | 0.33292 |  |  | 0.31289 |  |  | 0.1758 |  |  | -1.4898 |  |  | 1.6256 |  |  | 1.1959 |  |  | 1.0997 |  |  | 1.0624 |  |  | 1.0452 |  |  | 1.0323
[13 empty] | Expansion factor | 12 |  | 0.82661 |  |  | 0.83708 |  |  | 0.90759 |  |  | 1.7942 |  |  | 0.10659 |  |  | 0.30331 |  |  | 0.31077 |  |  | 0.25548 |  |  | 0.41002 |  |  | 0.086526
[13 empty] | C Non choked w/ reducers | 5 |  | 15.9484 |  |  | 53.4236 |  |  | 193.5199 |  |  | #NUM! |  |  | 1368.8151 |  |  | 262.0774 |  |  | 185.796 |  |  | 188.3147 |  |  | 113.2347 |  |  | 605.5213
[13 empty] | C Choked w/ reducers | 5 |  | 14.2549 |  |  | 46.873 |  |  | 138.647 |  |  | 826.3966 |  |  | 358.1043 |  |  | 172.2938 |  |  | 124.4778 |  |  | 107.7989 |  |  | 92.606 |  |  | 130.0342
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 15.9484 |  |  | 53.4236 |  |  | 193.5199 |  |  | #NUM! |  |  | 358.1043 |  |  | 172.2938 |  |  | 124.4778 |  |  | 107.7989 |  |  | 92.606 |  |  | 130.0342
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 11.2184 | 3007.4931 |  | 41.8236 | 9595.7986 |  | 170.5199 | 23496.5861 |  | 18000 | 45765.3523 |  | 18000 | 76780.0246 |  | 18000 | 112062.5371 |  | 18000 | 148067.218 |  | 18000 | 182476.8461 |  | 18000 | 211849.9533 |  | 18000 | 248410.7312
[13 empty] | Next iteration flow rate |  |  | 3067.643 | Abs Value of | Flow this | 9691.7566 | Abs Value of | Flow this | 23731.552 | Abs Value of | Flow this | 46223.0059 | Abs Value of | Flow this | 77547.8248 | Abs Value of | Flow this | 113183.1624 | Abs Value of | Flow this | 149547.8901 | Abs Value of | Flow this | 184301.6145 | Abs Value of | Flow this | 213968.4529 | Abs Value of | Flow this | 250894.8385 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.933 |  |  | 87.2644 |  |  | 72.4478 |  |  | 22.7689 |  |  | -99.6491 |  |  | -314.2543 |  |  | -615.9228 |  |  | -982.2679 |  |  | -1355.3351 |  |  | -1897.3364
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43381 |  |  | 0.42094 |  |  | 0.34947 |  |  | 0.10983 |  |  | -0.48068 |  |  | -1.5159 |  |  | -2.9711 |  |  | -4.7382 |  |  | -6.5378 |  |  | -9.1523
[13 empty] | Delta P at this iteration flow rate |  |  | 29.933 |  |  | 27.2644 |  |  | 12.4478 |  |  | -37.2311 |  |  | -159.6491 |  |  | -374.2543 |  |  | -675.9228 |  |  | -1042.2679 |  |  | -1415.3351 |  |  | -1957.3364
[13 empty] | Press drop ratio this iteration |  |  | 0.33284 |  |  | 0.31243 |  |  | 0.17182 |  |  | -1.6352 |  |  | 1.6021 |  |  | 1.1909 |  |  | 1.0974 |  |  | 1.0611 |  |  | 1.0443 |  |  | 1.0316
[13 empty] | Expansion factor | 12 |  | 0.82666 |  |  | 0.83732 |  |  | 0.90968 |  |  | 1.8716 |  |  | 0.1195 |  |  | 0.3062 |  |  | 0.31218 |  |  | 0.25642 |  |  | 0.41056 |  |  | 0.087115
[13 empty] | C Non choked w/ reducers | 5 |  | 16.2707 |  |  | 54.0183 |  |  | 198.208 |  |  | #NUM! |  |  | 1195.522 |  |  | 256.0789 |  |  | 182.7729 |  |  | 185.5402 |  |  | 111.8681 |  |  | 595.0901
[13 empty] | C Choked w/ reducers | 5 |  | 14.5419 |  |  | 47.3734 |  |  | 140.7108 |  |  | 883.3882 |  |  | 348.1057 |  |  | 169.6035 |  |  | 122.8824 |  |  | 106.5346 |  |  | 91.5664 |  |  | 128.6236
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 16.2707 |  |  | 54.0183 |  |  | 198.208 |  |  | #NUM! |  |  | 348.1057 |  |  | 169.6035 |  |  | 122.8824 |  |  | 106.5346 |  |  | 91.5664 |  |  | 128.6236
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 11.5407 | 3067.643 |  | 42.4183 | 9691.7566 |  | 175.208 | 23731.552 |  | 18000 | 46223.0059 |  | 18000 | 77547.8248 |  | 18000 | 113183.1624 |  | 18000 | 149547.8901 |  | 18000 | 184301.6145 |  | 18000 | 213968.4529 |  | 18000 | 250894.8385
[13 empty] | Next iteration flow rate |  |  | 3128.9958 | Abs Value of | Flow this | 9788.6742 | Abs Value of | Flow this | 23968.8675 | Abs Value of | Flow this | 46685.2359 | Abs Value of | Flow this | 78323.3031 | Abs Value of | Flow this | 114314.9941 | Abs Value of | Flow this | 151043.369 | Abs Value of | Flow this | 186144.6307 | Abs Value of | Flow this | 216108.1374 | Abs Value of | Flow this | 253403.7869 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.921 |  |  | 87.2048 |  |  | 72.0903 |  |  | 21.4129 |  |  | -103.4656 |  |  | -322.3844 |  |  | -630.1165 |  |  | -1003.8251 |  |  | -1384.391 |  |  | -1937.2865
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43376 |  |  | 0.42065 |  |  | 0.34775 |  |  | 0.10329 |  |  | -0.49909 |  |  | -1.5551 |  |  | -3.0395 |  |  | -4.8422 |  |  | -6.678 |  |  | -9.345
[13 empty] | Delta P at this iteration flow rate |  |  | 29.921 |  |  | 27.2048 |  |  | 12.0903 |  |  | -38.5871 |  |  | -163.4656 |  |  | -382.3844 |  |  | -690.1165 |  |  | -1063.8251 |  |  | -1444.391 |  |  | -1997.2865
[13 empty] | Press drop ratio this iteration |  |  | 0.33275 |  |  | 0.31196 |  |  | 0.16771 |  |  | -1.802 |  |  | 1.5799 |  |  | 1.1861 |  |  | 1.0952 |  |  | 1.0598 |  |  | 1.0433 |  |  | 1.031
[13 empty] | Expansion factor | 12 |  | 0.8267 |  |  | 0.83756 |  |  | 0.91184 |  |  | 1.9606 |  |  | 0.1317 |  |  | 0.30901 |  |  | 0.31356 |  |  | 0.25734 |  |  | 0.41108 |  |  | 0.087693
[13 empty] | C Non choked w/ reducers | 5 |  | 16.5996 |  |  | 54.6209 |  |  | 203.1485 |  |  | #NUM! |  |  | 1062.543 |  |  | 250.3351 |  |  | 179.8308 |  |  | 182.8292 |  |  | 110.5234 |  |  | 584.9578
[13 empty] | C Choked w/ reducers | 5 |  | 14.8347 |  |  | 47.8799 |  |  | 142.8225 |  |  | 948.722 |  |  | 338.6176 |  |  | 166.9795 |  |  | 121.3156 |  |  | 105.2892 |  |  | 90.5411 |  |  | 127.2309
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 16.5996 |  |  | 54.6209 |  |  | 203.1485 |  |  | #NUM! |  |  | 338.6176 |  |  | 166.9795 |  |  | 121.3156 |  |  | 105.2892 |  |  | 90.5411 |  |  | 127.2309
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 11.8696 | 3128.9958 |  | 43.0209 | 9788.6742 |  | 180.1485 | 23968.8675 |  | 18000 | 46685.2359 |  | 18000 | 78323.3031 |  | 18000 | 114314.9941 |  | 18000 | 151043.369 |  | 18000 | 186144.6307 |  | 18000 | 216108.1374 |  | 18000 | 253403.7869
[13 empty] | Next iteration flow rate |  |  | 3191.5758 | Abs Value of | Flow this | 9886.5609 | Abs Value of | Flow this | 24208.5562 | Abs Value of | Flow this | 47152.0883 | Abs Value of | Flow this | 79106.5361 | Abs Value of | Flow this | 115458.144 | Abs Value of | Flow this | 152553.8027 | Abs Value of | Flow this | 188006.077 | Abs Value of | Flow this | 218269.2188 | Abs Value of | Flow this | 255937.8248 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.9086 |  |  | 87.1439 |  |  | 71.7257 |  |  | 20.0297 |  |  | -107.3589 |  |  | -330.678 |  |  | -644.5955 |  |  | -1025.8156 |  |  | -1414.0309 |  |  | -1978.0395
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4337 |  |  | 0.42036 |  |  | 0.34599 |  |  | 0.096618 |  |  | -0.51787 |  |  | -1.5951 |  |  | -3.1094 |  |  | -4.9483 |  |  | -6.8209 |  |  | -9.5416
[13 empty] | Delta P at this iteration flow rate |  |  | 29.9086 |  |  | 27.1439 |  |  | 11.7257 |  |  | -39.9703 |  |  | -167.3589 |  |  | -390.678 |  |  | -704.5955 |  |  | -1085.8156 |  |  | -1474.0309 |  |  | -2038.0395
[13 empty] | Press drop ratio this iteration |  |  | 0.33266 |  |  | 0.31148 |  |  | 0.16348 |  |  | -1.9956 |  |  | 1.5589 |  |  | 1.1814 |  |  | 1.0931 |  |  | 1.0585 |  |  | 1.0424 |  |  | 1.0303
[13 empty] | Expansion factor | 12 |  | 0.82675 |  |  | 0.83781 |  |  | 0.91407 |  |  | 2.0637 |  |  | 0.14326 |  |  | 0.31173 |  |  | 0.3149 |  |  | 0.25824 |  |  | 0.4116 |  |  | 0.088257
[13 empty] | C Non choked w/ reducers | 5 |  | 16.9353 |  |  | 55.2317 |  |  | 208.3663 |  |  | #NUM! |  |  | 957.2032 |  |  | 244.8291 |  |  | 176.9664 |  |  | 180.1797 |  |  | 109.2002 |  |  | 575.1112
[13 empty] | C Choked w/ reducers | 5 |  | 15.1335 |  |  | 48.3924 |  |  | 144.984 |  |  | 1024.382 |  |  | 329.6013 |  |  | 164.4195 |  |  | 119.7765 |  |  | 104.0624 |  |  | 89.5296 |  |  | 125.8557
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 16.9353 |  |  | 55.2317 |  |  | 208.3663 |  |  | #NUM! |  |  | 329.6013 |  |  | 164.4195 |  |  | 119.7765 |  |  | 104.0624 |  |  | 89.5296 |  |  | 125.8557
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 12.2053 | 3191.5758 |  | 43.6317 | 9886.5609 |  | 185.3663 | 24208.5562 |  | 18000 | 47152.0883 |  | 18000 | 79106.5361 |  | 18000 | 115458.144 |  | 18000 | 152553.8027 |  | 18000 | 188006.077 |  | 18000 | 218269.2188 |  | 18000 | 255937.8248
[13 empty] | Next iteration flow rate |  |  | 3255.4073 | Abs Value of | Flow this | 9985.4265 | Abs Value of | Flow this | 24450.6417 | Abs Value of | Flow this | 47623.6092 | Abs Value of | Flow this | 79897.6015 | Abs Value of | Flow this | 116612.7255 | Abs Value of | Flow this | 154079.3408 | Abs Value of | Flow this | 189886.1377 | Abs Value of | Flow this | 220451.911 | Abs Value of | Flow this | 258497.203 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8956 |  |  | 87.0819 |  |  | 71.3538 |  |  | 18.6187 |  |  | -111.3305 |  |  | -339.1383 |  |  | -659.3655 |  |  | -1048.2481 |  |  | -1444.2665 |  |  | -2019.6118
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43363 |  |  | 0.42006 |  |  | 0.34419 |  |  | 0.089812 |  |  | -0.53703 |  |  | -1.6359 |  |  | -3.1806 |  |  | -5.0565 |  |  | -6.9668 |  |  | -9.7421
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8956 |  |  | 27.0819 |  |  | 11.3538 |  |  | -41.3813 |  |  | -171.3305 |  |  | -399.1383 |  |  | -719.3655 |  |  | -1108.2481 |  |  | -1504.2665 |  |  | -2079.6118
[13 empty] | Press drop ratio this iteration |  |  | 0.33256 |  |  | 0.31099 |  |  | 0.15912 |  |  | -2.2226 |  |  | 1.5389 |  |  | 1.1769 |  |  | 1.091 |  |  | 1.0572 |  |  | 1.0415 |  |  | 1.0297
[13 empty] | Expansion factor | 12 |  | 0.8268 |  |  | 0.83807 |  |  | 0.91636 |  |  | 2.1848 |  |  | 0.15422 |  |  | 0.31436 |  |  | 0.3162 |  |  | 0.25912 |  |  | 0.4121 |  |  | 0.08881
[13 empty] | C Non choked w/ reducers | 5 |  | 17.278 |  |  | 55.8507 |  |  | 213.8896 |  |  | #NUM! |  |  | 871.6399 |  |  | 239.5456 |  |  | 174.1764 |  |  | 177.5892 |  |  | 107.8978 |  |  | 565.5377
[13 empty] | C Choked w/ reducers | 5 |  | 15.4384 |  |  | 48.9112 |  |  | 147.1972 |  |  | 1113.0357 |  |  | 321.0217 |  |  | 161.921 |  |  | 118.2644 |  |  | 102.8538 |  |  | 88.5319 |  |  | 124.4977
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 17.278 |  |  | 55.8507 |  |  | 213.8896 |  |  | #NUM! |  |  | 321.0217 |  |  | 161.921 |  |  | 118.2644 |  |  | 102.8538 |  |  | 88.5319 |  |  | 124.4977
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 12.548 | 3255.4073 |  | 44.2507 | 9985.4265 |  | 190.8896 | 24450.6417 |  | 18000 | 47623.6092 |  | 18000 | 79897.6015 |  | 18000 | 116612.7255 |  | 18000 | 154079.3408 |  | 18000 | 189886.1377 |  | 18000 | 220451.911 |  | 18000 | 258497.203
[13 empty] | Next iteration flow rate |  |  | 3320.5154 | Abs Value of | Flow this | 10085.2808 | Abs Value of | Flow this | 24695.1481 | Abs Value of | Flow this | 48099.8452 | Abs Value of | Flow this | 80696.5775 | Abs Value of | Flow this | 117778.8527 | Abs Value of | Flow this | 155620.1342 | Abs Value of | Flow this | 191784.9991 | Abs Value of | Flow this | 222656.4301 | Abs Value of | Flow this | 261082.1751 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.882 |  |  | 87.0186 |  |  | 70.9744 |  |  | 17.1793 |  |  | -115.3818 |  |  | -347.7686 |  |  | -674.4323 |  |  | -1071.1315 |  |  | -1475.1099 |  |  | -2062.0196
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43357 |  |  | 0.41976 |  |  | 0.34236 |  |  | 0.082869 |  |  | -0.55657 |  |  | -1.6775 |  |  | -3.2533 |  |  | -5.1669 |  |  | -7.1156 |  |  | -9.9467
[13 empty] | Delta P at this iteration flow rate |  |  | 29.882 |  |  | 27.0186 |  |  | 10.9744 |  |  | -42.8207 |  |  | -175.3818 |  |  | -407.7686 |  |  | -734.4323 |  |  | -1131.1315 |  |  | -1535.1099 |  |  | -2122.0196
[13 empty] | Press drop ratio this iteration |  |  | 0.33246 |  |  | 0.31049 |  |  | 0.15462 |  |  | -2.4926 |  |  | 1.52 |  |  | 1.1725 |  |  | 1.089 |  |  | 1.056 |  |  | 1.0407 |  |  | 1.0291
[13 empty] | Expansion factor | 12 |  | 0.82685 |  |  | 0.83833 |  |  | 0.91872 |  |  | 2.3287 |  |  | 0.16462 |  |  | 0.31692 |  |  | 0.31748 |  |  | 0.25997 |  |  | 0.41259 |  |  | 0.08935
[13 empty] | C Non choked w/ reducers | 5 |  | 17.6277 |  |  | 56.4782 |  |  | 219.751 |  |  | #NUM! |  |  | 800.7169 |  |  | 234.4706 |  |  | 171.4577 |  |  | 175.0559 |  |  | 106.6158 |  |  | 556.2256
[13 empty] | C Choked w/ reducers | 5 |  | 15.7495 |  |  | 49.4362 |  |  | 149.4639 |  |  | 1218.356 |  |  | 312.8473 |  |  | 159.4818 |  |  | 116.7786 |  |  | 101.6631 |  |  | 87.5476 |  |  | 123.1566
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 17.6277 |  |  | 56.4782 |  |  | 219.751 |  |  | #NUM! |  |  | 312.8473 |  |  | 159.4818 |  |  | 116.7786 |  |  | 101.6631 |  |  | 87.5476 |  |  | 123.1566
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 12.8977 | 3320.5154 |  | 44.8782 | 10085.2808 |  | 196.751 | 24695.1481 |  | 18000 | 48099.8452 |  | 18000 | 80696.5775 |  | 18000 | 117778.8527 |  | 18000 | 155620.1342 |  | 18000 | 191784.9991 |  | 18000 | 222656.4301 |  | 18000 | 261082.1751
[13 empty] | Next iteration flow rate |  |  | 3386.9257 | Abs Value of | Flow this | 10186.1336 | Abs Value of | Flow this | 24942.0996 | Abs Value of | Flow this | 48580.8437 | Abs Value of | Flow this | 81503.5433 | Abs Value of | Flow this | 118956.6412 | Abs Value of | Flow this | 157176.3355 | Abs Value of | Flow this | 193702.8491 | Abs Value of | Flow this | 224882.9944 | Abs Value of | Flow this | 263692.9968 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.868 |  |  | 86.9541 |  |  | 70.5873 |  |  | 15.711 |  |  | -119.5146 |  |  | -356.5723 |  |  | -689.802 |  |  | -1094.4749 |  |  | -1506.5732 |  |  | -2105.2798
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4335 |  |  | 0.41944 |  |  | 0.3405 |  |  | 0.075786 |  |  | -0.57651 |  |  | -1.72 |  |  | -3.3274 |  |  | -5.2795 |  |  | -7.2673 |  |  | -10.1553
[13 empty] | Delta P at this iteration flow rate |  |  | 29.868 |  |  | 26.9541 |  |  | 10.5873 |  |  | -44.289 |  |  | -179.5146 |  |  | -416.5723 |  |  | -749.802 |  |  | -1154.4749 |  |  | -1566.5732 |  |  | -2165.2798
[13 empty] | Press drop ratio this iteration |  |  | 0.33235 |  |  | 0.30998 |  |  | 0.14999 |  |  | -2.819 |  |  | 1.502 |  |  | 1.1683 |  |  | 1.087 |  |  | 1.0548 |  |  | 1.0398 |  |  | 1.0285
[13 empty] | Expansion factor | 12 |  | 0.82691 |  |  | 0.8386 |  |  | 0.92116 |  |  | 2.5027 |  |  | 0.1745 |  |  | 0.3194 |  |  | 0.31872 |  |  | 0.26081 |  |  | 0.41307 |  |  | 0.089879
[13 empty] | C Non choked w/ reducers | 5 |  | 17.9847 |  |  | 57.1143 |  |  | 225.9883 |  |  | #NUM! |  |  | 740.9365 |  |  | 229.5913 |  |  | 168.8075 |  |  | 172.5776 |  |  | 105.3538 |  |  | 547.1638
[13 empty] | C Choked w/ reducers | 5 |  | 16.067 |  |  | 49.9676 |  |  | 151.7862 |  |  | 1345.544 |  |  | 305.0493 |  |  | 157.0996 |  |  | 115.3183 |  |  | 100.4897 |  |  | 86.5764 |  |  | 121.8322
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 17.9847 |  |  | 57.1143 |  |  | 225.9883 |  |  | #NUM! |  |  | 305.0493 |  |  | 157.0996 |  |  | 115.3183 |  |  | 100.4897 |  |  | 86.5764 |  |  | 121.8322
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 13.2547 | 3386.9257 |  | 45.5143 | 10186.1336 |  | 202.9883 | 24942.0996 |  | 18000 | 48580.8437 |  | 18000 | 81503.5433 |  | 18000 | 118956.6412 |  | 18000 | 157176.3355 |  | 18000 | 193702.8491 |  | 18000 | 224882.9944 |  | 18000 | 263692.9968
[13 empty] | Next iteration flow rate |  |  | 3454.6643 | Abs Value of | Flow this | 10287.995 | Abs Value of | Flow this | 25191.5206 | Abs Value of | Flow this | 49066.6521 | Abs Value of | Flow this | 82318.5787 | Abs Value of | Flow this | 120146.2076 | Abs Value of | Flow this | 158748.0989 | Abs Value of | Flow this | 195639.8776 | Abs Value of | Flow this | 227131.8243 | Abs Value of | Flow this | 266329.9268 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8533 |  |  | 86.8882 |  |  | 70.1925 |  |  | 14.2131 |  |  | -123.7305 |  |  | -365.5531 |  |  | -705.4807 |  |  | -1118.2874 |  |  | -1538.669 |  |  | -2149.4096
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43343 |  |  | 0.41913 |  |  | 0.33859 |  |  | 0.068561 |  |  | -0.59684 |  |  | -1.7633 |  |  | -3.4031 |  |  | -5.3943 |  |  | -7.4222 |  |  | -10.3682
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8533 |  |  | 26.8882 |  |  | 10.1925 |  |  | -45.7869 |  |  | -183.7305 |  |  | -425.5531 |  |  | -765.4807 |  |  | -1178.2874 |  |  | -1598.669 |  |  | -2209.4096
[13 empty] | Press drop ratio this iteration |  |  | 0.33225 |  |  | 0.30946 |  |  | 0.14521 |  |  | -3.2215 |  |  | 1.4849 |  |  | 1.1641 |  |  | 1.085 |  |  | 1.0537 |  |  | 1.039 |  |  | 1.0279
[13 empty] | Expansion factor | 12 |  | 0.82696 |  |  | 0.83887 |  |  | 0.92367 |  |  | 2.7172 |  |  | 0.1839 |  |  | 0.32181 |  |  | 0.31993 |  |  | 0.26163 |  |  | 0.41354 |  |  | 0.090397
[13 empty] | C Non choked w/ reducers | 5 |  | 18.3492 |  |  | 57.7591 |  |  | 232.6455 |  |  | #NUM! |  |  | 689.8345 |  |  | 224.8958 |  |  | 166.223 |  |  | 170.1526 |  |  | 104.1112 |  |  | 538.342
[13 empty] | C Choked w/ reducers | 5 |  | 16.391 |  |  | 50.5055 |  |  | 154.1664 |  |  | 1502.2163 |  |  | 297.6019 |  |  | 154.7725 |  |  | 113.8831 |  |  | 99.3334 |  |  | 85.6182 |  |  | 120.5242
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 18.3492 |  |  | 57.7591 |  |  | 232.6455 |  |  | #NUM! |  |  | 297.6019 |  |  | 154.7725 |  |  | 113.8831 |  |  | 99.3334 |  |  | 85.6182 |  |  | 120.5242
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 13.6192 | 3454.6643 |  | 46.1591 | 10287.995 |  | 209.6455 | 25191.5206 |  | 18000 | 49066.6521 |  | 18000 | 82318.5787 |  | 18000 | 120146.2076 |  | 18000 | 158748.0989 |  | 18000 | 195639.8776 |  | 18000 | 227131.8243 |  | 18000 | 266329.9268
[13 empty] | Next iteration flow rate |  |  | 3523.7575 | Abs Value of | Flow this | 10390.8749 | Abs Value of | Flow this | 25443.4358 | Abs Value of | Flow this | 49557.3187 | Abs Value of | Flow this | 83141.7645 | Abs Value of | Flow this | 121347.6697 | Abs Value of | Flow this | 160335.5799 | Abs Value of | Flow this | 197596.2764 | Abs Value of | Flow this | 229403.1426 | Abs Value of | Flow this | 268993.226 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8381 |  |  | 86.8211 |  |  | 69.7898 |  |  | 12.6852 |  |  | -128.0311 |  |  | -374.7143 |  |  | -721.4745 |  |  | -1142.5787 |  |  | -1571.4099 |  |  | -2194.4263
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43336 |  |  | 0.4188 |  |  | 0.33665 |  |  | 0.06119 |  |  | -0.61759 |  |  | -1.8075 |  |  | -3.4802 |  |  | -5.5115 |  |  | -7.5801 |  |  | -10.5854
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8381 |  |  | 26.8211 |  |  | 9.7898 |  |  | -47.3148 |  |  | -188.0311 |  |  | -434.7143 |  |  | -781.4745 |  |  | -1202.5787 |  |  | -1631.4099 |  |  | -2254.4263
[13 empty] | Press drop ratio this iteration |  |  | 0.33213 |  |  | 0.30892 |  |  | 0.14028 |  |  | -3.7299 |  |  | 1.4686 |  |  | 1.1601 |  |  | 1.0832 |  |  | 1.0525 |  |  | 1.0382 |  |  | 1.0273
[13 empty] | Expansion factor | 12 |  | 0.82702 |  |  | 0.83915 |  |  | 0.92626 |  |  | 2.9883 |  |  | 0.19285 |  |  | 0.32415 |  |  | 0.32111 |  |  | 0.26243 |  |  | 0.41399 |  |  | 0.090904
[13 empty] | C Non choked w/ reducers | 5 |  | 18.7212 |  |  | 58.4129 |  |  | 239.7744 |  |  | #NUM! |  |  | 645.6246 |  |  | 220.3734 |  |  | 163.7017 |  |  | 167.779 |  |  | 102.8876 |  |  | 529.7502
[13 empty] | C Choked w/ reducers | 5 |  | 16.7217 |  |  | 51.0501 |  |  | 156.6067 |  |  | 1699.9915 |  |  | 290.4814 |  |  | 152.4984 |  |  | 112.4721 |  |  | 98.1938 |  |  | 84.6726 |  |  | 119.2323
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 18.7212 |  |  | 58.4129 |  |  | 239.7744 |  |  | #NUM! |  |  | 290.4814 |  |  | 152.4984 |  |  | 112.4721 |  |  | 98.1938 |  |  | 84.6726 |  |  | 119.2323
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 13.9912 | 3523.7575 |  | 46.8129 | 10390.8749 |  | 216.7744 | 25443.4358 |  | 18000 | 49557.3187 |  | 18000 | 83141.7645 |  | 18000 | 121347.6697 |  | 18000 | 160335.5799 |  | 18000 | 197596.2764 |  | 18000 | 229403.1426 |  | 18000 | 268993.226
[13 empty] | Next iteration flow rate |  |  | 3594.2327 | Abs Value of | Flow this | 10494.7837 | Abs Value of | Flow this | 25697.8702 | Abs Value of | Flow this | 50052.8918 | Abs Value of | Flow this | 83973.1821 | Abs Value of | Flow this | 122561.1464 | Abs Value of | Flow this | 161938.9357 | Abs Value of | Flow this | 199572.2391 | Abs Value of | Flow this | 231697.174 | Abs Value of | Flow this | 271683.1583 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8223 |  |  | 86.7525 |  |  | 69.3789 |  |  | 11.1265 |  |  | -132.4182 |  |  | -384.0597 |  |  | -737.7897 |  |  | -1167.3581 |  |  | -1604.8088 |  |  | -2240.3479
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43328 |  |  | 0.41847 |  |  | 0.33467 |  |  | 0.053672 |  |  | -0.63875 |  |  | -1.8526 |  |  | -3.5589 |  |  | -5.631 |  |  | -7.7412 |  |  | -10.8069
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8223 |  |  | 26.7525 |  |  | 9.3789 |  |  | -48.8735 |  |  | -192.4182 |  |  | -444.0597 |  |  | -797.7897 |  |  | -1227.3581 |  |  | -1664.8088 |  |  | -2300.3479
[13 empty] | Press drop ratio this iteration |  |  | 0.33201 |  |  | 0.30838 |  |  | 0.13518 |  |  | -4.3925 |  |  | 1.4531 |  |  | 1.1562 |  |  | 1.0813 |  |  | 1.0514 |  |  | 1.0374 |  |  | 1.0268
[13 empty] | Expansion factor | 12 |  | 0.82708 |  |  | 0.83943 |  |  | 0.92894 |  |  | 3.3415 |  |  | 0.20139 |  |  | 0.32642 |  |  | 0.32227 |  |  | 0.26321 |  |  | 0.41444 |  |  | 0.0914
[13 empty] | C Non choked w/ reducers | 5 |  | 19.1009 |  |  | 59.0759 |  |  | 247.4362 |  |  | #NUM! |  |  | 606.9802 |  |  | 216.0141 |  |  | 161.2411 |  |  | 165.4552 |  |  | 101.6826 |  |  | 521.3791
[13 empty] | C Choked w/ reducers | 5 |  | 17.0591 |  |  | 51.6013 |  |  | 159.1094 |  |  | 1957.5156 |  |  | 283.6663 |  |  | 150.2755 |  |  | 111.0847 |  |  | 97.0705 |  |  | 83.7395 |  |  | 117.9562
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 19.1009 |  |  | 59.0759 |  |  | 247.4362 |  |  | #NUM! |  |  | 283.6663 |  |  | 150.2755 |  |  | 111.0847 |  |  | 97.0705 |  |  | 83.7395 |  |  | 117.9562
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 14.3709 | 3594.2327 |  | 47.4759 | 10494.7837 |  | 224.4362 | 25697.8702 |  | 18000 | 50052.8918 |  | 18000 | 83973.1821 |  | 18000 | 122561.1464 |  | 18000 | 161938.9357 |  | 18000 | 199572.2391 |  | 18000 | 231697.174 |  | 18000 | 271683.1583
[13 empty] | Next iteration flow rate |  |  | 3666.1173 | Abs Value of | Flow this | 10599.7315 | Abs Value of | Flow this | 25954.8489 | Abs Value of | Flow this | 50553.4208 | Abs Value of | Flow this | 84812.9139 | Abs Value of | Flow this | 123786.7579 | Abs Value of | Flow this | 163558.325 | Abs Value of | Flow this | 201567.9615 | Abs Value of | Flow this | 234014.1457 | Abs Value of | Flow this | 274399.9899 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.8058 |  |  | 86.6826 |  |  | 68.9598 |  |  | 9.5365 |  |  | -136.8934 |  |  | -393.5929 |  |  | -754.4329 |  |  | -1192.6356 |  |  | -1638.8791 |  |  | -2287.1925
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4332 |  |  | 0.41814 |  |  | 0.33264 |  |  | 0.046002 |  |  | -0.66034 |  |  | -1.8986 |  |  | -3.6392 |  |  | -5.753 |  |  | -7.9055 |  |  | -11.0328
[13 empty] | Delta P at this iteration flow rate |  |  | 29.8058 |  |  | 26.6826 |  |  | 8.9598 |  |  | -50.4635 |  |  | -196.8934 |  |  | -453.5929 |  |  | -814.4329 |  |  | -1252.6356 |  |  | -1698.8791 |  |  | -2347.1925
[13 empty] | Press drop ratio this iteration |  |  | 0.33189 |  |  | 0.30782 |  |  | 0.12993 |  |  | -5.2916 |  |  | 1.4383 |  |  | 1.1524 |  |  | 1.0795 |  |  | 1.0503 |  |  | 1.0366 |  |  | 1.0262
[13 empty] | Expansion factor | 12 |  | 0.82715 |  |  | 0.83972 |  |  | 0.9317 |  |  | 3.8207 |  |  | 0.20953 |  |  | 0.32862 |  |  | 0.32339 |  |  | 0.26397 |  |  | 0.41488 |  |  | 0.091885
[13 empty] | C Non choked w/ reducers | 5 |  | 19.4886 |  |  | 59.7482 |  |  | 255.7041 |  |  | #NUM! |  |  | 572.8953 |  |  | 211.8087 |  |  | 158.8389 |  |  | 163.1794 |  |  | 100.4957 |  |  | 513.2199
[13 empty] | C Choked w/ reducers | 5 |  | 17.4035 |  |  | 52.1593 |  |  | 161.6772 |  |  | 2306.7221 |  |  | 277.1368 |  |  | 148.102 |  |  | 109.7205 |  |  | 95.9633 |  |  | 82.8187 |  |  | 116.6957
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 19.4886 |  |  | 59.7482 |  |  | 255.7041 |  |  | #NUM! |  |  | 277.1368 |  |  | 148.102 |  |  | 109.7205 |  |  | 95.9633 |  |  | 82.8187 |  |  | 116.6957
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 14.7586 | 3666.1173 |  | 48.1482 | 10599.7315 |  | 232.7041 | 25954.8489 |  | 18000 | 50553.4208 |  | 18000 | 84812.9139 |  | 18000 | 123786.7579 |  | 18000 | 163558.325 |  | 18000 | 201567.9615 |  | 18000 | 234014.1457 |  | 18000 | 274399.9899
[13 empty] | Next iteration flow rate |  |  | 3739.4397 | Abs Value of | Flow this | 10705.7288 | Abs Value of | Flow this | 26214.3974 | Abs Value of | Flow this | 51058.955 | Abs Value of | Flow this | 85661.0431 | Abs Value of | Flow this | 125024.6255 | Abs Value of | Flow this | 165193.9083 | Abs Value of | Flow this | 203583.6411 | Abs Value of | Flow this | 236354.2872 | Abs Value of | Flow this | 277143.9898 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.7887 |  |  | 86.6113 |  |  | 68.5323 |  |  | 7.9146 |  |  | -141.4586 |  |  | -403.3178 |  |  | -771.4107 |  |  | -1218.4212 |  |  | -1673.6342 |  |  | -2334.9787
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43312 |  |  | 0.41779 |  |  | 0.33058 |  |  | 0.038178 |  |  | -0.68236 |  |  | -1.9455 |  |  | -3.7211 |  |  | -5.8774 |  |  | -8.0732 |  |  | -11.2634
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7887 |  |  | 26.6113 |  |  | 8.5323 |  |  | -52.0854 |  |  | -201.4586 |  |  | -463.3178 |  |  | -831.4107 |  |  | -1278.4212 |  |  | -1733.6342 |  |  | -2394.9787
[13 empty] | Press drop ratio this iteration |  |  | 0.33176 |  |  | 0.30725 |  |  | 0.1245 |  |  | -6.5809 |  |  | 1.4242 |  |  | 1.1488 |  |  | 1.0778 |  |  | 1.0492 |  |  | 1.0359 |  |  | 1.0257
[13 empty] | Expansion factor | 12 |  | 0.82721 |  |  | 0.84002 |  |  | 0.93456 |  |  | 4.508 |  |  | 0.2173 |  |  | 0.33077 |  |  | 0.32449 |  |  | 0.26472 |  |  | 0.41531 |  |  | 0.09236
[13 empty] | C Non choked w/ reducers | 5 |  | 19.8844 |  |  | 60.43 |  |  | 264.6663 |  |  | #NUM! |  |  | 542.5935 |  |  | 207.7486 |  |  | 156.493 |  |  | 160.9502 |  |  | 99.3266 |  |  | 505.2643
[13 empty] | C Choked w/ reducers | 5 |  | 17.755 |  |  | 52.7243 |  |  | 164.3127 |  |  | 2807.2343 |  |  | 270.8749 |  |  | 145.9763 |  |  | 108.3787 |  |  | 94.8717 |  |  | 81.9098 |  |  | 115.4505
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 19.8844 |  |  | 60.43 |  |  | 264.6663 |  |  | #NUM! |  |  | 270.8749 |  |  | 145.9763 |  |  | 108.3787 |  |  | 94.8717 |  |  | 81.9098 |  |  | 115.4505
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 15.1544 | 3739.4397 |  | 48.83 | 10705.7288 |  | 241.6663 | 26214.3974 |  | 18000 | 51058.955 |  | 18000 | 85661.0431 |  | 18000 | 125024.6255 |  | 18000 | 165193.9083 |  | 18000 | 203583.6411 |  | 18000 | 236354.2872 |  | 18000 | 277143.9898
[13 empty] | Next iteration flow rate |  |  | 3814.2285 | Abs Value of | Flow this | 10812.7861 | Abs Value of | Flow this | 26476.5413 | Abs Value of | Flow this | 51569.5445 | Abs Value of | Flow this | 86517.6535 | Abs Value of | Flow this | 126274.8717 | Abs Value of | Flow this | 166845.8473 | Abs Value of | Flow this | 205619.4776 | Abs Value of | Flow this | 238717.8301 | Abs Value of | Flow this | 279915.4297 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.7708 |  |  | 86.5386 |  |  | 68.0961 |  |  | 6.2601 |  |  | -146.1155 |  |  | -413.2381 |  |  | -788.7297 |  |  | -1244.7251 |  |  | -1709.0879 |  |  | -2383.7254
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43303 |  |  | 0.41744 |  |  | 0.32848 |  |  | 0.030197 |  |  | -0.70482 |  |  | -1.9934 |  |  | -3.8046 |  |  | -6.0042 |  |  | -8.2442 |  |  | -11.4985
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7708 |  |  | 26.5386 |  |  | 8.0961 |  |  | -53.7399 |  |  | -206.1155 |  |  | -473.2381 |  |  | -848.7297 |  |  | -1304.7251 |  |  | -1769.0879 |  |  | -2443.7254
[13 empty] | Press drop ratio this iteration |  |  | 0.33163 |  |  | 0.30667 |  |  | 0.11889 |  |  | -8.5846 |  |  | 1.4106 |  |  | 1.1452 |  |  | 1.0761 |  |  | 1.0482 |  |  | 1.0351 |  |  | 1.0252
[13 empty] | Expansion factor | 12 |  | 0.82728 |  |  | 0.84032 |  |  | 0.9375 |  |  | 5.5761 |  |  | 0.22473 |  |  | 0.33285 |  |  | 0.32556 |  |  | 0.26545 |  |  | 0.41573 |  |  | 0.092825
[13 empty] | C Non choked w/ reducers | 5 |  | 20.2885 |  |  | 61.1215 |  |  | 274.4303 |  |  | #NUM! |  |  | 515.4653 |  |  | 203.8259 |  |  | 154.2012 |  |  | 158.766 |  |  | 98.1749 |  |  | 497.5045
[13 empty] | C Choked w/ reducers | 5 |  | 18.1137 |  |  | 53.2963 |  |  | 167.0187 |  |  | 3584.6836 |  |  | 264.8641 |  |  | 143.8967 |  |  | 107.0589 |  |  | 93.7955 |  |  | 81.0128 |  |  | 114.2205
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 20.2885 |  |  | 61.1215 |  |  | 274.4303 |  |  | #NUM! |  |  | 264.8641 |  |  | 143.8967 |  |  | 107.0589 |  |  | 93.7955 |  |  | 81.0128 |  |  | 114.2205
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 15.5585 | 3814.2285 |  | 49.5215 | 10812.7861 |  | 251.4303 | 26476.5413 |  | 18000 | 51569.5445 |  | 18000 | 86517.6535 |  | 18000 | 126274.8717 |  | 18000 | 166845.8473 |  | 18000 | 205619.4776 |  | 18000 | 238717.8301 |  | 18000 | 279915.4297
[13 empty] | Next iteration flow rate |  |  | 3890.513 | Abs Value of | Flow this | 10920.914 | Abs Value of | Flow this | 26741.3068 | Abs Value of | Flow this | 52085.24 | Abs Value of | Flow this | 87382.8301 | Abs Value of | Flow this | 127537.6204 | Abs Value of | Flow this | 168514.3058 | Abs Value of | Flow this | 207675.6723 | Abs Value of | Flow this | 241105.0084 | Abs Value of | Flow this | 282714.584 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.7523 |  |  | 86.4644 |  |  | 67.6512 |  |  | 4.5723 |  |  | -150.8661 |  |  | -423.3578 |  |  | -806.3967 |  |  | -1271.5577 |  |  | -1745.2542 |  |  | -2433.4519
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43294 |  |  | 0.41708 |  |  | 0.32633 |  |  | 0.022055 |  |  | -0.72774 |  |  | -2.0422 |  |  | -3.8899 |  |  | -6.1337 |  |  | -8.4187 |  |  | -11.7384
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7523 |  |  | 26.4644 |  |  | 7.6512 |  |  | -55.4277 |  |  | -210.8661 |  |  | -483.3578 |  |  | -866.3967 |  |  | -1331.5577 |  |  | -1805.2542 |  |  | -2493.4519
[13 empty] | Press drop ratio this iteration |  |  | 0.33149 |  |  | 0.30607 |  |  | 0.1131 |  |  | -12.1226 |  |  | 1.3977 |  |  | 1.1417 |  |  | 1.0744 |  |  | 1.0472 |  |  | 1.0344 |  |  | 1.0247
[13 empty] | Expansion factor | 12 |  | 0.82736 |  |  | 0.84063 |  |  | 0.94055 |  |  | 7.4621 |  |  | 0.23184 |  |  | 0.33487 |  |  | 0.3266 |  |  | 0.26616 |  |  | 0.41614 |  |  | 0.093281
[13 empty] | C Non choked w/ reducers | 5 |  | 20.7011 |  |  | 61.8229 |  |  | 285.1287 |  |  | #NUM! |  |  | 491.0264 |  |  | 200.0334 |  |  | 151.9616 |  |  | 156.6255 |  |  | 97.0401 |  |  | 489.9328
[13 empty] | C Choked w/ reducers | 5 |  | 18.4798 |  |  | 53.8755 |  |  | 169.7982 |  |  | 4957.0119 |  |  | 259.0891 |  |  | 141.8616 |  |  | 105.7606 |  |  | 92.7344 |  |  | 80.1273 |  |  | 113.0053
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 20.7011 |  |  | 61.8229 |  |  | 285.1287 |  |  | #NUM! |  |  | 259.0891 |  |  | 141.8616 |  |  | 105.7606 |  |  | 92.7344 |  |  | 80.1273 |  |  | 113.0053
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 15.9711 | 3890.513 |  | 50.2229 | 10920.914 |  | 262.1287 | 26741.3068 |  | 18000 | 52085.24 |  | 18000 | 87382.8301 |  | 18000 | 127537.6204 |  | 18000 | 168514.3058 |  | 18000 | 207675.6723 |  | 18000 | 241105.0084 |  | 18000 | 282714.584
[13 empty] | Next iteration flow rate |  |  | 3968.3233 | Abs Value of | Flow this | 11030.1231 | Abs Value of | Flow this | 27008.7198 | Abs Value of | Flow this | 52606.0924 | Abs Value of | Flow this | 88256.6584 | Abs Value of | Flow this | 128812.9966 | Abs Value of | Flow this | 170199.4489 | Abs Value of | Flow this | 209752.4291 | Abs Value of | Flow this | 243516.0584 | Abs Value of | Flow this | 285541.7298 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.733 |  |  | 86.3887 |  |  | 67.1974 |  |  | 2.8505 |  |  | -155.7121 |  |  | -433.6809 |  |  | -824.4189 |  |  | -1298.9297 |  |  | -1782.1474 |  |  | -2484.1779
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43285 |  |  | 0.41672 |  |  | 0.32414 |  |  | 0.01375 |  |  | -0.75112 |  |  | -2.092 |  |  | -3.9768 |  |  | -6.2657 |  |  | -8.5966 |  |  | -11.9831
[13 empty] | Delta P at this iteration flow rate |  |  | 29.733 |  |  | 26.3887 |  |  | 7.1974 |  |  | -57.1495 |  |  | -215.7121 |  |  | -493.6809 |  |  | -884.4189 |  |  | -1358.9297 |  |  | -1842.1474 |  |  | -2544.1779
[13 empty] | Press drop ratio this iteration |  |  | 0.33135 |  |  | 0.30546 |  |  | 0.10711 |  |  | -20.0487 |  |  | 1.3853 |  |  | 1.1384 |  |  | 1.0728 |  |  | 1.0462 |  |  | 1.0337 |  |  | 1.0242
[13 empty] | Expansion factor | 12 |  | 0.82743 |  |  | 0.84095 |  |  | 0.9437 |  |  | 11.6871 |  |  | 0.23864 |  |  | 0.33683 |  |  | 0.32762 |  |  | 0.26686 |  |  | 0.41654 |  |  | 0.093726
[13 empty] | C Non choked w/ reducers | 5 |  | 21.1223 |  |  | 62.5344 |  |  | 296.9276 |  |  | #NUM! |  |  | 468.8863 |  |  | 196.3642 |  |  | 149.7723 |  |  | 154.5273 |  |  | 95.922 |  |  | 482.5423
[13 empty] | C Choked w/ reducers | 5 |  | 18.8534 |  |  | 54.4619 |  |  | 172.6544 |  |  | 8030.568 |  |  | 253.5361 |  |  | 139.8697 |  |  | 104.4831 |  |  | 91.688 |  |  | 79.2533 |  |  | 111.8048
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 21.1223 |  |  | 62.5344 |  |  | 296.9276 |  |  | #NUM! |  |  | 253.5361 |  |  | 139.8697 |  |  | 104.4831 |  |  | 91.688 |  |  | 79.2533 |  |  | 111.8048
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 16.3923 | 3968.3233 |  | 50.9344 | 11030.1231 |  | 273.9276 | 27008.7198 |  | 18000 | 52606.0924 |  | 18000 | 88256.6584 |  | 18000 | 128812.9966 |  | 18000 | 170199.4489 |  | 18000 | 209752.4291 |  | 18000 | 243516.0584 |  | 18000 | 285541.7298
[13 empty] | Next iteration flow rate |  |  | 4047.6898 | Abs Value of | Flow this | 11140.4243 | Abs Value of | Flow this | 27278.807 | Abs Value of | Flow this | 53132.1533 | Abs Value of | Flow this | 89139.2249 | Abs Value of | Flow this | 130101.1266 | Abs Value of | Flow this | 171901.4434 | Abs Value of | Flow this | 211849.9533 | Abs Value of | Flow this | 245951.219 | Abs Value of | Flow this | 288397.1471 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.7129 |  |  | 86.3115 |  |  | 66.7344 |  |  | 1.0942 |  |  | -160.6555 |  |  | -444.2115 |  |  | -842.8034 |  |  | -1326.8518 |  |  | -1819.7822 |  |  | -2535.9235
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43275 |  |  | 0.41635 |  |  | 0.32191 |  |  | 0.0052781 |  |  | -0.77496 |  |  | -2.1428 |  |  | -4.0655 |  |  | -6.4004 |  |  | -8.7782 |  |  | -12.2327
[13 empty] | Delta P at this iteration flow rate |  |  | 29.7129 |  |  | 26.3115 |  |  | 6.7344 |  |  | -58.9058 |  |  | -220.6555 |  |  | -504.2115 |  |  | -902.8034 |  |  | -1386.8518 |  |  | -1879.7822 |  |  | -2595.9235
[13 empty] | Press drop ratio this iteration |  |  | 0.3312 |  |  | 0.30484 |  |  | 0.10091 |  |  | -53.8348 |  |  | 1.3735 |  |  | 1.1351 |  |  | 1.0712 |  |  | 1.0452 |  |  | 1.033 |  |  | 1.0237
[13 empty] | Expansion factor | 12 |  | 0.82751 |  |  | 0.84127 |  |  | 0.94695 |  |  | 29.697 |  |  | 0.24516 |  |  | 0.33874 |  |  | 0.32862 |  |  | 0.26754 |  |  | 0.41694 |  |  | 0.094162
[13 empty] | C Non choked w/ reducers | 5 |  | 21.5524 |  |  | 63.2564 |  |  | 310.0376 |  |  | #NUM! |  |  | 448.727 |  |  | 192.812 |  |  | 147.6316 |  |  | 152.47 |  |  | 94.8201 |  |  | 475.3261
[13 empty] | C Choked w/ reducers | 5 |  | 19.2348 |  |  | 55.0557 |  |  | 175.5907 |  |  | 21129.9091 |  |  | 248.192 |  |  | 137.9194 |  |  | 103.226 |  |  | 90.6561 |  |  | 78.3904 |  |  | 110.6186
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 21.5524 |  |  | 63.2564 |  |  | 310.0376 |  |  | #NUM! |  |  | 248.192 |  |  | 137.9194 |  |  | 103.226 |  |  | 90.6561 |  |  | 78.3904 |  |  | 110.6186
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 16.8224 | 4047.6898 |  | 51.6564 | 11140.4243 |  | 287.0376 | 27278.807 |  | 18000 | 53132.1533 |  | 18000 | 89139.2249 |  | 18000 | 130101.1266 |  | 18000 | 171901.4434 |  | 18000 | 211849.9533 |  | 18000 | 245951.219 |  | 18000 | 288397.1471
[13 empty] | Next iteration flow rate |  |  | 4128.6436 | Abs Value of | Flow this | 11251.8286 | Abs Value of | Flow this | 27551.5951 | Abs Value of | Flow this | 53663.4748 | Abs Value of | Flow this | 90030.6172 | Abs Value of | Flow this | 131402.1379 | Abs Value of | Flow this | 173620.4578 | Abs Value of | Flow this | 213968.4529 | Abs Value of | Flow this | 248410.7312 | Abs Value of | Flow this | 291281.1186 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.692 |  |  | 86.2327 |  |  | 66.2622 |  |  | -0.69744 |  |  | -165.6983 |  |  | -454.9538 |  |  | -861.5574 |  |  | -1355.3351 |  |  | -1858.1735 |  |  | -2588.7092
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43265 |  |  | 0.41597 |  |  | 0.31963 |  |  | -0.0033643 |  |  | -0.79929 |  |  | -2.1946 |  |  | -4.1559 |  |  | -6.5378 |  |  | -8.9634 |  |  | -12.4873
[13 empty] | Delta P at this iteration flow rate |  |  | 29.692 |  |  | 26.2327 |  |  | 6.2622 |  |  | -60.6974 |  |  | -225.6983 |  |  | -514.9538 |  |  | -921.5574 |  |  | -1415.3351 |  |  | -1918.1735 |  |  | -2648.7092
[13 empty] | Press drop ratio this iteration |  |  | 0.33104 |  |  | 0.30421 |  |  | 0.094506 |  |  | 87.0293 |  |  | 1.3621 |  |  | 1.1319 |  |  | 1.0696 |  |  | 1.0443 |  |  | 1.0323 |  |  | 1.0232
[13 empty] | Expansion factor | 12 |  | 0.82759 |  |  | 0.8416 |  |  | 0.95032 |  |  | -45.3916 |  |  | 0.2514 |  |  | 0.3406 |  |  | 0.32959 |  |  | 0.2682 |  |  | 0.41732 |  |  | 0.094589
[13 empty] | C Non choked w/ reducers | 5 |  | 21.9916 |  |  | 63.9888 |  |  | 324.7311 |  |  | -41.7042 |  |  | 430.287 |  |  | 189.371 |  |  | 145.5376 |  |  | 150.4525 |  |  | 93.7342 |  |  | 468.278
[13 empty] | C Choked w/ reducers | 5 |  | 19.6241 |  |  | 55.6571 |  |  | 178.6106 |  |  | 33481.8287 |  |  | 243.045 |  |  | 136.0095 |  |  | 101.9888 |  |  | 89.6385 |  |  | 77.5385 |  |  | 109.4467
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 21.9916 |  |  | 63.9888 |  |  | 324.7311 |  |  | 33481.8287 |  |  | 243.045 |  |  | 136.0095 |  |  | 101.9888 |  |  | 89.6385 |  |  | 77.5385 |  |  | 109.4467
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 17.2616 | 4128.6436 |  | 52.3888 | 11251.8286 |  | 301.7311 | 27551.5951 |  | 18000 | 53663.4748 |  | 18000 | 90030.6172 |  | 18000 | 131402.1379 |  | 18000 | 173620.4578 |  | 18000 | 213968.4529 |  | 18000 | 248410.7312 |  | 18000 | 291281.1186
[13 empty] | Next iteration flow rate |  |  | 4211.2164 | Abs Value of | Flow this | 11364.3469 | Abs Value of | Flow this | 27827.111 | Abs Value of | Flow this | 54200.1096 | Abs Value of | Flow this | 90930.9234 | Abs Value of | Flow this | 132716.1593 | Abs Value of | Flow this | 175356.6624 | Abs Value of | Flow this | 216108.1374 | Abs Value of | Flow this | 250894.8385 | Abs Value of | Flow this | 294193.9298 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.6702 |  |  | 86.1524 |  |  | 65.7804 |  |  | -2.5251 |  |  | -170.8425 |  |  | -465.912 |  |  | -880.6883 |  |  | -1384.391 |  |  | -1897.3364 |  |  | -2642.5559
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43255 |  |  | 0.41558 |  |  | 0.31731 |  |  | -0.01218 |  |  | -0.8241 |  |  | -2.2474 |  |  | -4.2482 |  |  | -6.678 |  |  | -9.1523 |  |  | -12.747
[13 empty] | Delta P at this iteration flow rate |  |  | 29.6702 |  |  | 26.1524 |  |  | 5.7804 |  |  | -62.5251 |  |  | -230.8425 |  |  | -525.912 |  |  | -940.6883 |  |  | -1444.391 |  |  | -1957.3364 |  |  | -2702.5559
[13 empty] | Press drop ratio this iteration |  |  | 0.33088 |  |  | 0.30356 |  |  | 0.087875 |  |  | 24.7616 |  |  | 1.3512 |  |  | 1.1288 |  |  | 1.0681 |  |  | 1.0433 |  |  | 1.0316 |  |  | 1.0227
[13 empty] | Expansion factor | 12 |  | 0.82767 |  |  | 0.84194 |  |  | 0.95381 |  |  | -12.1993 |  |  | 0.25739 |  |  | 0.34241 |  |  | 0.33054 |  |  | 0.26886 |  |  | 0.4177 |  |  | 0.095007
[13 empty] | C Non choked w/ reducers | 5 |  | 22.4401 |  |  | 64.7321 |  |  | 341.3679 |  |  | -81.1545 |  |  | 413.349 |  |  | 186.0356 |  |  | 143.4889 |  |  | 148.4735 |  |  | 92.6638 |  |  | 461.3917
[13 empty] | C Choked w/ reducers | 5 |  | 20.0214 |  |  | 56.2661 |  |  | 181.7179 |  |  | 9340.2835 |  |  | 238.0841 |  |  | 134.1387 |  |  | 100.771 |  |  | 88.6347 |  |  | 76.6974 |  |  | 108.2886
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 22.4401 |  |  | 64.7321 |  |  | 341.3679 |  |  | 9340.2835 |  |  | 238.0841 |  |  | 134.1387 |  |  | 100.771 |  |  | 88.6347 |  |  | 76.6974 |  |  | 108.2886
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 17.7101 | 4211.2164 |  | 53.1321 | 11364.3469 |  | 318.3679 | 27827.111 |  | 18000 | 54200.1096 |  | 18000 | 90930.9234 |  | 18000 | 132716.1593 |  | 18000 | 175356.6624 |  | 18000 | 216108.1374 |  | 18000 | 250894.8385 |  | 18000 | 294193.9298
[13 empty] | Next iteration flow rate |  |  | 4295.4408 | Abs Value of | Flow this | 11477.9903 | Abs Value of | Flow this | 28105.3822 | Abs Value of | Flow this | 54742.1107 | Abs Value of | Flow this | 91840.2326 | Abs Value of | Flow this | 134043.3208 | Abs Value of | Flow this | 177110.229 | Abs Value of | Flow this | 218269.2188 | Abs Value of | Flow this | 253403.7869 | Abs Value of | Flow this | 297135.8691 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.6476 |  |  | 86.0704 |  |  | 65.289 |  |  | -4.3895 |  |  | -176.0901 |  |  | -477.0905 |  |  | -900.2038 |  |  | -1414.0309 |  |  | -1937.2865 |  |  | -2697.4849
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43244 |  |  | 0.41518 |  |  | 0.31494 |  |  | -0.021174 |  |  | -0.84941 |  |  | -2.3014 |  |  | -4.3424 |  |  | -6.8209 |  |  | -9.345 |  |  | -13.012
[13 empty] | Delta P at this iteration flow rate |  |  | 29.6476 |  |  | 26.0704 |  |  | 5.289 |  |  | -64.3895 |  |  | -236.0901 |  |  | -537.0905 |  |  | -960.2038 |  |  | -1474.0309 |  |  | -1997.2865 |  |  | -2757.4849
[13 empty] | Press drop ratio this iteration |  |  | 0.33071 |  |  | 0.3029 |  |  | 0.081009 |  |  | 14.6691 |  |  | 1.3407 |  |  | 1.1258 |  |  | 1.0667 |  |  | 1.0424 |  |  | 1.031 |  |  | 1.0222
[13 empty] | Expansion factor | 12 |  | 0.82776 |  |  | 0.84229 |  |  | 0.95742 |  |  | -6.8195 |  |  | 0.26315 |  |  | 0.34417 |  |  | 0.33146 |  |  | 0.26949 |  |  | 0.41806 |  |  | 0.095416
[13 empty] | C Non choked w/ reducers | 5 |  | 22.8981 |  |  | 65.4864 |  |  | 360.4342 |  |  | -109.5903 |  |  | 397.7311 |  |  | 182.8008 |  |  | 141.4839 |  |  | 146.5319 |  |  | 91.6087 |  |  | 454.6617
[13 empty] | C Choked w/ reducers | 5 |  | 20.427 |  |  | 56.8828 |  |  | 184.9166 |  |  | 5426.8218 |  |  | 233.2989 |  |  | 132.3057 |  |  | 99.5723 |  |  | 87.6445 |  |  | 75.8669 |  |  | 107.1444
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 22.8981 |  |  | 65.4864 |  |  | 360.4342 |  |  | 5426.8218 |  |  | 233.2989 |  |  | 132.3057 |  |  | 99.5723 |  |  | 87.6445 |  |  | 75.8669 |  |  | 107.1444
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18.1681 | 4295.4408 |  | 53.8864 | 11477.9903 |  | 337.4342 | 28105.3822 |  | 18000 | 54742.1107 |  | 18000 | 91840.2326 |  | 18000 | 134043.3208 |  | 18000 | 177110.229 |  | 18000 | 218269.2188 |  | 18000 | 253403.7869 |  | 18000 | 297135.8691
[13 empty] | Next iteration flow rate |  |  | 4381.3496 | Abs Value of | Flow this | 11592.7702 | Abs Value of | Flow this | 28386.436 | Abs Value of | Flow this | 55289.5318 | Abs Value of | Flow this | 92758.6349 | Abs Value of | Flow this | 135383.7541 | Abs Value of | Flow this | 178881.3313 | Abs Value of | Flow this | 220451.911 | Abs Value of | Flow this | 255937.8248 | Abs Value of | Flow this | 300107.2278 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.6241 |  |  | 85.9868 |  |  | 64.7877 |  |  | -6.2913 |  |  | -181.4431 |  |  | -488.4936 |  |  | -920.1115 |  |  | -1444.2665 |  |  | -1978.0395 |  |  | -2753.518
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43232 |  |  | 0.41478 |  |  | 0.31252 |  |  | -0.030348 |  |  | -0.87524 |  |  | -2.3564 |  |  | -4.4384 |  |  | -6.9668 |  |  | -9.5416 |  |  | -13.2823
[13 empty] | Delta P at this iteration flow rate |  |  | 29.6241 |  |  | 25.9868 |  |  | 4.7877 |  |  | -66.2913 |  |  | -241.4431 |  |  | -548.4936 |  |  | -980.1115 |  |  | -1504.2665 |  |  | -2038.0395 |  |  | -2813.518
[13 empty] | Press drop ratio this iteration |  |  | 0.33054 |  |  | 0.30222 |  |  | 0.073898 |  |  | 10.537 |  |  | 1.3307 |  |  | 1.1228 |  |  | 1.0652 |  |  | 1.0415 |  |  | 1.0303 |  |  | 1.0218
[13 empty] | Expansion factor | 12 |  | 0.82785 |  |  | 0.84264 |  |  | 0.96116 |  |  | -4.6168 |  |  | 0.26867 |  |  | 0.34588 |  |  | 0.33237 |  |  | 0.27011 |  |  | 0.41842 |  |  | 0.095817
[13 empty] | C Non choked w/ reducers | 5 |  | 23.3658 |  |  | 66.2521 |  |  | 382.6071 |  |  | -134.5913 |  |  | 383.2799 |  |  | 179.6617 |  |  | 139.5211 |  |  | 144.6266 |  |  | 90.5686 |  |  | 448.0822
[13 empty] | C Choked w/ reducers | 5 |  | 20.841 |  |  | 57.5075 |  |  | 188.2109 |  |  | 3824.1657 |  |  | 228.6802 |  |  | 130.5094 |  |  | 98.3921 |  |  | 86.6678 |  |  | 75.0469 |  |  | 106.0137
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 23.3658 |  |  | 66.2521 |  |  | 382.6071 |  |  | 3824.1657 |  |  | 228.6802 |  |  | 130.5094 |  |  | 98.3921 |  |  | 86.6678 |  |  | 75.0469 |  |  | 106.0137
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18.6358 | 4381.3496 |  | 54.6521 | 11592.7702 |  | 359.6071 | 28386.436 |  | 18000 | 55289.5318 |  | 18000 | 92758.6349 |  | 18000 | 135383.7541 |  | 18000 | 178881.3313 |  | 18000 | 220451.911 |  | 18000 | 255937.8248 |  | 18000 | 300107.2278
[13 empty] | Next iteration flow rate |  |  | 4468.9766 | Abs Value of | Flow this | 11708.6979 | Abs Value of | Flow this | 28670.3003 | Abs Value of | Flow this | 55842.4271 | Abs Value of | Flow this | 93686.2213 | Abs Value of | Flow this | 136737.5916 | Abs Value of | Flow this | 180670.1446 | Abs Value of | Flow this | 222656.4301 | Abs Value of | Flow this | 258497.203 | Abs Value of | Flow this | 303108.3 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.5996 |  |  | 85.9015 |  |  | 64.2763 |  |  | -8.2314 |  |  | -186.9037 |  |  | -500.1259 |  |  | -940.4193 |  |  | -1475.1099 |  |  | -2019.6118 |  |  | -2810.6773
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43221 |  |  | 0.41437 |  |  | 0.31005 |  |  | -0.039706 |  |  | -0.90158 |  |  | -2.4125 |  |  | -4.5363 |  |  | -7.1156 |  |  | -9.7421 |  |  | -13.558
[13 empty] | Delta P at this iteration flow rate |  |  | 29.5996 |  |  | 25.9015 |  |  | 4.2763 |  |  | -68.2314 |  |  | -246.9037 |  |  | -560.1259 |  |  | -1000.4193 |  |  | -1535.1099 |  |  | -2079.6118 |  |  | -2870.6773
[13 empty] | Press drop ratio this iteration |  |  | 0.33035 |  |  | 0.30153 |  |  | 0.06653 |  |  | 8.2892 |  |  | 1.321 |  |  | 1.12 |  |  | 1.0638 |  |  | 1.0407 |  |  | 1.0297 |  |  | 1.0213
[13 empty] | Expansion factor | 12 |  | 0.82795 |  |  | 0.843 |  |  | 0.96503 |  |  | -3.4186 |  |  | 0.27398 |  |  | 0.34754 |  |  | 0.33325 |  |  | 0.27072 |  |  | 0.41878 |  |  | 0.096209
[13 empty] | C Non choked w/ reducers | 5 |  | 23.8435 |  |  | 67.0292 |  |  | 408.8632 |  |  | -158.1982 |  |  | 369.8647 |  |  | 176.6139 |  |  | 137.5991 |  |  | 142.7565 |  |  | 89.5431 |  |  | 441.6482
[13 empty] | C Choked w/ reducers | 5 |  | 21.2636 |  |  | 58.1403 |  |  | 191.6054 |  |  | 2952.0656 |  |  | 224.219 |  |  | 128.7487 |  |  | 97.2301 |  |  | 85.7042 |  |  | 74.2371 |  |  | 104.8963
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 23.8435 |  |  | 67.0292 |  |  | 408.8632 |  |  | 2952.0656 |  |  | 224.219 |  |  | 128.7487 |  |  | 97.2301 |  |  | 85.7042 |  |  | 74.2371 |  |  | 104.8963
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 19.1135 | 4468.9766 |  | 55.4292 | 11708.6979 |  | 385.8632 | 28670.3003 |  | 18000 | 55842.4271 |  | 18000 | 93686.2213 |  | 18000 | 136737.5916 |  | 18000 | 180670.1446 |  | 18000 | 222656.4301 |  | 18000 | 258497.203 |  | 18000 | 303108.3
[13 empty] | Next iteration flow rate |  |  | 4558.3561 | Abs Value of | Flow this | 11825.7849 | Abs Value of | Flow this | 28957.0033 | Abs Value of | Flow this | 56400.8514 | Abs Value of | Flow this | 94623.0835 | Abs Value of | Flow this | 138104.9675 | Abs Value of | Flow this | 182476.8461 | Abs Value of | Flow this | 224882.9944 | Abs Value of | Flow this | 261082.1751 | Abs Value of | Flow this | 306139.383 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.5741 |  |  | 85.8145 |  |  | 63.7546 |  |  | -10.2105 |  |  | -192.4741 |  |  | -511.9921 |  |  | -961.1354 |  |  | -1506.5732 |  |  | -2062.0196 |  |  | -2868.9856
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43208 |  |  | 0.41395 |  |  | 0.30754 |  |  | -0.049253 |  |  | -0.92845 |  |  | -2.4697 |  |  | -4.6363 |  |  | -7.2673 |  |  | -9.9467 |  |  | -13.8393
[13 empty] | Delta P at this iteration flow rate |  |  | 29.5741 |  |  | 25.8145 |  |  | 3.7546 |  |  | -70.2105 |  |  | -252.4741 |  |  | -571.9921 |  |  | -1021.1354 |  |  | -1566.5732 |  |  | -2122.0196 |  |  | -2928.9856
[13 empty] | Press drop ratio this iteration |  |  | 0.33016 |  |  | 0.30082 |  |  | 0.058891 |  |  | 6.8763 |  |  | 1.3117 |  |  | 1.1172 |  |  | 1.0624 |  |  | 1.0398 |  |  | 1.0291 |  |  | 1.0209
[13 empty] | Expansion factor | 12 |  | 0.82805 |  |  | 0.84337 |  |  | 0.96904 |  |  | -2.6655 |  |  | 0.27909 |  |  | 0.34916 |  |  | 0.33411 |  |  | 0.27132 |  |  | 0.41912 |  |  | 0.096593
[13 empty] | C Non choked w/ reducers | 5 |  | 24.3314 |  |  | 67.8182 |  |  | 440.6733 |  |  | -181.3853 |  |  | 357.3743 |  |  | 173.6531 |  |  | 135.7167 |  |  | 140.9207 |  |  | 88.5319 |  |  | 435.3546
[13 empty] | C Choked w/ reducers | 5 |  | 21.695 |  |  | 58.7812 |  |  | 195.105 |  |  | 2403.6709 |  |  | 219.9072 |  |  | 127.0224 |  |  | 96.0857 |  |  | 84.7535 |  |  | 73.4375 |  |  | 103.7921
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 24.3314 |  |  | 67.8182 |  |  | 440.6733 |  |  | 2403.6709 |  |  | 219.9072 |  |  | 127.0224 |  |  | 96.0857 |  |  | 84.7535 |  |  | 73.4375 |  |  | 103.7921
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 19.6014 | 4558.3561 |  | 56.2182 | 11825.7849 |  | 417.6733 | 28957.0033 |  | 18000 | 56400.8514 |  | 18000 | 94623.0835 |  | 18000 | 138104.9675 |  | 18000 | 182476.8461 |  | 18000 | 224882.9944 |  | 18000 | 261082.1751 |  | 18000 | 306139.383
[13 empty] | Next iteration flow rate |  |  | 4649.5232 | Abs Value of | Flow this | 11944.0428 | Abs Value of | Flow this | 29246.5734 | Abs Value of | Flow this | 56964.8599 | Abs Value of | Flow this | 95569.3143 | Abs Value of | Flow this | 139486.0172 | Abs Value of | Flow this | 184301.6145 | Abs Value of | Flow this | 227131.8243 | Abs Value of | Flow this | 263692.9968 | Abs Value of | Flow this | 309200.7769 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.5476 |  |  | 85.7257 |  |  | 63.2224 |  |  | -12.2293 |  |  | -198.1565 |  |  | -524.0968 |  |  | -982.2679 |  |  | -1538.669 |  |  | -2105.2798 |  |  | -2928.4658
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43196 |  |  | 0.41352 |  |  | 0.30497 |  |  | -0.058991 |  |  | -0.95586 |  |  | -2.5281 |  |  | -4.7382 |  |  | -7.4222 |  |  | -10.1553 |  |  | -14.1262
[13 empty] | Delta P at this iteration flow rate |  |  | 29.5476 |  |  | 25.7257 |  |  | 3.2224 |  |  | -72.2293 |  |  | -258.1565 |  |  | -584.0968 |  |  | -1042.2679 |  |  | -1598.669 |  |  | -2165.2798 |  |  | -2988.4658
[13 empty] | Press drop ratio this iteration |  |  | 0.32997 |  |  | 0.30009 |  |  | 0.05097 |  |  | 5.9062 |  |  | 1.3028 |  |  | 1.1145 |  |  | 1.0611 |  |  | 1.039 |  |  | 1.0285 |  |  | 1.0205
[13 empty] | Expansion factor | 12 |  | 0.82815 |  |  | 0.84374 |  |  | 0.97321 |  |  | -2.1484 |  |  | 0.284 |  |  | 0.35074 |  |  | 0.33495 |  |  | 0.2719 |  |  | 0.41946 |  |  | 0.096969
[13 empty] | C Non choked w/ reducers | 5 |  | 24.8297 |  |  | 68.6193 |  |  | 480.3806 |  |  | -204.765 |  |  | 345.7125 |  |  | 170.7755 |  |  | 133.8724 |  |  | 139.1182 |  |  | 87.5348 |  |  | 429.1967
[13 empty] | C Choked w/ reducers | 5 |  | 22.1355 |  |  | 59.4305 |  |  | 198.7147 |  |  | 2026.934 |  |  | 215.7371 |  |  | 125.3295 |  |  | 94.9587 |  |  | 83.8155 |  |  | 72.6477 |  |  | 102.7008
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 24.8297 |  |  | 68.6193 |  |  | 480.3806 |  |  | 2026.934 |  |  | 215.7371 |  |  | 125.3295 |  |  | 94.9587 |  |  | 83.8155 |  |  | 72.6477 |  |  | 102.7008
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 20.0997 | 4649.5232 |  | 57.0193 | 11944.0428 |  | 457.3806 | 29246.5734 |  | 18000 | 56964.8599 |  | 18000 | 95569.3143 |  | 18000 | 139486.0172 |  | 18000 | 184301.6145 |  | 18000 | 227131.8243 |  | 18000 | 263692.9968 |  | 18000 | 309200.7769
[13 empty] | Next iteration flow rate |  |  | 4742.5137 | Abs Value of | Flow this | 12063.4832 | Abs Value of | Flow this | 29539.0391 | Abs Value of | Flow this | 57534.5085 | Abs Value of | Flow this | 96525.0075 | Abs Value of | Flow this | 140880.8774 | Abs Value of | Flow this | 186144.6307 | Abs Value of | Flow this | 229403.1426 | Abs Value of | Flow this | 266329.9268 | Abs Value of | Flow this | 312292.7846 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.52 |  |  | 85.6352 |  |  | 62.6796 |  |  | -14.2888 |  |  | -203.9531 |  |  | -536.4447 |  |  | -1003.8251 |  |  | -1571.4099 |  |  | -2149.4096 |  |  | -2989.1416
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43182 |  |  | 0.41308 |  |  | 0.30235 |  |  | -0.068925 |  |  | -0.98382 |  |  | -2.5877 |  |  | -4.8422 |  |  | -7.5801 |  |  | -10.3682 |  |  | -14.4189
[13 empty] | Delta P at this iteration flow rate |  |  | 29.52 |  |  | 25.6352 |  |  | 2.6796 |  |  | -74.2888 |  |  | -263.9531 |  |  | -596.4447 |  |  | -1063.8251 |  |  | -1631.4099 |  |  | -2209.4096 |  |  | -3049.1416
[13 empty] | Press drop ratio this iteration |  |  | 0.32976 |  |  | 0.29935 |  |  | 0.042751 |  |  | 5.1991 |  |  | 1.2942 |  |  | 1.1118 |  |  | 1.0598 |  |  | 1.0382 |  |  | 1.0279 |  |  | 1.0201
[13 empty] | Expansion factor | 12 |  | 0.82826 |  |  | 0.84413 |  |  | 0.97753 |  |  | -1.7714 |  |  | 0.28873 |  |  | 0.35227 |  |  | 0.33577 |  |  | 0.27247 |  |  | 0.41979 |  |  | 0.097337
[13 empty] | C Non choked w/ reducers | 5 |  | 25.3387 |  |  | 69.4328 |  |  | 532.0033 |  |  | -228.8034 |  |  | 334.7963 |  |  | 167.9774 |  |  | 132.0652 |  |  | 137.3481 |  |  | 86.5515 |  |  | 423.1699
[13 empty] | C Choked w/ reducers | 5 |  | 22.5852 |  |  | 60.0883 |  |  | 202.4401 |  |  | 1752.1405 |  |  | 211.7017 |  |  | 123.6691 |  |  | 93.8487 |  |  | 82.8898 |  |  | 71.8677 |  |  | 101.6223
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 25.3387 |  |  | 69.4328 |  |  | 532.0033 |  |  | 1752.1405 |  |  | 211.7017 |  |  | 123.6691 |  |  | 93.8487 |  |  | 82.8898 |  |  | 71.8677 |  |  | 101.6223
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 20.6087 | 4742.5137 |  | 57.8328 | 12063.4832 |  | 509.0033 | 29539.0391 |  | 18000 | 57534.5085 |  | 18000 | 96525.0075 |  | 18000 | 140880.8774 |  | 18000 | 186144.6307 |  | 18000 | 229403.1426 |  | 18000 | 266329.9268 |  | 18000 | 312292.7846
[13 empty] | Next iteration flow rate |  |  | 4837.364 | Abs Value of | Flow this | 12184.118 | Abs Value of | Flow this | 29834.4295 | Abs Value of | Flow this | 58109.8536 | Abs Value of | Flow this | 97490.2575 | Abs Value of | Flow this | 142289.6861 | Abs Value of | Flow this | 188006.077 | Abs Value of | Flow this | 231697.174 | Abs Value of | Flow this | 268993.226 | Abs Value of | Flow this | 315415.7125 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.4913 |  |  | 85.5428 |  |  | 62.1258 |  |  | -16.3896 |  |  | -209.8661 |  |  | -549.0409 |  |  | -1025.8156 |  |  | -1604.8088 |  |  | -2194.4263 |  |  | -3051.037
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43168 |  |  | 0.41264 |  |  | 0.29968 |  |  | -0.079059 |  |  | -1.0123 |  |  | -2.6484 |  |  | -4.9483 |  |  | -7.7412 |  |  | -10.5854 |  |  | -14.7174
[13 empty] | Delta P at this iteration flow rate |  |  | 29.4913 |  |  | 25.5428 |  |  | 2.1258 |  |  | -76.3896 |  |  | -269.8661 |  |  | -609.0409 |  |  | -1085.8156 |  |  | -1664.8088 |  |  | -2254.4263 |  |  | -3111.037
[13 empty] | Press drop ratio this iteration |  |  | 0.32954 |  |  | 0.2986 |  |  | 0.034218 |  |  | 4.6609 |  |  | 1.2859 |  |  | 1.1093 |  |  | 1.0585 |  |  | 1.0374 |  |  | 1.0273 |  |  | 1.0197
[13 empty] | Expansion factor | 12 |  | 0.82837 |  |  | 0.84452 |  |  | 0.98201 |  |  | -1.4845 |  |  | 0.29329 |  |  | 0.35377 |  |  | 0.33658 |  |  | 0.27303 |  |  | 0.42011 |  |  | 0.097697
[13 empty] | C Non choked w/ reducers | 5 |  | 25.8587 |  |  | 70.2589 |  |  | 603.1777 |  |  | -253.9109 |  |  | 324.5537 |  |  | 165.2552 |  |  | 130.2938 |  |  | 135.6094 |  |  | 85.5817 |  |  | 417.2699
[13 empty] | C Choked w/ reducers | 5 |  | 23.0443 |  |  | 60.7547 |  |  | 206.287 |  |  | 1542.8254 |  |  | 207.7942 |  |  | 122.0402 |  |  | 92.7552 |  |  | 81.9764 |  |  | 71.0974 |  |  | 100.5563
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 25.8587 |  |  | 70.2589 |  |  | 603.1777 |  |  | 1542.8254 |  |  | 207.7942 |  |  | 122.0402 |  |  | 92.7552 |  |  | 81.9764 |  |  | 71.0974 |  |  | 100.5563
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 21.1287 | 4837.364 |  | 58.6589 | 12184.118 |  | 580.1777 | 29834.4295 |  | 18000 | 58109.8536 |  | 18000 | 97490.2575 |  | 18000 | 142289.6861 |  | 18000 | 188006.077 |  | 18000 | 231697.174 |  | 18000 | 268993.226 |  | 18000 | 315415.7125
[13 empty] | Next iteration flow rate |  |  | 4934.1113 | Abs Value of | Flow this | 12305.9592 | Abs Value of | Flow this | 30132.7738 | Abs Value of | Flow this | 58690.9521 | Abs Value of | Flow this | 98465.1601 | Abs Value of | Flow this | 143712.583 | Abs Value of | Flow this | 189886.1377 | Abs Value of | Flow this | 234014.1457 | Abs Value of | Flow this | 271683.1583 | Abs Value of | Flow this | 318569.8696 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.4615 |  |  | 85.4486 |  |  | 61.5609 |  |  | -18.5327 |  |  | -215.8981 |  |  | -561.8903 |  |  | -1048.2481 |  |  | -1638.8791 |  |  | -2240.3479 |  |  | -3114.1764
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43154 |  |  | 0.41218 |  |  | 0.29695 |  |  | -0.089397 |  |  | -1.0414 |  |  | -2.7104 |  |  | -5.0565 |  |  | -7.9055 |  |  | -10.8069 |  |  | -15.022
[13 empty] | Delta P at this iteration flow rate |  |  | 29.4615 |  |  | 25.4486 |  |  | 1.5609 |  |  | -78.5327 |  |  | -275.8981 |  |  | -621.8903 |  |  | -1108.2481 |  |  | -1698.8791 |  |  | -2300.3479 |  |  | -3174.1764
[13 empty] | Press drop ratio this iteration |  |  | 0.32932 |  |  | 0.29782 |  |  | 0.025356 |  |  | 4.2375 |  |  | 1.2779 |  |  | 1.1068 |  |  | 1.0572 |  |  | 1.0366 |  |  | 1.0268 |  |  | 1.0193
[13 empty] | Expansion factor | 12 |  | 0.82849 |  |  | 0.84493 |  |  | 0.98667 |  |  | -1.2588 |  |  | 0.29768 |  |  | 0.35522 |  |  | 0.33736 |  |  | 0.27357 |  |  | 0.42043 |  |  | 0.09805
[13 empty] | C Non choked w/ reducers | 5 |  | 26.39 |  |  | 71.098 |  |  | 710.8329 |  |  | -280.4912 |  |  | 314.9214 |  |  | 162.6057 |  |  | 128.5571 |  |  | 133.9013 |  |  | 84.6251 |  |  | 411.4926
[13 empty] | C Choked w/ reducers | 5 |  | 23.513 |  |  | 61.4299 |  |  | 210.2617 |  |  | 1378.0622 |  |  | 204.0086 |  |  | 120.4419 |  |  | 91.6779 |  |  | 81.0749 |  |  | 70.3364 |  |  | 99.5027
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 26.39 |  |  | 71.098 |  |  | 710.8329 |  |  | 1378.0622 |  |  | 204.0086 |  |  | 120.4419 |  |  | 91.6779 |  |  | 81.0749 |  |  | 70.3364 |  |  | 99.5027
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 21.66 | 4934.1113 |  | 59.498 | 12305.9592 |  | 687.8329 | 30132.7738 |  | 18000 | 58690.9521 |  | 18000 | 98465.1601 |  | 18000 | 143712.583 |  | 18000 | 189886.1377 |  | 18000 | 234014.1457 |  | 18000 | 271683.1583 |  | 18000 | 318569.8696
[13 empty] | Next iteration flow rate |  |  | 5032.7935 | Abs Value of | Flow this | 12429.0188 | Abs Value of | Flow this | 30434.1015 | Abs Value of | Flow this | 59277.8616 | Abs Value of | Flow this | 99449.8117 | Abs Value of | Flow this | 145149.7088 | Abs Value of | Flow this | 191784.9991 | Abs Value of | Flow this | 236354.2872 | Abs Value of | Flow this | 274399.9899 | Abs Value of | Flow this | 321755.5683 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.4304 |  |  | 85.3525 |  |  | 60.9847 |  |  | -20.7188 |  |  | -222.0512 |  |  | -574.9979 |  |  | -1071.1315 |  |  | -1673.6342 |  |  | -2287.1925 |  |  | -3178.585
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43139 |  |  | 0.41172 |  |  | 0.29417 |  |  | -0.099942 |  |  | -1.0711 |  |  | -2.7736 |  |  | -5.1669 |  |  | -8.0732 |  |  | -11.0328 |  |  | -15.3327
[13 empty] | Delta P at this iteration flow rate |  |  | 29.4304 |  |  | 25.3525 |  |  | 0.98467 |  |  | -80.7188 |  |  | -282.0512 |  |  | -634.9979 |  |  | -1131.1315 |  |  | -1733.6342 |  |  | -2347.1925 |  |  | -3238.585
[13 empty] | Press drop ratio this iteration |  |  | 0.32909 |  |  | 0.29703 |  |  | 0.016146 |  |  | 3.8959 |  |  | 1.2702 |  |  | 1.1043 |  |  | 1.056 |  |  | 1.0359 |  |  | 1.0262 |  |  | 1.0189
[13 empty] | Expansion factor | 12 |  | 0.82861 |  |  | 0.84534 |  |  | 0.99151 |  |  | -1.0767 |  |  | 0.30191 |  |  | 0.35664 |  |  | 0.33813 |  |  | 0.2741 |  |  | 0.42074 |  |  | 0.098395
[13 empty] | C Non choked w/ reducers | 5 |  | 26.9327 |  |  | 71.9504 |  |  | 903.7552 |  |  | -308.9746 |  |  | 305.8442 |  |  | 160.0259 |  |  | 126.8541 |  |  | 132.2229 |  |  | 83.6816 |  |  | 405.8341
[13 empty] | C Choked w/ reducers | 5 |  | 23.9916 |  |  | 62.114 |  |  | 214.371 |  |  | 1244.9832 |  |  | 200.3389 |  |  | 118.8732 |  |  | 90.6166 |  |  | 80.1852 |  |  | 69.5848 |  |  | 98.4613
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 26.9327 |  |  | 71.9504 |  |  | 903.7552 |  |  | 1244.9832 |  |  | 200.3389 |  |  | 118.8732 |  |  | 90.6166 |  |  | 80.1852 |  |  | 69.5848 |  |  | 98.4613
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 22.2027 | 5032.7935 |  | 60.3504 | 12429.0188 |  | 880.7552 | 30434.1015 |  | 18000 | 59277.8616 |  | 18000 | 99449.8117 |  | 18000 | 145149.7088 |  | 18000 | 191784.9991 |  | 18000 | 236354.2872 |  | 18000 | 274399.9899 |  | 18000 | 321755.5683
[13 empty] | Next iteration flow rate |  |  | 5133.4493 | Abs Value of | Flow this | 12553.309 | Abs Value of | Flow this | 30738.4425 | Abs Value of | Flow this | 59870.6402 | Abs Value of | Flow this | 100444.3098 | Abs Value of | Flow this | 146601.2059 | Abs Value of | Flow this | 193702.8491 | Abs Value of | Flow this | 238717.8301 | Abs Value of | Flow this | 277143.9898 | Abs Value of | Flow this | 324973.124 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.3981 |  |  | 85.2545 |  |  | 60.3968 |  |  | -22.9489 |  |  | -228.3281 |  |  | -588.369 |  |  | -1094.4749 |  |  | -1709.0879 |  |  | -2334.9787 |  |  | -3244.2882
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43123 |  |  | 0.41125 |  |  | 0.29134 |  |  | -0.1107 |  |  | -1.1014 |  |  | -2.8381 |  |  | -5.2795 |  |  | -8.2442 |  |  | -11.2634 |  |  | -15.6496
[13 empty] | Delta P at this iteration flow rate |  |  | 29.3981 |  |  | 25.2545 |  |  | 0.39683 |  |  | -82.9489 |  |  | -288.3281 |  |  | -648.369 |  |  | -1154.4749 |  |  | -1769.0879 |  |  | -2394.9787 |  |  | -3304.2882
[13 empty] | Press drop ratio this iteration |  |  | 0.32884 |  |  | 0.29622 |  |  | 0.0065705 |  |  | 3.6145 |  |  | 1.2628 |  |  | 1.102 |  |  | 1.0548 |  |  | 1.0351 |  |  | 1.0257 |  |  | 1.0185
[13 empty] | Expansion factor | 12 |  | 0.82873 |  |  | 0.84576 |  |  | 0.99655 |  |  | -0.92674 |  |  | 0.30599 |  |  | 0.35802 |  |  | 0.33888 |  |  | 0.27463 |  |  | 0.42104 |  |  | 0.098734
[13 empty] | C Non choked w/ reducers | 5 |  | 27.4872 |  |  | 72.8164 |  |  | 1437.5294 |  |  | -339.848 |  |  | 297.2733 |  |  | 157.5128 |  |  | 125.1837 |  |  | 130.5736 |  |  | 82.7507 |  |  | 400.2905
[13 empty] | C Choked w/ reducers | 5 |  | 24.4802 |  |  | 62.8073 |  |  | 218.622 |  |  | 1135.241 |  |  | 196.7798 |  |  | 117.3335 |  |  | 89.5707 |  |  | 79.307 |  |  | 68.8424 |  |  | 97.432
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 27.4872 |  |  | 72.8164 |  |  | 1437.5294 |  |  | 1135.241 |  |  | 196.7798 |  |  | 117.3335 |  |  | 89.5707 |  |  | 79.307 |  |  | 68.8424 |  |  | 97.432
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 22.7572 | 5133.4493 |  | 61.2164 | 12553.309 |  | 1414.5294 | 30738.4425 |  | 18000 | 59870.6402 |  | 18000 | 100444.3098 |  | 18000 | 146601.2059 |  | 18000 | 193702.8491 |  | 18000 | 238717.8301 |  | 18000 | 277143.9898 |  | 18000 | 324973.124
[13 empty] | Next iteration flow rate |  |  | 5236.1183 | Abs Value of | Flow this | 12678.8421 | Abs Value of | Flow this | 31045.827 | Abs Value of | Flow this | 60469.3466 | Abs Value of | Flow this | 101448.7529 | Abs Value of | Flow this | 148067.218 | Abs Value of | Flow this | 195639.8776 | Abs Value of | Flow this | 241105.0084 | Abs Value of | Flow this | 279915.4297 | Abs Value of | Flow this | 328222.8552 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.3645 |  |  | 85.1545 |  |  | 59.7972 |  |  | -25.2238 |  |  | -234.7311 |  |  | -602.0088 |  |  | -1118.2874 |  |  | -1745.2542 |  |  | -2383.7254 |  |  | -3311.312
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43107 |  |  | 0.41076 |  |  | 0.28845 |  |  | -0.12167 |  |  | -1.1323 |  |  | -2.9039 |  |  | -5.3943 |  |  | -8.4187 |  |  | -11.4985 |  |  | -15.9729
[13 empty] | Delta P at this iteration flow rate |  |  | 29.3645 |  |  | 25.1545 |  |  | -0.20282 |  |  | -85.2238 |  |  | -294.7311 |  |  | -662.0088 |  |  | -1178.2874 |  |  | -1805.2542 |  |  | -2443.7254 |  |  | -3371.312
[13 empty] | Press drop ratio this iteration |  |  | 0.32859 |  |  | 0.2954 |  |  | -0.0033917 |  |  | 3.3787 |  |  | 1.2556 |  |  | 1.0997 |  |  | 1.0537 |  |  | 1.0344 |  |  | 1.0252 |  |  | 1.0181
[13 empty] | Expansion factor | 12 |  | 0.82887 |  |  | 0.84619 |  |  | 1.0018 |  |  | -0.80104 |  |  | 0.30993 |  |  | 0.35937 |  |  | 0.33961 |  |  | 0.27514 |  |  | 0.42134 |  |  | 0.099065
[13 empty] | C Non choked w/ reducers | 5 |  | 28.0538 |  |  | 73.6964 |  |  | #NUM! |  |  | -373.6864 |  |  | 289.1654 |  |  | 155.0638 |  |  | 123.5451 |  |  | 128.9524 |  |  | 81.8324 |  |  | 394.8582
[13 empty] | C Choked w/ reducers | 5 |  | 24.9792 |  |  | 63.5099 |  |  | 223.0225 |  |  | 1043.1836 |  |  | 193.3262 |  |  | 115.8218 |  |  | 88.54 |  |  | 78.4402 |  |  | 68.1089 |  |  | 96.4145
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 28.0538 |  |  | 73.6964 |  |  | #NUM! |  |  | 1043.1836 |  |  | 193.3262 |  |  | 115.8218 |  |  | 88.54 |  |  | 78.4402 |  |  | 68.1089 |  |  | 96.4145
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 23.3238 | 5236.1183 |  | 62.0964 | 12678.8421 |  | 18000 | 31045.827 |  | 18000 | 60469.3466 |  | 18000 | 101448.7529 |  | 18000 | 148067.218 |  | 18000 | 195639.8776 |  | 18000 | 241105.0084 |  | 18000 | 279915.4297 |  | 18000 | 328222.8552
[13 empty] | Next iteration flow rate |  |  | 5340.8407 | Abs Value of | Flow this | 12805.6305 | Abs Value of | Flow this | 31356.2852 | Abs Value of | Flow this | 61074.0401 | Abs Value of | Flow this | 102463.2405 | Abs Value of | Flow this | 149547.8901 | Abs Value of | Flow this | 197596.2764 | Abs Value of | Flow this | 243516.0584 | Abs Value of | Flow this | 282714.584 | Abs Value of | Flow this | 331505.0838 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.3295 |  |  | 85.0524 |  |  | 59.1855 |  |  | -27.5444 |  |  | -241.2628 |  |  | -615.9228 |  |  | -1142.5787 |  |  | -1782.1474 |  |  | -2433.4519 |  |  | -3379.683
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4309 |  |  | 0.41027 |  |  | 0.2855 |  |  | -0.13287 |  |  | -1.1638 |  |  | -2.9711 |  |  | -5.5115 |  |  | -8.5966 |  |  | -11.7384 |  |  | -16.3027
[13 empty] | Delta P at this iteration flow rate |  |  | 29.3295 |  |  | 25.0524 |  |  | -0.81452 |  |  | -87.5444 |  |  | -301.2628 |  |  | -675.9228 |  |  | -1202.5787 |  |  | -1842.1474 |  |  | -2493.4519 |  |  | -3439.683
[13 empty] | Press drop ratio this iteration |  |  | 0.32833 |  |  | 0.29455 |  |  | -0.013762 |  |  | 3.1783 |  |  | 1.2487 |  |  | 1.0974 |  |  | 1.0525 |  |  | 1.0337 |  |  | 1.0247 |  |  | 1.0178
[13 empty] | Expansion factor | 12 |  | 0.829 |  |  | 0.84663 |  |  | 1.0072 |  |  | -0.69422 |  |  | 0.31373 |  |  | 0.36068 |  |  | 0.34032 |  |  | 0.27563 |  |  | 0.42163 |  |  | 0.099389
[13 empty] | C Non choked w/ reducers | 5 |  | 28.6328 |  |  | 74.5907 |  |  | #NUM! |  |  | -411.1926 |  |  | 281.4823 |  |  | 152.6761 |  |  | 121.9372 |  |  | 127.3588 |  |  | 80.9264 |  |  | 389.5338
[13 empty] | C Choked w/ reducers | 5 |  | 25.4888 |  |  | 64.2219 |  |  | 227.5808 |  |  | 964.848 |  |  | 189.9732 |  |  | 114.3374 |  |  | 87.5242 |  |  | 77.5846 |  |  | 67.3843 |  |  | 95.4086
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 28.6328 |  |  | 74.5907 |  |  | #NUM! |  |  | 964.848 |  |  | 189.9732 |  |  | 114.3374 |  |  | 87.5242 |  |  | 77.5846 |  |  | 67.3843 |  |  | 95.4086
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 23.9028 | 5340.8407 |  | 62.9907 | 12805.6305 |  | 18000 | 31356.2852 |  | 18000 | 61074.0401 |  | 18000 | 102463.2405 |  | 18000 | 149547.8901 |  | 18000 | 197596.2764 |  | 18000 | 243516.0584 |  | 18000 | 282714.584 |  | 18000 | 331505.0838
[13 empty] | Next iteration flow rate |  |  | 5447.6575 | Abs Value of | Flow this | 12933.6868 | Abs Value of | Flow this | 31669.8481 | Abs Value of | Flow this | 61684.7805 | Abs Value of | Flow this | 103487.8729 | Abs Value of | Flow this | 151043.369 | Abs Value of | Flow this | 199572.2391 | Abs Value of | Flow this | 245951.219 | Abs Value of | Flow this | 285541.7298 | Abs Value of | Flow this | 334820.1346 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.2931 |  |  | 84.9484 |  |  | 58.5615 |  |  | -29.9117 |  |  | -247.9259 |  |  | -630.1165 |  |  | -1167.3581 |  |  | -1819.7822 |  |  | -2484.1779 |  |  | -3449.4283
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43073 |  |  | 0.40977 |  |  | 0.28249 |  |  | -0.14429 |  |  | -1.1959 |  |  | -3.0395 |  |  | -5.631 |  |  | -8.7782 |  |  | -11.9831 |  |  | -16.6392
[13 empty] | Delta P at this iteration flow rate |  |  | 29.2931 |  |  | 24.9484 |  |  | -1.4385 |  |  | -89.9117 |  |  | -307.9259 |  |  | -690.1165 |  |  | -1227.3581 |  |  | -1879.7822 |  |  | -2544.1779 |  |  | -3509.4283
[13 empty] | Press drop ratio this iteration |  |  | 0.32806 |  |  | 0.29369 |  |  | -0.024564 |  |  | 3.0059 |  |  | 1.242 |  |  | 1.0952 |  |  | 1.0514 |  |  | 1.033 |  |  | 1.0242 |  |  | 1.0174
[13 empty] | Expansion factor | 12 |  | 0.82915 |  |  | 0.84708 |  |  | 1.0129 |  |  | -0.60232 |  |  | 0.31741 |  |  | 0.36196 |  |  | 0.34102 |  |  | 0.27612 |  |  | 0.42191 |  |  | 0.099707
[13 empty] | C Non choked w/ reducers | 5 |  | 29.2245 |  |  | 75.4997 |  |  | #NUM! |  |  | -453.2489 |  |  | 274.1898 |  |  | 150.3474 |  |  | 120.3591 |  |  | 125.7919 |  |  | 80.0324 |  |  | 384.314
[13 empty] | C Choked w/ reducers | 5 |  | 26.0092 |  |  | 64.9436 |  |  | 232.3059 |  |  | 897.3729 |  |  | 186.7163 |  |  | 112.8795 |  |  | 86.523 |  |  | 76.7398 |  |  | 66.6684 |  |  | 94.4143
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 29.2245 |  |  | 75.4997 |  |  | #NUM! |  |  | 897.3729 |  |  | 186.7163 |  |  | 112.8795 |  |  | 86.523 |  |  | 76.7398 |  |  | 66.6684 |  |  | 94.4143
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 24.4945 | 5447.6575 |  | 63.8997 | 12933.6868 |  | 18000 | 31669.8481 |  | 18000 | 61684.7805 |  | 18000 | 103487.8729 |  | 18000 | 151043.369 |  | 18000 | 199572.2391 |  | 18000 | 245951.219 |  | 18000 | 285541.7298 |  | 18000 | 334820.1346
[13 empty] | Next iteration flow rate |  |  | 5556.6107 | Abs Value of | Flow this | 13063.0237 | Abs Value of | Flow this | 31986.5466 | Abs Value of | Flow this | 62301.6283 | Abs Value of | Flow this | 104522.7516 | Abs Value of | Flow this | 152553.8027 | Abs Value of | Flow this | 201567.9615 | Abs Value of | Flow this | 248410.7312 | Abs Value of | Flow this | 288397.1471 | Abs Value of | Flow this | 338168.336 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.2553 |  |  | 84.8422 |  |  | 57.9249 |  |  | -32.3265 |  |  | -254.7228 |  |  | -644.5955 |  |  | -1192.6356 |  |  | -1858.1735 |  |  | -2535.9235 |  |  | -3520.5754
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43055 |  |  | 0.40926 |  |  | 0.27942 |  |  | -0.15594 |  |  | -1.2287 |  |  | -3.1094 |  |  | -5.753 |  |  | -8.9634 |  |  | -12.2327 |  |  | -16.9824
[13 empty] | Delta P at this iteration flow rate |  |  | 29.2553 |  |  | 24.8422 |  |  | -2.0751 |  |  | -92.3265 |  |  | -314.7228 |  |  | -704.5955 |  |  | -1252.6356 |  |  | -1918.1735 |  |  | -2595.9235 |  |  | -3580.5754
[13 empty] | Press drop ratio this iteration |  |  | 0.32777 |  |  | 0.2928 |  |  | -0.035823 |  |  | 2.8561 |  |  | 1.2356 |  |  | 1.0931 |  |  | 1.0503 |  |  | 1.0323 |  |  | 1.0237 |  |  | 1.017
[13 empty] | Expansion factor | 12 |  | 0.82929 |  |  | 0.84754 |  |  | 1.0188 |  |  | -0.52244 |  |  | 0.32095 |  |  | 0.36321 |  |  | 0.3417 |  |  | 0.2766 |  |  | 0.42219 |  |  | 0.10002
[13 empty] | C Non choked w/ reducers | 5 |  | 29.8293 |  |  | 76.4237 |  |  | #NUM! |  |  | -500.9926 |  |  | 267.2573 |  |  | 148.0754 |  |  | 118.81 |  |  | 124.2511 |  |  | 79.1502 |  |  | 379.1956
[13 empty] | C Choked w/ reducers | 5 |  | 26.5406 |  |  | 65.6751 |  |  | 237.2073 |  |  | 838.6408 |  |  | 183.5514 |  |  | 111.4474 |  |  | 85.5361 |  |  | 75.9059 |  |  | 65.9611 |  |  | 93.4314
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 29.8293 |  |  | 76.4237 |  |  | #NUM! |  |  | 838.6408 |  |  | 183.5514 |  |  | 111.4474 |  |  | 85.5361 |  |  | 75.9059 |  |  | 65.9611 |  |  | 93.4314
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 25.0993 | 5556.6107 |  | 64.8237 | 13063.0237 |  | 18000 | 31986.5466 |  | 18000 | 62301.6283 |  | 18000 | 104522.7516 |  | 18000 | 152553.8027 |  | 18000 | 201567.9615 |  | 18000 | 248410.7312 |  | 18000 | 288397.1471 |  | 18000 | 338168.336
[13 empty] | Next iteration flow rate |  |  | 5667.7429 | Abs Value of | Flow this | 13193.6539 | Abs Value of | Flow this | 32306.412 | Abs Value of | Flow this | 62924.6446 | Abs Value of | Flow this | 105567.9791 | Abs Value of | Flow this | 154079.3408 | Abs Value of | Flow this | 203583.6411 | Abs Value of | Flow this | 250894.8385 | Abs Value of | Flow this | 291281.1186 | Abs Value of | Flow this | 341550.0193 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.2159 |  |  | 84.7339 |  |  | 57.2756 |  |  | -34.7899 |  |  | -261.6563 |  |  | -659.3655 |  |  | -1218.4212 |  |  | -1897.3364 |  |  | -2588.7092 |  |  | -3593.1526
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43036 |  |  | 0.40874 |  |  | 0.27628 |  |  | -0.16782 |  |  | -1.2622 |  |  | -3.1806 |  |  | -5.8774 |  |  | -9.1523 |  |  | -12.4873 |  |  | -17.3325
[13 empty] | Delta P at this iteration flow rate |  |  | 29.2159 |  |  | 24.7339 |  |  | -2.7244 |  |  | -94.7899 |  |  | -321.6563 |  |  | -719.3655 |  |  | -1278.4212 |  |  | -1957.3364 |  |  | -2648.7092 |  |  | -3653.1526
[13 empty] | Press drop ratio this iteration |  |  | 0.32747 |  |  | 0.2919 |  |  | -0.047566 |  |  | 2.7246 |  |  | 1.2293 |  |  | 1.091 |  |  | 1.0492 |  |  | 1.0316 |  |  | 1.0232 |  |  | 1.0167
[13 empty] | Expansion factor | 12 |  | 0.82945 |  |  | 0.84801 |  |  | 1.025 |  |  | -0.45239 |  |  | 0.32439 |  |  | 0.36442 |  |  | 0.34237 |  |  | 0.27707 |  |  | 0.42246 |  |  | 0.10032
[13 empty] | C Non choked w/ reducers | 5 |  | 30.4474 |  |  | 77.3632 |  |  | #NUM! |  |  | -555.9254 |  |  | 260.6574 |  |  | 145.8579 |  |  | 117.2891 |  |  | 122.7358 |  |  | 78.2796 |  |  | 374.1756
[13 empty] | C Choked w/ reducers | 5 |  | 27.0834 |  |  | 66.4167 |  |  | 242.2955 |  |  | 787.0512 |  |  | 180.4744 |  |  | 110.0405 |  |  | 84.5631 |  |  | 75.0825 |  |  | 65.2623 |  |  | 92.4596
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 30.4474 |  |  | 77.3632 |  |  | #NUM! |  |  | 787.0512 |  |  | 180.4744 |  |  | 110.0405 |  |  | 84.5631 |  |  | 75.0825 |  |  | 65.2623 |  |  | 92.4596
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 25.7174 | 5667.7429 |  | 65.7632 | 13193.6539 |  | 18000 | 32306.412 |  | 18000 | 62924.6446 |  | 18000 | 105567.9791 |  | 18000 | 154079.3408 |  | 18000 | 203583.6411 |  | 18000 | 250894.8385 |  | 18000 | 291281.1186 |  | 18000 | 341550.0193
[13 empty] | Next iteration flow rate |  |  | 5781.0977 | Abs Value of | Flow this | 13325.5904 | Abs Value of | Flow this | 32629.4762 | Abs Value of | Flow this | 63553.891 | Abs Value of | Flow this | 106623.6589 | Abs Value of | Flow this | 155620.1342 | Abs Value of | Flow this | 205619.4776 | Abs Value of | Flow this | 253403.7869 | Abs Value of | Flow this | 294193.9298 | Abs Value of | Flow this | 344965.5195 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.1749 |  |  | 84.6234 |  |  | 56.6132 |  |  | -37.3028 |  |  | -268.7293 |  |  | -674.4323 |  |  | -1244.7251 |  |  | -1937.2865 |  |  | -2642.5559 |  |  | -3667.1886
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.43016 |  |  | 0.4082 |  |  | 0.27309 |  |  | -0.17994 |  |  | -1.2963 |  |  | -3.2533 |  |  | -6.0042 |  |  | -9.345 |  |  | -12.747 |  |  | -17.6896
[13 empty] | Delta P at this iteration flow rate |  |  | 29.1749 |  |  | 24.6234 |  |  | -3.3868 |  |  | -97.3028 |  |  | -328.7293 |  |  | -734.4323 |  |  | -1304.7251 |  |  | -1997.2865 |  |  | -2702.5559 |  |  | -3727.1886
[13 empty] | Press drop ratio this iteration |  |  | 0.32717 |  |  | 0.29098 |  |  | -0.059823 |  |  | 2.6085 |  |  | 1.2233 |  |  | 1.089 |  |  | 1.0482 |  |  | 1.031 |  |  | 1.0227 |  |  | 1.0164
[13 empty] | Expansion factor | 12 |  | 0.82961 |  |  | 0.84849 |  |  | 1.0314 |  |  | -0.39046 |  |  | 0.3277 |  |  | 0.3656 |  |  | 0.34302 |  |  | 0.27752 |  |  | 0.42273 |  |  | 0.10062
[13 empty] | C Non choked w/ reducers | 5 |  | 31.0793 |  |  | 78.3186 |  |  | #NUM! |  |  | -620.0829 |  |  | 254.3655 |  |  | 143.6928 |  |  | 115.7956 |  |  | 121.2452 |  |  | 77.4204 |  |  | 369.2511
[13 empty] | C Choked w/ reducers | 5 |  | 27.6377 |  |  | 67.1684 |  |  | 247.5817 |  |  | 741.3718 |  |  | 177.4816 |  |  | 108.658 |  |  | 83.6039 |  |  | 74.2695 |  |  | 64.5718 |  |  | 91.4989
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 31.0793 |  |  | 78.3186 |  |  | #NUM! |  |  | 741.3718 |  |  | 177.4816 |  |  | 108.658 |  |  | 83.6039 |  |  | 74.2695 |  |  | 64.5718 |  |  | 91.4989
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 26.3493 | 5781.0977 |  | 66.7186 | 13325.5904 |  | 18000 | 32629.4762 |  | 18000 | 63553.891 |  | 18000 | 106623.6589 |  | 18000 | 155620.1342 |  | 18000 | 205619.4776 |  | 18000 | 253403.7869 |  | 18000 | 294193.9298 |  | 18000 | 344965.5195
[13 empty] | Next iteration flow rate |  |  | 5896.7197 | Abs Value of | Flow this | 13458.8463 | Abs Value of | Flow this | 32955.7709 | Abs Value of | Flow this | 64189.4299 | Abs Value of | Flow this | 107689.8955 | Abs Value of | Flow this | 157176.3355 | Abs Value of | Flow this | 207675.6723 | Abs Value of | Flow this | 255937.8248 | Abs Value of | Flow this | 297135.8691 | Abs Value of | Flow this | 348415.1747 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.1323 |  |  | 84.5107 |  |  | 55.9375 |  |  | -39.8662 |  |  | -275.9444 |  |  | -689.802 |  |  | -1271.5577 |  |  | -1978.0395 |  |  | -2697.4849 |  |  | -3742.7127
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42995 |  |  | 0.40766 |  |  | 0.26983 |  |  | -0.1923 |  |  | -1.3311 |  |  | -3.3274 |  |  | -6.1337 |  |  | -9.5416 |  |  | -13.012 |  |  | -18.0539
[13 empty] | Delta P at this iteration flow rate |  |  | 29.1323 |  |  | 24.5107 |  |  | -4.0625 |  |  | -99.8662 |  |  | -335.9444 |  |  | -749.802 |  |  | -1331.5577 |  |  | -2038.0395 |  |  | -2757.4849 |  |  | -3802.7127
[13 empty] | Press drop ratio this iteration |  |  | 0.32684 |  |  | 0.29003 |  |  | -0.072625 |  |  | 2.505 |  |  | 1.2174 |  |  | 1.087 |  |  | 1.0472 |  |  | 1.0303 |  |  | 1.0222 |  |  | 1.016
[13 empty] | Expansion factor | 12 |  | 0.82978 |  |  | 0.84898 |  |  | 1.0382 |  |  | -0.33533 |  |  | 0.33091 |  |  | 0.36676 |  |  | 0.34366 |  |  | 0.27797 |  |  | 0.42299 |  |  | 0.10091
[13 empty] | C Non choked w/ reducers | 5 |  | 31.7252 |  |  | 79.2902 |  |  | #NUM! |  |  | -696.3041 |  |  | 248.3593 |  |  | 141.5782 |  |  | 114.3287 |  |  | 119.7788 |  |  | 76.5723 |  |  | 364.4193
[13 empty] | C Choked w/ reducers | 5 |  | 28.204 |  |  | 67.9306 |  |  | 253.0781 |  |  | 700.6384 |  |  | 174.5694 |  |  | 107.2993 |  |  | 82.6581 |  |  | 73.4667 |  |  | 63.8895 |  |  | 90.5491
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 31.7252 |  |  | 79.2902 |  |  | #NUM! |  |  | 700.6384 |  |  | 174.5694 |  |  | 107.2993 |  |  | 82.6581 |  |  | 73.4667 |  |  | 63.8895 |  |  | 90.5491
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 26.9952 | 5896.7197 |  | 67.6902 | 13458.8463 |  | 18000 | 32955.7709 |  | 18000 | 64189.4299 |  | 18000 | 107689.8955 |  | 18000 | 157176.3355 |  | 18000 | 207675.6723 |  | 18000 | 255937.8248 |  | 18000 | 297135.8691 |  | 18000 | 348415.1747
[13 empty] | Next iteration flow rate |  |  | 6014.6541 | Abs Value of | Flow this | 13593.4348 | Abs Value of | Flow this | 33285.3286 | Abs Value of | Flow this | 64831.3242 | Abs Value of | Flow this | 108766.7944 | Abs Value of | Flow this | 158748.0989 | Abs Value of | Flow this | 209752.4291 | Abs Value of | Flow this | 258497.203 | Abs Value of | Flow this | 300107.2278 | Abs Value of | Flow this | 351899.3265 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.0879 |  |  | 84.3958 |  |  | 55.2482 |  |  | -42.4812 |  |  | -283.3045 |  |  | -705.4807 |  |  | -1298.9297 |  |  | -2019.6118 |  |  | -2753.518 |  |  | -3819.7549
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42974 |  |  | 0.4071 |  |  | 0.2665 |  |  | -0.20492 |  |  | -1.3666 |  |  | -3.4031 |  |  | -6.2657 |  |  | -9.7421 |  |  | -13.2823 |  |  | -18.4255
[13 empty] | Delta P at this iteration flow rate |  |  | 29.0879 |  |  | 24.3958 |  |  | -4.7518 |  |  | -102.4812 |  |  | -343.3045 |  |  | -765.4807 |  |  | -1358.9297 |  |  | -2079.6118 |  |  | -2813.518 |  |  | -3879.7549
[13 empty] | Press drop ratio this iteration |  |  | 0.32651 |  |  | 0.28906 |  |  | -0.086008 |  |  | 2.4124 |  |  | 1.2118 |  |  | 1.085 |  |  | 1.0462 |  |  | 1.0297 |  |  | 1.0218 |  |  | 1.0157
[13 empty] | Expansion factor | 12 |  | 0.82995 |  |  | 0.84949 |  |  | 1.0452 |  |  | -0.28594 |  |  | 0.33402 |  |  | 0.36789 |  |  | 0.34429 |  |  | 0.27841 |  |  | 0.42325 |  |  | 0.1012
[13 empty] | C Non choked w/ reducers | 5 |  | 32.3857 |  |  | 80.2786 |  |  | #NUM! |  |  | -788.6805 |  |  | 242.6187 |  |  | 139.5122 |  |  | 112.8876 |  |  | 118.3361 |  |  | 75.7353 |  |  | 359.6774
[13 empty] | C Choked w/ reducers | 5 |  | 28.7824 |  |  | 68.7033 |  |  | 258.7979 |  |  | 664.0855 |  |  | 171.7345 |  |  | 105.9638 |  |  | 81.7254 |  |  | 72.674 |  |  | 63.2152 |  |  | 89.61
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 32.3857 |  |  | 80.2786 |  |  | #NUM! |  |  | 664.0855 |  |  | 171.7345 |  |  | 105.9638 |  |  | 81.7254 |  |  | 72.674 |  |  | 63.2152 |  |  | 89.61
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 27.6557 | 6014.6541 |  | 68.6786 | 13593.4348 |  | 18000 | 33285.3286 |  | 18000 | 64831.3242 |  | 18000 | 108766.7944 |  | 18000 | 158748.0989 |  | 18000 | 209752.4291 |  | 18000 | 258497.203 |  | 18000 | 300107.2278 |  | 18000 | 351899.3265
[13 empty] | Next iteration flow rate |  |  | 6134.9472 | Abs Value of | Flow this | 13729.3692 | Abs Value of | Flow this | 33618.1819 | Abs Value of | Flow this | 65479.6375 | Abs Value of | Flow this | 109854.4624 | Abs Value of | Flow this | 160335.5799 | Abs Value of | Flow this | 211849.9533 | Abs Value of | Flow this | 261082.1751 | Abs Value of | Flow this | 303108.3 | Abs Value of | Flow this | 355418.3197 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 89.0418 |  |  | 84.2785 |  |  | 54.5451 |  |  | -45.1487 |  |  | -290.8125 |  |  | -721.4745 |  |  | -1326.8518 |  |  | -2062.0196 |  |  | -2810.6773 |  |  | -3898.3456
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42952 |  |  | 0.40654 |  |  | 0.26311 |  |  | -0.21779 |  |  | -1.4028 |  |  | -3.4802 |  |  | -6.4004 |  |  | -9.9467 |  |  | -13.558 |  |  | -18.8046
[13 empty] | Delta P at this iteration flow rate |  |  | 29.0418 |  |  | 24.2785 |  |  | -5.4549 |  |  | -105.1487 |  |  | -350.8125 |  |  | -781.4745 |  |  | -1386.8518 |  |  | -2122.0196 |  |  | -2870.6773 |  |  | -3958.3456
[13 empty] | Press drop ratio this iteration |  |  | 0.32616 |  |  | 0.28807 |  |  | -0.10001 |  |  | 2.3289 |  |  | 1.2063 |  |  | 1.0832 |  |  | 1.0452 |  |  | 1.0291 |  |  | 1.0213 |  |  | 1.0154
[13 empty] | Expansion factor | 12 |  | 0.83013 |  |  | 0.85 |  |  | 1.0526 |  |  | -0.24146 |  |  | 0.33702 |  |  | 0.36898 |  |  | 0.34489 |  |  | 0.27884 |  |  | 0.4235 |  |  | 0.10148
[13 empty] | C Non choked w/ reducers | 5 |  | 33.0609 |  |  | 81.2843 |  |  | #NUM! |  |  | -903.3413 |  |  | 237.1255 |  |  | 137.493 |  |  | 111.4718 |  |  | 116.9163 |  |  | 74.909 |  |  | 355.023
[13 empty] | C Choked w/ reducers | 5 |  | 29.3732 |  |  | 69.4869 |  |  | 264.7553 |  |  | 631.0981 |  |  | 168.9738 |  |  | 104.6509 |  |  | 80.8056 |  |  | 71.8912 |  |  | 62.5489 |  |  | 88.6815
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 33.0609 |  |  | 81.2843 |  |  | #NUM! |  |  | 631.0981 |  |  | 168.9738 |  |  | 104.6509 |  |  | 80.8056 |  |  | 71.8912 |  |  | 62.5489 |  |  | 88.6815
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 28.3309 | 6134.9472 |  | 69.6843 | 13729.3692 |  | 18000 | 33618.1819 |  | 18000 | 65479.6375 |  | 18000 | 109854.4624 |  | 18000 | 160335.5799 |  | 18000 | 211849.9533 |  | 18000 | 261082.1751 |  | 18000 | 303108.3 |  | 18000 | 355418.3197
[13 empty] | Next iteration flow rate |  |  | 6257.6461 | Abs Value of | Flow this | 13866.6628 | Abs Value of | Flow this | 33954.3637 | Abs Value of | Flow this | 66134.4339 | Abs Value of | Flow this | 110953.007 | Abs Value of | Flow this | 161938.9357 | Abs Value of | Flow this | 213968.4529 | Abs Value of | Flow this | 263692.9968 | Abs Value of | Flow this | 306139.383 | Abs Value of | Flow this | 358972.5029 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.9938 |  |  | 84.1589 |  |  | 53.8278 |  |  | -47.8698 |  |  | -298.4715 |  |  | -737.7897 |  |  | -1355.3351 |  |  | -2105.2798 |  |  | -2868.9856 |  |  | -3978.5159
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42928 |  |  | 0.40596 |  |  | 0.25965 |  |  | -0.23091 |  |  | -1.4398 |  |  | -3.5589 |  |  | -6.5378 |  |  | -10.1553 |  |  | -13.8393 |  |  | -19.1914
[13 empty] | Delta P at this iteration flow rate |  |  | 28.9938 |  |  | 24.1589 |  |  | -6.1722 |  |  | -107.8698 |  |  | -358.4715 |  |  | -797.7897 |  |  | -1415.3351 |  |  | -2165.2798 |  |  | -2928.9856 |  |  | -4038.5159
[13 empty] | Press drop ratio this iteration |  |  | 0.3258 |  |  | 0.28706 |  |  | -0.11467 |  |  | 2.2534 |  |  | 1.201 |  |  | 1.0813 |  |  | 1.0443 |  |  | 1.0285 |  |  | 1.0209 |  |  | 1.0151
[13 empty] | Expansion factor | 12 |  | 0.83032 |  |  | 0.85053 |  |  | 1.0603 |  |  | -0.20119 |  |  | 0.33993 |  |  | 0.37006 |  |  | 0.34549 |  |  | 0.27926 |  |  | 0.42374 |  |  | 0.10175
[13 empty] | C Non choked w/ reducers | 5 |  | 33.7515 |  |  | 82.3076 |  |  | #NUM! |  |  | -1049.9118 |  |  | 231.8631 |  |  | 135.519 |  |  | 110.0805 |  |  | 115.519 |  |  | 74.0934 |  |  | 350.4536
[13 empty] | C Choked w/ reducers | 5 |  | 29.9769 |  |  | 70.2815 |  |  | 270.9661 |  |  | 601.1762 |  |  | 166.2842 |  |  | 103.3601 |  |  | 79.8985 |  |  | 71.1181 |  |  | 61.8905 |  |  | 87.7634
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 33.7515 |  |  | 82.3076 |  |  | #NUM! |  |  | 601.1762 |  |  | 166.2842 |  |  | 103.3601 |  |  | 79.8985 |  |  | 71.1181 |  |  | 61.8905 |  |  | 87.7634
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 29.0215 | 6257.6461 |  | 70.7076 | 13866.6628 |  | 18000 | 33954.3637 |  | 18000 | 66134.4339 |  | 18000 | 110953.007 |  | 18000 | 161938.9357 |  | 18000 | 213968.4529 |  | 18000 | 263692.9968 |  | 18000 | 306139.383 |  | 18000 | 358972.5029
[13 empty] | Next iteration flow rate |  |  | 6382.799 | Abs Value of | Flow this | 14005.3295 | Abs Value of | Flow this | 34293.9074 | Abs Value of | Flow this | 66795.7782 | Abs Value of | Flow this | 112062.5371 | Abs Value of | Flow this | 163558.325 | Abs Value of | Flow this | 216108.1374 | Abs Value of | Flow this | 266329.9268 | Abs Value of | Flow this | 309200.7769 | Abs Value of | Flow this | 362562.228 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.9438 |  |  | 84.0368 |  |  | 53.0961 |  |  | -50.6456 |  |  | -306.2844 |  |  | -754.4329 |  |  | -1384.391 |  |  | -2149.4096 |  |  | -2928.4658 |  |  | -4060.2977
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42904 |  |  | 0.40537 |  |  | 0.25612 |  |  | -0.2443 |  |  | -1.4774 |  |  | -3.6392 |  |  | -6.678 |  |  | -10.3682 |  |  | -14.1262 |  |  | -19.5859
[13 empty] | Delta P at this iteration flow rate |  |  | 28.9438 |  |  | 24.0368 |  |  | -6.9039 |  |  | -110.6456 |  |  | -366.2844 |  |  | -814.4329 |  |  | -1444.391 |  |  | -2209.4096 |  |  | -2988.4658 |  |  | -4120.2977
[13 empty] | Press drop ratio this iteration |  |  | 0.32542 |  |  | 0.28603 |  |  | -0.13003 |  |  | 2.1847 |  |  | 1.1959 |  |  | 1.0795 |  |  | 1.0433 |  |  | 1.0279 |  |  | 1.0205 |  |  | 1.0148
[13 empty] | Expansion factor | 12 |  | 0.83052 |  |  | 0.85107 |  |  | 1.0683 |  |  | -0.16457 |  |  | 0.34275 |  |  | 0.3711 |  |  | 0.34607 |  |  | 0.27967 |  |  | 0.42398 |  |  | 0.10202
[13 empty] | C Non choked w/ reducers | 5 |  | 34.4577 |  |  | 83.3491 |  |  | #NUM! |  |  | -1244.4308 |  |  | 226.8163 |  |  | 133.5886 |  |  | 108.713 |  |  | 114.1437 |  |  | 73.2881 |  |  | 345.9667
[13 empty] | C Choked w/ reducers | 5 |  | 30.5936 |  |  | 71.0874 |  |  | 277.4471 |  |  | 573.9088 |  |  | 163.6629 |  |  | 102.0907 |  |  | 79.0038 |  |  | 70.3545 |  |  | 61.2398 |  |  | 86.8557
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 34.4577 |  |  | 83.3491 |  |  | #NUM! |  |  | 573.9088 |  |  | 163.6629 |  |  | 102.0907 |  |  | 79.0038 |  |  | 70.3545 |  |  | 61.2398 |  |  | 86.8557
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 29.7277 | 6382.799 |  | 71.7491 | 14005.3295 |  | 18000 | 34293.9074 |  | 18000 | 66795.7782 |  | 18000 | 112062.5371 |  | 18000 | 163558.325 |  | 18000 | 216108.1374 |  | 18000 | 266329.9268 |  | 18000 | 309200.7769 |  | 18000 | 362562.228
[13 empty] | Next iteration flow rate |  |  | 6510.455 | Abs Value of | Flow this | 14145.3828 | Abs Value of | Flow this | 34636.8464 | Abs Value of | Flow this | 67463.736 | Abs Value of | Flow this | 113183.1624 | Abs Value of | Flow this | 165193.9083 | Abs Value of | Flow this | 218269.2188 | Abs Value of | Flow this | 268993.226 | Abs Value of | Flow this | 312292.7846 | Abs Value of | Flow this | 366187.8502 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.8919 |  |  | 83.9124 |  |  | 52.3497 |  |  | -53.4772 |  |  | -314.2543 |  |  | -771.4107 |  |  | -1414.0309 |  |  | -2194.4263 |  |  | -2989.1416 |  |  | -4143.7233
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42879 |  |  | 0.40477 |  |  | 0.25252 |  |  | -0.25796 |  |  | -1.5159 |  |  | -3.7211 |  |  | -6.8209 |  |  | -10.5854 |  |  | -14.4189 |  |  | -19.9883
[13 empty] | Delta P at this iteration flow rate |  |  | 28.8919 |  |  | 23.9124 |  |  | -7.6503 |  |  | -113.4772 |  |  | -374.2543 |  |  | -831.4107 |  |  | -1474.0309 |  |  | -2254.4263 |  |  | -3049.1416 |  |  | -4203.7233
[13 empty] | Press drop ratio this iteration |  |  | 0.32502 |  |  | 0.28497 |  |  | -0.14614 |  |  | 2.122 |  |  | 1.1909 |  |  | 1.0778 |  |  | 1.0424 |  |  | 1.0273 |  |  | 1.0201 |  |  | 1.0145
[13 empty] | Expansion factor | 12 |  | 0.83073 |  |  | 0.85162 |  |  | 1.0768 |  |  | -0.13113 |  |  | 0.34548 |  |  | 0.37212 |  |  | 0.34664 |  |  | 0.28007 |  |  | 0.42422 |  |  | 0.10229
[13 empty] | C Non choked w/ reducers | 5 |  | 35.18 |  |  | 84.4093 |  |  | #NUM! |  |  | -1515.7731 |  |  | 221.9715 |  |  | 131.7002 |  |  | 107.3687 |  |  | 112.7898 |  |  | 72.4931 |  |  | 341.5602
[13 empty] | C Choked w/ reducers | 5 |  | 31.2237 |  |  | 71.9048 |  |  | 284.217 |  |  | 548.9557 |  |  | 161.1073 |  |  | 100.8423 |  |  | 78.1213 |  |  | 69.6004 |  |  | 60.5967 |  |  | 85.9581
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 35.18 |  |  | 84.4093 |  |  | #NUM! |  |  | 548.9557 |  |  | 161.1073 |  |  | 100.8423 |  |  | 78.1213 |  |  | 69.6004 |  |  | 60.5967 |  |  | 85.9581
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 30.45 | 6510.455 |  | 72.8093 | 14145.3828 |  | 18000 | 34636.8464 |  | 18000 | 67463.736 |  | 18000 | 113183.1624 |  | 18000 | 165193.9083 |  | 18000 | 218269.2188 |  | 18000 | 268993.226 |  | 18000 | 312292.7846 |  | 18000 | 366187.8502
[13 empty] | Next iteration flow rate |  |  | 6640.6641 | Abs Value of | Flow this | 14286.8366 | Abs Value of | Flow this | 34983.2149 | Abs Value of | Flow this | 68138.3733 | Abs Value of | Flow this | 114314.9941 | Abs Value of | Flow this | 166845.8473 | Abs Value of | Flow this | 220451.911 | Abs Value of | Flow this | 271683.1583 | Abs Value of | Flow this | 315415.7125 | Abs Value of | Flow this | 369849.7287 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.8378 |  |  | 83.7854 |  |  | 51.5884 |  |  | -56.3657 |  |  | -322.3844 |  |  | -788.7297 |  |  | -1444.2665 |  |  | -2240.3479 |  |  | -3051.037 |  |  | -4228.8258
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42853 |  |  | 0.40416 |  |  | 0.24885 |  |  | -0.27189 |  |  | -1.5551 |  |  | -3.8046 |  |  | -6.9668 |  |  | -10.8069 |  |  | -14.7174 |  |  | -20.3988
[13 empty] | Delta P at this iteration flow rate |  |  | 28.8378 |  |  | 23.7854 |  |  | -8.4116 |  |  | -116.3657 |  |  | -382.3844 |  |  | -848.7297 |  |  | -1504.2665 |  |  | -2300.3479 |  |  | -3111.037 |  |  | -4288.8258
[13 empty] | Press drop ratio this iteration |  |  | 0.32461 |  |  | 0.28388 |  |  | -0.16305 |  |  | 2.0645 |  |  | 1.1861 |  |  | 1.0761 |  |  | 1.0415 |  |  | 1.0268 |  |  | 1.0197 |  |  | 1.0142
[13 empty] | Expansion factor | 12 |  | 0.83094 |  |  | 0.85218 |  |  | 1.0857 |  |  | -0.10048 |  |  | 0.34812 |  |  | 0.37312 |  |  | 0.3472 |  |  | 0.28046 |  |  | 0.42445 |  |  | 0.10254
[13 empty] | C Non choked w/ reducers | 5 |  | 35.9189 |  |  | 85.4887 |  |  | #NUM! |  |  | -1921.7171 |  |  | 217.316 |  |  | 129.8524 |  |  | 106.0471 |  |  | 111.4568 |  |  | 71.7082 |  |  | 337.2318
[13 empty] | C Choked w/ reducers | 5 |  | 31.8675 |  |  | 72.7339 |  |  | 291.2959 |  |  | 526.0322 |  |  | 158.6148 |  |  | 99.6142 |  |  | 77.2507 |  |  | 68.8555 |  |  | 59.961 |  |  | 85.0705
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 35.9189 |  |  | 85.4887 |  |  | #NUM! |  |  | 526.0322 |  |  | 158.6148 |  |  | 99.6142 |  |  | 77.2507 |  |  | 68.8555 |  |  | 59.961 |  |  | 85.0705
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 31.1889 | 6640.6641 |  | 73.8887 | 14286.8366 |  | 18000 | 34983.2149 |  | 18000 | 68138.3733 |  | 18000 | 114314.9941 |  | 18000 | 166845.8473 |  | 18000 | 220451.911 |  | 18000 | 271683.1583 |  | 18000 | 315415.7125 |  | 18000 | 369849.7287
[13 empty] | Next iteration flow rate |  |  | 6773.4774 | Abs Value of | Flow this | 14429.705 | Abs Value of | Flow this | 35333.0471 | Abs Value of | Flow this | 68819.7571 | Abs Value of | Flow this | 115458.144 | Abs Value of | Flow this | 168514.3058 | Abs Value of | Flow this | 222656.4301 | Abs Value of | Flow this | 274399.9899 | Abs Value of | Flow this | 318569.8696 | Abs Value of | Flow this | 373548.226 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.7815 |  |  | 83.6558 |  |  | 50.8117 |  |  | -59.3123 |  |  | -330.678 |  |  | -806.3967 |  |  | -1475.1099 |  |  | -2287.1925 |  |  | -3114.1764 |  |  | -4315.6388
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42826 |  |  | 0.40353 |  |  | 0.2451 |  |  | -0.28611 |  |  | -1.5951 |  |  | -3.8899 |  |  | -7.1156 |  |  | -11.0328 |  |  | -15.022 |  |  | -20.8176
[13 empty] | Delta P at this iteration flow rate |  |  | 28.7815 |  |  | 23.6558 |  |  | -9.1883 |  |  | -119.3123 |  |  | -390.678 |  |  | -866.3967 |  |  | -1535.1099 |  |  | -2347.1925 |  |  | -3174.1764 |  |  | -4375.6388
[13 empty] | Press drop ratio this iteration |  |  | 0.32418 |  |  | 0.28278 |  |  | -0.18083 |  |  | 2.0116 |  |  | 1.1814 |  |  | 1.0744 |  |  | 1.0407 |  |  | 1.0262 |  |  | 1.0193 |  |  | 1.0139
[13 empty] | Expansion factor | 12 |  | 0.83116 |  |  | 0.85276 |  |  | 1.0951 |  |  | -0.072295 |  |  | 0.35069 |  |  | 0.37409 |  |  | 0.34774 |  |  | 0.28084 |  |  | 0.42467 |  |  | 0.1028
[13 empty] | C Non choked w/ reducers | 5 |  | 36.6749 |  |  | 86.5881 |  |  | #NUM! |  |  | -2597.2049 |  |  | 212.8381 |  |  | 128.0438 |  |  | 104.7476 |  |  | 110.1442 |  |  | 70.9331 |  |  | 332.9794
[13 empty] | C Choked w/ reducers | 5 |  | 32.5255 |  |  | 73.575 |  |  | 298.7061 |  |  | 504.8984 |  |  | 156.1831 |  |  | 98.4061 |  |  | 76.3918 |  |  | 68.1197 |  |  | 59.3328 |  |  | 84.1928
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 36.6749 |  |  | 86.5881 |  |  | #NUM! |  |  | 504.8984 |  |  | 156.1831 |  |  | 98.4061 |  |  | 76.3918 |  |  | 68.1197 |  |  | 59.3328 |  |  | 84.1928
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 31.9449 | 6773.4774 |  | 74.9881 | 14429.705 |  | 18000 | 35333.0471 |  | 18000 | 68819.7571 |  | 18000 | 115458.144 |  | 18000 | 168514.3058 |  | 18000 | 222656.4301 |  | 18000 | 274399.9899 |  | 18000 | 318569.8696 |  | 18000 | 373548.226
[13 empty] | Next iteration flow rate |  |  | 6908.9469 | Abs Value of | Flow this | 14574.002 | Abs Value of | Flow this | 35686.3775 | Abs Value of | Flow this | 69507.9546 | Abs Value of | Flow this | 116612.7255 | Abs Value of | Flow this | 170199.4489 | Abs Value of | Flow this | 224882.9944 | Abs Value of | Flow this | 277143.9898 | Abs Value of | Flow this | 321755.5683 | Abs Value of | Flow this | 377283.7083 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.723 |  |  | 83.5237 |  |  | 50.0193 |  |  | -62.3181 |  |  | -339.1383 |  |  | -824.4189 |  |  | -1506.5732 |  |  | -2334.9787 |  |  | -3178.585 |  |  | -4404.1968
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42798 |  |  | 0.4029 |  |  | 0.24128 |  |  | -0.30061 |  |  | -1.6359 |  |  | -3.9768 |  |  | -7.2673 |  |  | -11.2634 |  |  | -15.3327 |  |  | -21.2447
[13 empty] | Delta P at this iteration flow rate |  |  | 28.723 |  |  | 23.5237 |  |  | -9.9807 |  |  | -122.3181 |  |  | -399.1383 |  |  | -884.4189 |  |  | -1566.5732 |  |  | -2394.9787 |  |  | -3238.585 |  |  | -4464.1968
[13 empty] | Press drop ratio this iteration |  |  | 0.32374 |  |  | 0.28164 |  |  | -0.19954 |  |  | 1.9628 |  |  | 1.1769 |  |  | 1.0728 |  |  | 1.0398 |  |  | 1.0257 |  |  | 1.0189 |  |  | 1.0136
[13 empty] | Expansion factor | 12 |  | 0.83139 |  |  | 0.85335 |  |  | 1.1049 |  |  | -0.046285 |  |  | 0.35318 |  |  | 0.37503 |  |  | 0.34828 |  |  | 0.28122 |  |  | 0.42489 |  |  | 0.10304
[13 empty] | C Non choked w/ reducers | 5 |  | 37.4483 |  |  | 87.7078 |  |  | #NUM! |  |  | -3947.7695 |  |  | 208.5273 |  |  | 126.2732 |  |  | 103.4695 |  |  | 108.8517 |  |  | 70.1678 |  |  | 328.801
[13 empty] | C Choked w/ reducers | 5 |  | 33.1979 |  |  | 74.4284 |  |  | 306.472 |  |  | 485.351 |  |  | 153.8097 |  |  | 97.2175 |  |  | 75.5444 |  |  | 67.3929 |  |  | 58.7118 |  |  | 83.3249
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 37.4483 |  |  | 87.7078 |  |  | #NUM! |  |  | 485.351 |  |  | 153.8097 |  |  | 97.2175 |  |  | 75.5444 |  |  | 67.3929 |  |  | 58.7118 |  |  | 83.3249
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 32.7183 | 6908.9469 |  | 76.1078 | 14574.002 |  | 18000 | 35686.3775 |  | 18000 | 69507.9546 |  | 18000 | 116612.7255 |  | 18000 | 170199.4489 |  | 18000 | 224882.9944 |  | 18000 | 277143.9898 |  | 18000 | 321755.5683 |  | 18000 | 377283.7083
[13 empty] | Next iteration flow rate |  |  | 7047.1259 | Abs Value of | Flow this | 14719.742 | Abs Value of | Flow this | 36043.2413 | Abs Value of | Flow this | 70203.0342 | Abs Value of | Flow this | 117778.8527 | Abs Value of | Flow this | 171901.4434 | Abs Value of | Flow this | 227131.8243 | Abs Value of | Flow this | 279915.4297 | Abs Value of | Flow this | 324973.124 | Abs Value of | Flow this | 381056.5454 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.6621 |  |  | 83.3889 |  |  | 49.2111 |  |  | -65.3843 |  |  | -347.7686 |  |  | -842.8034 |  |  | -1538.669 |  |  | -2383.7254 |  |  | -3244.2882 |  |  | -4494.5348
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42768 |  |  | 0.40225 |  |  | 0.23738 |  |  | -0.3154 |  |  | -1.6775 |  |  | -4.0655 |  |  | -7.4222 |  |  | -11.4985 |  |  | -15.6496 |  |  | -21.6805
[13 empty] | Delta P at this iteration flow rate |  |  | 28.6621 |  |  | 23.3889 |  |  | -10.7889 |  |  | -125.3843 |  |  | -407.7686 |  |  | -902.8034 |  |  | -1598.669 |  |  | -2443.7254 |  |  | -3304.2882 |  |  | -4554.5348
[13 empty] | Press drop ratio this iteration |  |  | 0.32327 |  |  | 0.28048 |  |  | -0.21924 |  |  | 1.9177 |  |  | 1.1725 |  |  | 1.0712 |  |  | 1.039 |  |  | 1.0252 |  |  | 1.0185 |  |  | 1.0133
[13 empty] | Expansion factor | 12 |  | 0.83164 |  |  | 0.85396 |  |  | 1.1152 |  |  | -0.022217 |  |  | 0.35559 |  |  | 0.37596 |  |  | 0.3488 |  |  | 0.28159 |  |  | 0.42511 |  |  | 0.10329
[13 empty] | C Non choked w/ reducers | 5 |  | 38.2399 |  |  | 88.8486 |  |  | #NUM! |  |  | -8009.7407 |  |  | 204.3738 |  |  | 124.5392 |  |  | 102.2124 |  |  | 107.5787 |  |  | 69.412 |  |  | 324.6947
[13 empty] | C Choked w/ reducers | 5 |  | 33.8851 |  |  | 75.2942 |  |  | 314.6205 |  |  | 467.2161 |  |  | 151.4927 |  |  | 96.0478 |  |  | 74.7082 |  |  | 66.6748 |  |  | 58.098 |  |  | 82.4666
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 38.2399 |  |  | 88.8486 |  |  | #NUM! |  |  | 467.2161 |  |  | 151.4927 |  |  | 96.0478 |  |  | 74.7082 |  |  | 66.6748 |  |  | 58.098 |  |  | 82.4666
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 33.5099 | 7047.1259 |  | 77.2486 | 14719.742 |  | 18000 | 36043.2413 |  | 18000 | 70203.0342 |  | 18000 | 117778.8527 |  | 18000 | 171901.4434 |  | 18000 | 227131.8243 |  | 18000 | 279915.4297 |  | 18000 | 324973.124 |  | 18000 | 381056.5454
[13 empty] | Next iteration flow rate |  |  | 7188.0684 | Abs Value of | Flow this | 14866.9395 | Abs Value of | Flow this | 36403.6737 | Abs Value of | Flow this | 70905.0645 | Abs Value of | Flow this | 118956.6412 | Abs Value of | Flow this | 173620.4578 | Abs Value of | Flow this | 229403.1426 | Abs Value of | Flow this | 282714.584 | Abs Value of | Flow this | 328222.8552 | Abs Value of | Flow this | 384867.1108 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.5988 |  |  | 83.2514 |  |  | 48.3866 |  |  | -68.5121 |  |  | -356.5723 |  |  | -861.5574 |  |  | -1571.4099 |  |  | -2433.4519 |  |  | -3311.312 |  |  | -4586.6885
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42738 |  |  | 0.40158 |  |  | 0.2334 |  |  | -0.33049 |  |  | -1.72 |  |  | -4.1559 |  |  | -7.5801 |  |  | -11.7384 |  |  | -15.9729 |  |  | -22.125
[13 empty] | Delta P at this iteration flow rate |  |  | 28.5988 |  |  | 23.2514 |  |  | -11.6134 |  |  | -128.5121 |  |  | -416.5723 |  |  | -921.5574 |  |  | -1631.4099 |  |  | -2493.4519 |  |  | -3371.312 |  |  | -4646.6885
[13 empty] | Press drop ratio this iteration |  |  | 0.32279 |  |  | 0.27929 |  |  | -0.24001 |  |  | 1.8758 |  |  | 1.1683 |  |  | 1.0696 |  |  | 1.0382 |  |  | 1.0247 |  |  | 1.0181 |  |  | 1.0131
[13 empty] | Expansion factor | 12 |  | 0.83189 |  |  | 0.85458 |  |  | 1.1262 |  |  | 0.00011473 |  |  | 0.35793 |  |  | 0.37686 |  |  | 0.34931 |  |  | 0.28195 |  |  | 0.42532 |  |  | 0.10352
[13 empty] | C Non choked w/ reducers | 5 |  | 39.0499 |  |  | 90.0112 |  |  | #NUM! |  |  | 1511693.415 |  |  | 200.3687 |  |  | 122.8407 |  |  | 100.9757 |  |  | 106.3248 |  |  | 68.6656 |  |  | 320.6584
[13 empty] | C Choked w/ reducers | 5 |  | 34.5875 |  |  | 76.1727 |  |  | 323.1813 |  |  | 450.3447 |  |  | 149.2298 |  |  | 94.8966 |  |  | 73.8832 |  |  | 65.9655 |  |  | 57.4913 |  |  | 81.6178
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 39.0499 |  |  | 90.0112 |  |  | #NUM! |  |  | 450.3447 |  |  | 149.2298 |  |  | 94.8966 |  |  | 73.8832 |  |  | 65.9655 |  |  | 57.4913 |  |  | 81.6178
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 34.3199 | 7188.0684 |  | 78.4112 | 14866.9395 |  | 18000 | 36403.6737 |  | 18000 | 70905.0645 |  | 18000 | 118956.6412 |  | 18000 | 173620.4578 |  | 18000 | 229403.1426 |  | 18000 | 282714.584 |  | 18000 | 328222.8552 |  | 18000 | 384867.1108
[13 empty] | Next iteration flow rate |  |  | 7331.8298 | Abs Value of | Flow this | 15015.6088 | Abs Value of | Flow this | 36767.7105 | Abs Value of | Flow this | 71614.1152 | Abs Value of | Flow this | 120146.2076 | Abs Value of | Flow this | 175356.6624 | Abs Value of | Flow this | 231697.174 | Abs Value of | Flow this | 285541.7298 | Abs Value of | Flow this | 331505.0838 | Abs Value of | Flow this | 388715.7819 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.5329 |  |  | 83.1111 |  |  | 47.5456 |  |  | -71.7029 |  |  | -365.5531 |  |  | -880.6883 |  |  | -1604.8088 |  |  | -2484.1779 |  |  | -3379.683 |  |  | -4680.6946
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42706 |  |  | 0.40091 |  |  | 0.22935 |  |  | -0.34588 |  |  | -1.7633 |  |  | -4.2482 |  |  | -7.7412 |  |  | -11.9831 |  |  | -16.3027 |  |  | -22.5785
[13 empty] | Delta P at this iteration flow rate |  |  | 28.5329 |  |  | 23.1111 |  |  | -12.4544 |  |  | -131.7029 |  |  | -425.5531 |  |  | -940.6883 |  |  | -1664.8088 |  |  | -2544.1779 |  |  | -3439.683 |  |  | -4740.6946
[13 empty] | Press drop ratio this iteration |  |  | 0.32229 |  |  | 0.27807 |  |  | -0.26195 |  |  | 1.8368 |  |  | 1.1641 |  |  | 1.0681 |  |  | 1.0374 |  |  | 1.0242 |  |  | 1.0178 |  |  | 1.0128
[13 empty] | Expansion factor | 12 |  | 0.83215 |  |  | 0.85521 |  |  | 1.1377 |  |  | 0.020888 |  |  | 0.3602 |  |  | 0.37774 |  |  | 0.3498 |  |  | 0.2823 |  |  | 0.42553 |  |  | 0.10376
[13 empty] | C Non choked w/ reducers | 5 |  | 39.8792 |  |  | 91.1961 |  |  | #NUM! |  |  | 8097.3914 |  |  | 196.5034 |  |  | 121.1765 |  |  | 99.759 |  |  | 105.0896 |  |  | 67.9284 |  |  | 316.6905
[13 empty] | C Choked w/ reducers | 5 |  | 35.3055 |  |  | 77.0643 |  |  | 332.1872 |  |  | 434.6078 |  |  | 147.0193 |  |  | 93.7636 |  |  | 73.069 |  |  | 65.2647 |  |  | 56.8915 |  |  | 80.7784
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 39.8792 |  |  | 91.1961 |  |  | #NUM! |  |  | 434.6078 |  |  | 147.0193 |  |  | 93.7636 |  |  | 73.069 |  |  | 65.2647 |  |  | 56.8915 |  |  | 80.7784
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 35.1492 | 7331.8298 |  | 79.5961 | 15015.6088 |  | 18000 | 36767.7105 |  | 18000 | 71614.1152 |  | 18000 | 120146.2076 |  | 18000 | 175356.6624 |  | 18000 | 231697.174 |  | 18000 | 285541.7298 |  | 18000 | 331505.0838 |  | 18000 | 388715.7819
[13 empty] | Next iteration flow rate |  |  | 7478.4664 | Abs Value of | Flow this | 15165.7649 | Abs Value of | Flow this | 37135.3876 | Abs Value of | Flow this | 72330.2563 | Abs Value of | Flow this | 121347.6697 | Abs Value of | Flow this | 177110.229 | Abs Value of | Flow this | 234014.1457 | Abs Value of | Flow this | 288397.1471 | Abs Value of | Flow this | 334820.1346 | Abs Value of | Flow this | 392602.9398 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.4643 |  |  | 82.968 |  |  | 46.6876 |  |  | -74.9577 |  |  | -374.7143 |  |  | -900.2038 |  |  | -1638.8791 |  |  | -2535.9235 |  |  | -3449.4283 |  |  | -4776.5902
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42673 |  |  | 0.40022 |  |  | 0.22521 |  |  | -0.36158 |  |  | -1.8075 |  |  | -4.3424 |  |  | -7.9055 |  |  | -12.2327 |  |  | -16.6392 |  |  | -23.0411
[13 empty] | Delta P at this iteration flow rate |  |  | 28.4643 |  |  | 22.968 |  |  | -13.3124 |  |  | -134.9577 |  |  | -434.7143 |  |  | -960.2038 |  |  | -1698.8791 |  |  | -2595.9235 |  |  | -3509.4283 |  |  | -4836.5902
[13 empty] | Press drop ratio this iteration |  |  | 0.32176 |  |  | 0.27683 |  |  | -0.28514 |  |  | 1.8005 |  |  | 1.1601 |  |  | 1.0667 |  |  | 1.0366 |  |  | 1.0237 |  |  | 1.0174 |  |  | 1.0126
[13 empty] | Expansion factor | 12 |  | 0.83242 |  |  | 0.85586 |  |  | 1.1499 |  |  | 0.040257 |  |  | 0.36241 |  |  | 0.3786 |  |  | 0.35029 |  |  | 0.28265 |  |  | 0.42573 |  |  | 0.10398
[13 empty] | C Non choked w/ reducers | 5 |  | 40.7281 |  |  | 92.4041 |  |  | #NUM! |  |  | 4100.0087 |  |  | 192.7705 |  |  | 119.5456 |  |  | 98.5617 |  |  | 103.8726 |  |  | 67.2004 |  |  | 312.7892
[13 empty] | C Choked w/ reducers | 5 |  | 36.0396 |  |  | 77.9692 |  |  | 341.6746 |  |  | 419.8934 |  |  | 144.8591 |  |  | 92.6482 |  |  | 72.2655 |  |  | 64.5723 |  |  | 56.2986 |  |  | 79.9483
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 40.7281 |  |  | 92.4041 |  |  | #NUM! |  |  | 419.8934 |  |  | 144.8591 |  |  | 92.6482 |  |  | 72.2655 |  |  | 64.5723 |  |  | 56.2986 |  |  | 79.9483
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 35.9981 | 7478.4664 |  | 80.8041 | 15165.7649 |  | 18000 | 37135.3876 |  | 18000 | 72330.2563 |  | 18000 | 121347.6697 |  | 18000 | 177110.229 |  | 18000 | 234014.1457 |  | 18000 | 288397.1471 |  | 18000 | 334820.1346 |  | 18000 | 392602.9398
[13 empty] | Next iteration flow rate |  |  | 7628.0357 | Abs Value of | Flow this | 15317.4226 | Abs Value of | Flow this | 37506.7414 | Abs Value of | Flow this | 73053.5589 | Abs Value of | Flow this | 122561.1464 | Abs Value of | Flow this | 178881.3313 | Abs Value of | Flow this | 236354.2872 | Abs Value of | Flow this | 291281.1186 | Abs Value of | Flow this | 338168.336 | Abs Value of | Flow this | 396528.9692 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.3929 |  |  | 82.822 |  |  | 45.8124 |  |  | -78.278 |  |  | -384.0597 |  |  | -920.1115 |  |  | -1673.6342 |  |  | -2588.7092 |  |  | -3520.5754 |  |  | -4874.4133
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42639 |  |  | 0.39951 |  |  | 0.22099 |  |  | -0.37759 |  |  | -1.8526 |  |  | -4.4384 |  |  | -8.0732 |  |  | -12.4873 |  |  | -16.9824 |  |  | -23.513
[13 empty] | Delta P at this iteration flow rate |  |  | 28.3929 |  |  | 22.822 |  |  | -14.1876 |  |  | -138.278 |  |  | -444.0597 |  |  | -980.1115 |  |  | -1733.6342 |  |  | -2648.7092 |  |  | -3580.5754 |  |  | -4934.4133
[13 empty] | Press drop ratio this iteration |  |  | 0.32121 |  |  | 0.27556 |  |  | -0.30969 |  |  | 1.7665 |  |  | 1.1562 |  |  | 1.0652 |  |  | 1.0359 |  |  | 1.0232 |  |  | 1.017 |  |  | 1.0123
[13 empty] | Expansion factor | 12 |  | 0.83271 |  |  | 0.85652 |  |  | 1.1628 |  |  | 0.058356 |  |  | 0.36455 |  |  | 0.37944 |  |  | 0.35077 |  |  | 0.28298 |  |  | 0.42593 |  |  | 0.10421
[13 empty] | C Non choked w/ reducers | 5 |  | 41.5974 |  |  | 93.636 |  |  | #NUM! |  |  | 2761.6998 |  |  | 189.1627 |  |  | 117.9469 |  |  | 97.3834 |  |  | 102.6735 |  |  | 66.4813 |  |  | 308.9528
[13 empty] | C Choked w/ reducers | 5 |  | 36.79 |  |  | 78.8877 |  |  | 351.684 |  |  | 406.1038 |  |  | 142.7476 |  |  | 91.5501 |  |  | 71.4724 |  |  | 63.8882 |  |  | 55.7125 |  |  | 79.1272
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 41.5974 |  |  | 93.636 |  |  | #NUM! |  |  | 406.1038 |  |  | 142.7476 |  |  | 91.5501 |  |  | 71.4724 |  |  | 63.8882 |  |  | 55.7125 |  |  | 79.1272
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 36.8674 | 7628.0357 |  | 82.036 | 15317.4226 |  | 18000 | 37506.7414 |  | 18000 | 73053.5589 |  | 18000 | 122561.1464 |  | 18000 | 178881.3313 |  | 18000 | 236354.2872 |  | 18000 | 291281.1186 |  | 18000 | 338168.336 |  | 18000 | 396528.9692
[13 empty] | Next iteration flow rate |  |  | 7780.5964 | Abs Value of | Flow this | 15470.5968 | Abs Value of | Flow this | 37881.8088 | Abs Value of | Flow this | 73784.0945 | Abs Value of | Flow this | 123786.7579 | Abs Value of | Flow this | 180670.1446 | Abs Value of | Flow this | 238717.8301 | Abs Value of | Flow this | 294193.9298 | Abs Value of | Flow this | 341550.0193 | Abs Value of | Flow this | 400494.2588 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.3187 |  |  | 82.6731 |  |  | 44.9196 |  |  | -81.665 |  |  | -393.5929 |  |  | -940.4193 |  |  | -1709.0879 |  |  | -2642.5559 |  |  | -3593.1526 |  |  | -4974.2026
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42603 |  |  | 0.39879 |  |  | 0.21668 |  |  | -0.39393 |  |  | -1.8986 |  |  | -4.5363 |  |  | -8.2442 |  |  | -12.747 |  |  | -17.3325 |  |  | -23.9943
[13 empty] | Delta P at this iteration flow rate |  |  | 28.3187 |  |  | 22.6731 |  |  | -15.0804 |  |  | -141.665 |  |  | -453.5929 |  |  | -1000.4193 |  |  | -1769.0879 |  |  | -2702.5559 |  |  | -3653.1526 |  |  | -5034.2026
[13 empty] | Press drop ratio this iteration |  |  | 0.32064 |  |  | 0.27425 |  |  | -0.33572 |  |  | 1.7347 |  |  | 1.1524 |  |  | 1.0638 |  |  | 1.0351 |  |  | 1.0227 |  |  | 1.0167 |  |  | 1.0121
[13 empty] | Expansion factor | 12 |  | 0.83301 |  |  | 0.8572 |  |  | 1.1765 |  |  | 0.075302 |  |  | 0.36663 |  |  | 0.38026 |  |  | 0.35123 |  |  | 0.28332 |  |  | 0.42612 |  |  | 0.10443
[13 empty] | C Non choked w/ reducers | 5 |  | 42.4876 |  |  | 94.8925 |  |  | #NUM! |  |  | 2090.8528 |  |  | 185.6734 |  |  | 116.3794 |  |  | 96.2236 |  |  | 101.4919 |  |  | 65.7709 |  |  | 305.1797
[13 empty] | C Choked w/ reducers | 5 |  | 37.5574 |  |  | 79.82 |  |  | 362.2606 |  |  | 393.1535 |  |  | 140.683 |  |  | 90.4688 |  |  | 70.6897 |  |  | 63.2122 |  |  | 55.133 |  |  | 78.3152
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 42.4876 |  |  | 94.8925 |  |  | #NUM! |  |  | 393.1535 |  |  | 140.683 |  |  | 90.4688 |  |  | 70.6897 |  |  | 63.2122 |  |  | 55.133 |  |  | 78.3152
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 37.7576 | 7780.5964 |  | 83.2925 | 15470.5968 |  | 18000 | 37881.8088 |  | 18000 | 73784.0945 |  | 18000 | 123786.7579 |  | 18000 | 180670.1446 |  | 18000 | 238717.8301 |  | 18000 | 294193.9298 |  | 18000 | 341550.0193 |  | 18000 | 400494.2588
[13 empty] | Next iteration flow rate |  |  | 7936.2083 | Abs Value of | Flow this | 15625.3028 | Abs Value of | Flow this | 38260.6269 | Abs Value of | Flow this | 74521.9354 | Abs Value of | Flow this | 125024.6255 | Abs Value of | Flow this | 182476.8461 | Abs Value of | Flow this | 241105.0084 | Abs Value of | Flow this | 297135.8691 | Abs Value of | Flow this | 344965.5195 | Abs Value of | Flow this | 404499.2014 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.2415 |  |  | 82.5212 |  |  | 44.0089 |  |  | -85.1201 |  |  | -403.3178 |  |  | -961.1354 |  |  | -1745.2542 |  |  | -2697.4849 |  |  | -3667.1886 |  |  | -5075.9977
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42565 |  |  | 0.39806 |  |  | 0.21229 |  |  | -0.4106 |  |  | -1.9455 |  |  | -4.6363 |  |  | -8.4187 |  |  | -13.012 |  |  | -17.6896 |  |  | -24.4853
[13 empty] | Delta P at this iteration flow rate |  |  | 28.2415 |  |  | 22.5212 |  |  | -15.9911 |  |  | -145.1201 |  |  | -463.3178 |  |  | -1021.1354 |  |  | -1805.2542 |  |  | -2757.4849 |  |  | -3727.1886 |  |  | -5135.9977
[13 empty] | Press drop ratio this iteration |  |  | 0.32005 |  |  | 0.27291 |  |  | -0.36336 |  |  | 1.7049 |  |  | 1.1488 |  |  | 1.0624 |  |  | 1.0344 |  |  | 1.0222 |  |  | 1.0164 |  |  | 1.0118
[13 empty] | Expansion factor | 12 |  | 0.83332 |  |  | 0.8579 |  |  | 1.191 |  |  | 0.091199 |  |  | 0.36865 |  |  | 0.38106 |  |  | 0.35169 |  |  | 0.28364 |  |  | 0.42631 |  |  | 0.10464
[13 empty] | C Non choked w/ reducers | 5 |  | 43.3994 |  |  | 96.1745 |  |  | #NUM! |  |  | 1687.4466 |  |  | 182.2965 |  |  | 114.8422 |  |  | 95.0819 |  |  | 100.3275 |  |  | 65.0693 |  |  | 301.4683
[13 empty] | C Choked w/ reducers | 5 |  | 38.342 |  |  | 80.7666 |  |  | 373.455 |  |  | 380.967 |  |  | 138.6637 |  |  | 89.4041 |  |  | 69.9171 |  |  | 62.5442 |  |  | 54.5602 |  |  | 77.5121
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 43.3994 |  |  | 96.1745 |  |  | #NUM! |  |  | 380.967 |  |  | 138.6637 |  |  | 89.4041 |  |  | 69.9171 |  |  | 62.5442 |  |  | 54.5602 |  |  | 77.5121
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 38.6694 | 7936.2083 |  | 84.5745 | 15625.3028 |  | 18000 | 38260.6269 |  | 18000 | 74521.9354 |  | 18000 | 125024.6255 |  | 18000 | 182476.8461 |  | 18000 | 241105.0084 |  | 18000 | 297135.8691 |  | 18000 | 344965.5195 |  | 18000 | 404499.2014
[13 empty] | Next iteration flow rate |  |  | 8094.9325 | Abs Value of | Flow this | 15781.5558 | Abs Value of | Flow this | 38643.2332 | Abs Value of | Flow this | 75267.1548 | Abs Value of | Flow this | 126274.8717 | Abs Value of | Flow this | 184301.6145 | Abs Value of | Flow this | 243516.0584 | Abs Value of | Flow this | 300107.2278 | Abs Value of | Flow this | 348415.1747 | Abs Value of | Flow this | 408544.1934 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.1612 |  |  | 82.3663 |  |  | 43.0798 |  |  | -88.6446 |  |  | -413.2381 |  |  | -982.2679 |  |  | -1782.1474 |  |  | -2753.518 |  |  | -3742.7127 |  |  | -5179.8389
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42527 |  |  | 0.39731 |  |  | 0.20781 |  |  | -0.4276 |  |  | -1.9934 |  |  | -4.7382 |  |  | -8.5966 |  |  | -13.2823 |  |  | -18.0539 |  |  | -24.9862
[13 empty] | Delta P at this iteration flow rate |  |  | 28.1612 |  |  | 22.3663 |  |  | -16.9202 |  |  | -148.6446 |  |  | -473.2381 |  |  | -1042.2679 |  |  | -1842.1474 |  |  | -2813.518 |  |  | -3802.7127 |  |  | -5239.8389
[13 empty] | Press drop ratio this iteration |  |  | 0.31943 |  |  | 0.27155 |  |  | -0.39276 |  |  | 1.6769 |  |  | 1.1452 |  |  | 1.0611 |  |  | 1.0337 |  |  | 1.0218 |  |  | 1.016 |  |  | 1.0116
[13 empty] | Expansion factor | 12 |  | 0.83364 |  |  | 0.85861 |  |  | 1.2065 |  |  | 0.10614 |  |  | 0.37061 |  |  | 0.38185 |  |  | 0.35214 |  |  | 0.28396 |  |  | 0.4265 |  |  | 0.10485
[13 empty] | C Non choked w/ reducers | 5 |  | 44.3335 |  |  | 97.4829 |  |  | #NUM! |  |  | 1417.9023 |  |  | 179.0262 |  |  | 113.3343 |  |  | 93.9579 |  |  | 99.1798 |  |  | 64.3761 |  |  | 297.8171
[13 empty] | C Choked w/ reducers | 5 |  | 39.1445 |  |  | 81.7278 |  |  | 385.3239 |  |  | 369.4778 |  |  | 136.6883 |  |  | 88.3555 |  |  | 69.1544 |  |  | 61.8842 |  |  | 53.9938 |  |  | 76.7178
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 44.3335 |  |  | 97.4829 |  |  | #NUM! |  |  | 369.4778 |  |  | 136.6883 |  |  | 88.3555 |  |  | 69.1544 |  |  | 61.8842 |  |  | 53.9938 |  |  | 76.7178
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 39.6035 | 8094.9325 |  | 85.8829 | 15781.5558 |  | 18000 | 38643.2332 |  | 18000 | 75267.1548 |  | 18000 | 126274.8717 |  | 18000 | 184301.6145 |  | 18000 | 243516.0584 |  | 18000 | 300107.2278 |  | 18000 | 348415.1747 |  | 18000 | 408544.1934
[13 empty] | Next iteration flow rate |  |  | 8256.8311 | Abs Value of | Flow this | 15939.3714 | Abs Value of | Flow this | 39029.6655 | Abs Value of | Flow this | 76019.8263 | Abs Value of | Flow this | 127537.6204 | Abs Value of | Flow this | 186144.6307 | Abs Value of | Flow this | 245951.219 | Abs Value of | Flow this | 303108.3 | Abs Value of | Flow this | 351899.3265 | Abs Value of | Flow this | 412629.6354 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 88.0776 |  |  | 82.2082 |  |  | 42.1321 |  |  | -92.24 |  |  | -423.3578 |  |  | -1003.8251 |  |  | -1819.7822 |  |  | -2810.6773 |  |  | -3819.7549 |  |  | -5285.7673
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42486 |  |  | 0.39655 |  |  | 0.20323 |  |  | -0.44494 |  |  | -2.0422 |  |  | -4.8422 |  |  | -8.7782 |  |  | -13.558 |  |  | -18.4255 |  |  | -25.4972
[13 empty] | Delta P at this iteration flow rate |  |  | 28.0776 |  |  | 22.2082 |  |  | -17.8679 |  |  | -152.24 |  |  | -483.3578 |  |  | -1063.8251 |  |  | -1879.7822 |  |  | -2870.6773 |  |  | -3879.7549 |  |  | -5345.7673
[13 empty] | Press drop ratio this iteration |  |  | 0.31878 |  |  | 0.27015 |  |  | -0.42409 |  |  | 1.6505 |  |  | 1.1417 |  |  | 1.0598 |  |  | 1.033 |  |  | 1.0213 |  |  | 1.0157 |  |  | 1.0114
[13 empty] | Expansion factor | 12 |  | 0.83398 |  |  | 0.85934 |  |  | 1.2229 |  |  | 0.1202 |  |  | 0.37252 |  |  | 0.38261 |  |  | 0.35257 |  |  | 0.28427 |  |  | 0.42668 |  |  | 0.10505
[13 empty] | C Non choked w/ reducers | 5 |  | 45.2907 |  |  | 98.8185 |  |  | #NUM! |  |  | 1224.9124 |  |  | 175.8573 |  |  | 111.8549 |  |  | 92.8511 |  |  | 98.0485 |  |  | 63.6914 |  |  | 294.2247
[13 empty] | C Choked w/ reducers | 5 |  | 39.9653 |  |  | 82.7038 |  |  | 397.9313 |  |  | 358.6269 |  |  | 134.7552 |  |  | 87.3226 |  |  | 68.4014 |  |  | 61.232 |  |  | 53.4338 |  |  | 75.9322
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 45.2907 |  |  | 98.8185 |  |  | #NUM! |  |  | 358.6269 |  |  | 134.7552 |  |  | 87.3226 |  |  | 68.4014 |  |  | 61.232 |  |  | 53.4338 |  |  | 75.9322
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 40.5607 | 8256.8311 |  | 87.2185 | 15939.3714 |  | 18000 | 39029.6655 |  | 18000 | 76019.8263 |  | 18000 | 127537.6204 |  | 18000 | 186144.6307 |  | 18000 | 245951.219 |  | 18000 | 303108.3 |  | 18000 | 351899.3265 |  | 18000 | 412629.6354
[13 empty] | Next iteration flow rate |  |  | 8421.9678 | Abs Value of | Flow this | 16098.7651 | Abs Value of | Flow this | 39419.9622 | Abs Value of | Flow this | 76780.0246 | Abs Value of | Flow this | 128812.9966 | Abs Value of | Flow this | 188006.077 | Abs Value of | Flow this | 248410.7312 | Abs Value of | Flow this | 306139.383 | Abs Value of | Flow this | 355418.3197 | Abs Value of | Flow this | 416755.9317 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.9906 |  |  | 82.047 |  |  | 41.1653 |  |  | -95.9077 |  |  | -433.6809 |  |  | -1025.8156 |  |  | -1858.1735 |  |  | -2868.9856 |  |  | -3898.3456 |  |  | -5393.8248
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42444 |  |  | 0.39577 |  |  | 0.19857 |  |  | -0.46263 |  |  | -2.092 |  |  | -4.9483 |  |  | -8.9634 |  |  | -13.8393 |  |  | -18.8046 |  |  | -26.0185
[13 empty] | Delta P at this iteration flow rate |  |  | 27.9906 |  |  | 22.047 |  |  | -18.8347 |  |  | -155.9077 |  |  | -493.6809 |  |  | -1085.8156 |  |  | -1918.1735 |  |  | -2928.9856 |  |  | -3958.3456 |  |  | -5453.8248
[13 empty] | Press drop ratio this iteration |  |  | 0.31811 |  |  | 0.26871 |  |  | -0.45754 |  |  | 1.6256 |  |  | 1.1384 |  |  | 1.0585 |  |  | 1.0323 |  |  | 1.0209 |  |  | 1.0154 |  |  | 1.0111
[13 empty] | Expansion factor | 12 |  | 0.83433 |  |  | 0.86009 |  |  | 1.2405 |  |  | 0.13346 |  |  | 0.37437 |  |  | 0.38336 |  |  | 0.353 |  |  | 0.28457 |  |  | 0.42686 |  |  | 0.10526
[13 empty] | C Non choked w/ reducers | 5 |  | 46.2716 |  |  | 100.1823 |  |  | #NUM! |  |  | 1079.8029 |  |  | 172.7848 |  |  | 110.4031 |  |  | 91.7613 |  |  | 96.9333 |  |  | 63.0148 |  |  | 290.6895
[13 empty] | C Choked w/ reducers | 5 |  | 40.8049 |  |  | 83.6949 |  |  | 411.3496 |  |  | 348.3616 |  |  | 132.863 |  |  | 86.3052 |  |  | 67.6581 |  |  | 60.5874 |  |  | 52.8801 |  |  | 75.1551
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 46.2716 |  |  | 100.1823 |  |  | #NUM! |  |  | 348.3616 |  |  | 132.863 |  |  | 86.3052 |  |  | 67.6581 |  |  | 60.5874 |  |  | 52.8801 |  |  | 75.1551
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 41.5416 | 8421.9678 |  | 88.5823 | 16098.7651 |  | 18000 | 39419.9622 |  | 18000 | 76780.0246 |  | 18000 | 128812.9966 |  | 18000 | 188006.077 |  | 18000 | 248410.7312 |  | 18000 | 306139.383 |  | 18000 | 355418.3197 |  | 18000 | 416755.9317
[13 empty] | Next iteration flow rate |  |  | 8590.4071 | Abs Value of | Flow this | 16259.7527 | Abs Value of | Flow this | 39814.1618 | Abs Value of | Flow this | 77547.8248 | Abs Value of | Flow this | 130101.1266 | Abs Value of | Flow this | 189886.1377 | Abs Value of | Flow this | 250894.8385 | Abs Value of | Flow this | 309200.7769 | Abs Value of | Flow this | 358972.5029 | Abs Value of | Flow this | 420923.4911 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.9001 |  |  | 81.8825 |  |  | 40.1791 |  |  | -99.6491 |  |  | -444.2115 |  |  | -1048.2481 |  |  | -1897.3364 |  |  | -2928.4658 |  |  | -3978.5159 |  |  | -5504.0544
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42401 |  |  | 0.39498 |  |  | 0.19381 |  |  | -0.48068 |  |  | -2.1428 |  |  | -5.0565 |  |  | -9.1523 |  |  | -14.1262 |  |  | -19.1914 |  |  | -26.5502
[13 empty] | Delta P at this iteration flow rate |  |  | 27.9001 |  |  | 21.8825 |  |  | -19.8209 |  |  | -159.6491 |  |  | -504.2115 |  |  | -1108.2481 |  |  | -1957.3364 |  |  | -2988.4658 |  |  | -4038.5159 |  |  | -5564.0544
[13 empty] | Press drop ratio this iteration |  |  | 0.31741 |  |  | 0.26724 |  |  | -0.49331 |  |  | 1.6021 |  |  | 1.1351 |  |  | 1.0572 |  |  | 1.0316 |  |  | 1.0205 |  |  | 1.0151 |  |  | 1.0109
[13 empty] | Expansion factor | 12 |  | 0.83469 |  |  | 0.86085 |  |  | 1.2593 |  |  | 0.14598 |  |  | 0.37618 |  |  | 0.38409 |  |  | 0.35342 |  |  | 0.28487 |  |  | 0.42703 |  |  | 0.10545
[13 empty] | C Non choked w/ reducers | 5 |  | 47.2771 |  |  | 101.5753 |  |  | #NUM! |  |  | 966.6354 |  |  | 169.804 |  |  | 108.9781 |  |  | 90.6879 |  |  | 95.8338 |  |  | 62.3464 |  |  | 287.2103
[13 empty] | C Choked w/ reducers | 5 |  | 41.6638 |  |  | 84.7017 |  |  | 425.6607 |  |  | 338.635 |  |  | 131.0104 |  |  | 85.3028 |  |  | 66.9242 |  |  | 59.9503 |  |  | 52.3327 |  |  | 74.3865
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 47.2771 |  |  | 101.5753 |  |  | #NUM! |  |  | 338.635 |  |  | 131.0104 |  |  | 85.3028 |  |  | 66.9242 |  |  | 59.9503 |  |  | 52.3327 |  |  | 74.3865
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 42.5471 | 8590.4071 |  | 89.9753 | 16259.7527 |  | 18000 | 39814.1618 |  | 18000 | 77547.8248 |  | 18000 | 130101.1266 |  | 18000 | 189886.1377 |  | 18000 | 250894.8385 |  | 18000 | 309200.7769 |  | 18000 | 358972.5029 |  | 18000 | 420923.4911
[13 empty] | Next iteration flow rate |  |  | 8762.2153 | Abs Value of | Flow this | 16422.3503 | Abs Value of | Flow this | 40212.3034 | Abs Value of | Flow this | 78323.3031 | Abs Value of | Flow this | 131402.1379 | Abs Value of | Flow this | 191784.9991 | Abs Value of | Flow this | 253403.7869 | Abs Value of | Flow this | 312292.7846 | Abs Value of | Flow this | 362562.228 | Abs Value of | Flow this | 425132.726 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.806 |  |  | 81.7147 |  |  | 39.1731 |  |  | -103.4656 |  |  | -454.9538 |  |  | -1071.1315 |  |  | -1937.2865 |  |  | -2989.1416 |  |  | -4060.2977 |  |  | -5616.4995
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42355 |  |  | 0.39417 |  |  | 0.18896 |  |  | -0.49909 |  |  | -2.1946 |  |  | -5.1669 |  |  | -9.345 |  |  | -14.4189 |  |  | -19.5859 |  |  | -27.0926
[13 empty] | Delta P at this iteration flow rate |  |  | 27.806 |  |  | 21.7147 |  |  | -20.8269 |  |  | -163.4656 |  |  | -514.9538 |  |  | -1131.1315 |  |  | -1997.2865 |  |  | -3049.1416 |  |  | -4120.2977 |  |  | -5676.4995
[13 empty] | Press drop ratio this iteration |  |  | 0.31668 |  |  | 0.26574 |  |  | -0.53166 |  |  | 1.5799 |  |  | 1.1319 |  |  | 1.056 |  |  | 1.031 |  |  | 1.0201 |  |  | 1.0148 |  |  | 1.0107
[13 empty] | Expansion factor | 12 |  | 0.83507 |  |  | 0.86163 |  |  | 1.2795 |  |  | 0.15782 |  |  | 0.37793 |  |  | 0.3848 |  |  | 0.35383 |  |  | 0.28516 |  |  | 0.42721 |  |  | 0.10565
[13 empty] | C Non choked w/ reducers | 5 |  | 48.308 |  |  | 102.9986 |  |  | #NUM! |  |  | 875.8428 |  |  | 166.9106 |  |  | 107.5793 |  |  | 89.6306 |  |  | 94.7498 |  |  | 61.686 |  |  | 283.7858
[13 empty] | C Choked w/ reducers | 5 |  | 42.5427 |  |  | 85.7244 |  |  | 440.9582 |  |  | 329.4051 |  |  | 129.1962 |  |  | 84.3152 |  |  | 66.1995 |  |  | 59.3208 |  |  | 51.7914 |  |  | 73.6262
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 48.308 |  |  | 102.9986 |  |  | #NUM! |  |  | 329.4051 |  |  | 129.1962 |  |  | 84.3152 |  |  | 66.1995 |  |  | 59.3208 |  |  | 51.7914 |  |  | 73.6262
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 43.578 | 8762.2153 |  | 91.3986 | 16422.3503 |  | 18000 | 40212.3034 |  | 18000 | 78323.3031 |  | 18000 | 131402.1379 |  | 18000 | 191784.9991 |  | 18000 | 253403.7869 |  | 18000 | 312292.7846 |  | 18000 | 362562.228 |  | 18000 | 425132.726
[13 empty] | Next iteration flow rate |  |  | 8937.4596 | Abs Value of | Flow this | 16586.5738 | Abs Value of | Flow this | 40614.4265 | Abs Value of | Flow this | 79106.5361 | Abs Value of | Flow this | 132716.1593 | Abs Value of | Flow this | 193702.8491 | Abs Value of | Flow this | 255937.8248 | Abs Value of | Flow this | 315415.7125 | Abs Value of | Flow this | 366187.8502 | Abs Value of | Flow this | 429384.0532 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.7081 |  |  | 81.5435 |  |  | 38.1468 |  |  | -107.3589 |  |  | -465.912 |  |  | -1094.4749 |  |  | -1978.0395 |  |  | -3051.037 |  |  | -4143.7233 |  |  | -5731.2047
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42308 |  |  | 0.39335 |  |  | 0.18401 |  |  | -0.51787 |  |  | -2.2474 |  |  | -5.2795 |  |  | -9.5416 |  |  | -14.7174 |  |  | -19.9883 |  |  | -27.6459
[13 empty] | Delta P at this iteration flow rate |  |  | 27.7081 |  |  | 21.5435 |  |  | -21.8532 |  |  | -167.3589 |  |  | -525.912 |  |  | -1154.4749 |  |  | -2038.0395 |  |  | -3111.037 |  |  | -4203.7233 |  |  | -5791.2047
[13 empty] | Press drop ratio this iteration |  |  | 0.31591 |  |  | 0.2642 |  |  | -0.57287 |  |  | 1.5589 |  |  | 1.1288 |  |  | 1.0548 |  |  | 1.0303 |  |  | 1.0197 |  |  | 1.0145 |  |  | 1.0105
[13 empty] | Expansion factor | 12 |  | 0.83547 |  |  | 0.86244 |  |  | 1.3011 |  |  | 0.16903 |  |  | 0.37963 |  |  | 0.3855 |  |  | 0.35422 |  |  | 0.28545 |  |  | 0.42737 |  |  | 0.10583
[13 empty] | C Non choked w/ reducers | 5 |  | 49.3652 |  |  | 104.4533 |  |  | #NUM! |  |  | 801.3345 |  |  | 164.1005 |  |  | 106.2057 |  |  | 88.5892 |  |  | 93.6809 |  |  | 61.0335 |  |  | 280.4147
[13 empty] | C Choked w/ reducers | 5 |  | 43.442 |  |  | 86.7634 |  |  | 457.3494 |  |  | 320.6341 |  |  | 127.4191 |  |  | 83.3421 |  |  | 65.484 |  |  | 58.6985 |  |  | 51.2562 |  |  | 72.8741
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 49.3652 |  |  | 104.4533 |  |  | #NUM! |  |  | 320.6341 |  |  | 127.4191 |  |  | 83.3421 |  |  | 65.484 |  |  | 58.6985 |  |  | 51.2562 |  |  | 72.8741
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 44.6352 | 8937.4596 |  | 92.8533 | 16586.5738 |  | 18000 | 40614.4265 |  | 18000 | 79106.5361 |  | 18000 | 132716.1593 |  | 18000 | 193702.8491 |  | 18000 | 255937.8248 |  | 18000 | 315415.7125 |  | 18000 | 366187.8502 |  | 18000 | 429384.0532
[13 empty] | Next iteration flow rate |  |  | 9116.2088 | Abs Value of | Flow this | 16752.4395 | Abs Value of | Flow this | 41020.5707 | Abs Value of | Flow this | 79897.6015 | Abs Value of | Flow this | 134043.3208 | Abs Value of | Flow this | 195639.8776 | Abs Value of | Flow this | 258497.203 | Abs Value of | Flow this | 318569.8696 | Abs Value of | Flow this | 369849.7287 | Abs Value of | Flow this | 433677.8938 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.6062 |  |  | 81.3689 |  |  | 37.1 |  |  | -111.3305 |  |  | -477.0905 |  |  | -1118.2874 |  |  | -2019.6118 |  |  | -3114.1764 |  |  | -4228.8258 |  |  | -5848.2156
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42259 |  |  | 0.3925 |  |  | 0.17896 |  |  | -0.53703 |  |  | -2.3014 |  |  | -5.3943 |  |  | -9.7421 |  |  | -15.022 |  |  | -20.3988 |  |  | -28.2103
[13 empty] | Delta P at this iteration flow rate |  |  | 27.6062 |  |  | 21.3689 |  |  | -22.9 |  |  | -171.3305 |  |  | -537.0905 |  |  | -1178.2874 |  |  | -2079.6118 |  |  | -3174.1764 |  |  | -4288.8258 |  |  | -5908.2156
[13 empty] | Press drop ratio this iteration |  |  | 0.31512 |  |  | 0.26262 |  |  | -0.61725 |  |  | 1.5389 |  |  | 1.1258 |  |  | 1.0537 |  |  | 1.0297 |  |  | 1.0193 |  |  | 1.0142 |  |  | 1.0103
[13 empty] | Expansion factor | 12 |  | 0.83588 |  |  | 0.86326 |  |  | 1.3245 |  |  | 0.17966 |  |  | 0.38129 |  |  | 0.38618 |  |  | 0.35462 |  |  | 0.28573 |  |  | 0.42754 |  |  | 0.10602
[13 empty] | C Non choked w/ reducers | 5 |  | 50.4497 |  |  | 105.9406 |  |  | #NUM! |  |  | 739.0488 |  |  | 161.37 |  |  | 104.8568 |  |  | 87.5631 |  |  | 92.6268 |  |  | 60.3887 |  |  | 277.0957
[13 empty] | C Choked w/ reducers | 5 |  | 44.3623 |  |  | 87.819 |  |  | 474.9572 |  |  | 312.2879 |  |  | 125.6779 |  |  | 82.3831 |  |  | 64.7774 |  |  | 58.0835 |  |  | 50.7269 |  |  | 72.1302
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 50.4497 |  |  | 105.9406 |  |  | #NUM! |  |  | 312.2879 |  |  | 125.6779 |  |  | 82.3831 |  |  | 64.7774 |  |  | 58.0835 |  |  | 50.7269 |  |  | 72.1302
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 45.7197 | 9116.2088 |  | 94.3406 | 16752.4395 |  | 18000 | 41020.5707 |  | 18000 | 79897.6015 |  | 18000 | 134043.3208 |  | 18000 | 195639.8776 |  | 18000 | 258497.203 |  | 18000 | 318569.8696 |  | 18000 | 369849.7287 |  | 18000 | 433677.8938
[13 empty] | Next iteration flow rate |  |  | 9298.5329 | Abs Value of | Flow this | 16919.9639 | Abs Value of | Flow this | 41430.7764 | Abs Value of | Flow this | 80696.5775 | Abs Value of | Flow this | 135383.7541 | Abs Value of | Flow this | 197596.2764 | Abs Value of | Flow this | 261082.1751 | Abs Value of | Flow this | 321755.5683 | Abs Value of | Flow this | 373548.226 | Abs Value of | Flow this | 438014.6727 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.5002 |  |  | 81.1908 |  |  | 36.032 |  |  | -115.3818 |  |  | -488.4936 |  |  | -1142.5787 |  |  | -2062.0196 |  |  | -3178.585 |  |  | -4315.6388 |  |  | -5967.5783
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42208 |  |  | 0.39164 |  |  | 0.17381 |  |  | -0.55657 |  |  | -2.3564 |  |  | -5.5115 |  |  | -9.9467 |  |  | -15.3327 |  |  | -20.8176 |  |  | -28.7861
[13 empty] | Delta P at this iteration flow rate |  |  | 27.5002 |  |  | 21.1908 |  |  | -23.968 |  |  | -175.3818 |  |  | -548.4936 |  |  | -1202.5787 |  |  | -2122.0196 |  |  | -3238.585 |  |  | -4375.6388 |  |  | -6027.5783
[13 empty] | Press drop ratio this iteration |  |  | 0.31429 |  |  | 0.261 |  |  | -0.66518 |  |  | 1.52 |  |  | 1.1228 |  |  | 1.0525 |  |  | 1.0291 |  |  | 1.0189 |  |  | 1.0139 |  |  | 1.0101
[13 empty] | Expansion factor | 12 |  | 0.83632 |  |  | 0.8641 |  |  | 1.3497 |  |  | 0.18975 |  |  | 0.38291 |  |  | 0.38684 |  |  | 0.355 |  |  | 0.286 |  |  | 0.4277 |  |  | 0.1062
[13 empty] | C Non choked w/ reducers | 5 |  | 51.5623 |  |  | 107.4616 |  |  | #NUM! |  |  | 686.1728 |  |  | 158.7154 |  |  | 103.5318 |  |  | 86.5521 |  |  | 91.5872 |  |  | 59.7516 |  |  | 273.8276
[13 empty] | C Choked w/ reducers | 5 |  | 45.3044 |  |  | 88.8918 |  |  | 493.9244 |  |  | 304.3359 |  |  | 123.9716 |  |  | 81.4379 |  |  | 64.0796 |  |  | 57.4756 |  |  | 50.2036 |  |  | 71.3944
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 51.5623 |  |  | 107.4616 |  |  | #NUM! |  |  | 304.3359 |  |  | 123.9716 |  |  | 81.4379 |  |  | 64.0796 |  |  | 57.4756 |  |  | 50.2036 |  |  | 71.3944
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 46.8323 | 9298.5329 |  | 95.8616 | 16919.9639 |  | 18000 | 41430.7764 |  | 18000 | 80696.5775 |  | 18000 | 135383.7541 |  | 18000 | 197596.2764 |  | 18000 | 261082.1751 |  | 18000 | 321755.5683 |  | 18000 | 373548.226 |  | 18000 | 438014.6727
[13 empty] | Next iteration flow rate |  |  | 9484.5036 | Abs Value of | Flow this | 17089.1635 | Abs Value of | Flow this | 41845.0842 | Abs Value of | Flow this | 81503.5433 | Abs Value of | Flow this | 136737.5916 | Abs Value of | Flow this | 199572.2391 | Abs Value of | Flow this | 263692.9968 | Abs Value of | Flow this | 324973.124 | Abs Value of | Flow this | 377283.7083 | Abs Value of | Flow this | 442394.8194 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.3899 |  |  | 81.0091 |  |  | 34.9427 |  |  | -119.5146 |  |  | -500.1259 |  |  | -1167.3581 |  |  | -2105.2798 |  |  | -3244.2882 |  |  | -4404.1968 |  |  | -6089.3403
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42155 |  |  | 0.39077 |  |  | 0.16855 |  |  | -0.57651 |  |  | -2.4125 |  |  | -5.631 |  |  | -10.1553 |  |  | -15.6496 |  |  | -21.2447 |  |  | -29.3735
[13 empty] | Delta P at this iteration flow rate |  |  | 27.3899 |  |  | 21.0091 |  |  | -25.0573 |  |  | -179.5146 |  |  | -560.1259 |  |  | -1227.3581 |  |  | -2165.2798 |  |  | -3304.2882 |  |  | -4464.1968 |  |  | -6149.3403
[13 empty] | Press drop ratio this iteration |  |  | 0.31342 |  |  | 0.25934 |  |  | -0.7171 |  |  | 1.502 |  |  | 1.12 |  |  | 1.0514 |  |  | 1.0285 |  |  | 1.0185 |  |  | 1.0136 |  |  | 1.0099
[13 empty] | Expansion factor | 12 |  | 0.83677 |  |  | 0.86496 |  |  | 1.3769 |  |  | 0.19933 |  |  | 0.38448 |  |  | 0.38749 |  |  | 0.35537 |  |  | 0.28627 |  |  | 0.42786 |  |  | 0.10638
[13 empty] | C Non choked w/ reducers | 5 |  | 52.7042 |  |  | 109.0178 |  |  | #NUM! |  |  | 640.6966 |  |  | 156.1335 |  |  | 102.2301 |  |  | 85.5559 |  |  | 90.5619 |  |  | 59.122 |  |  | 270.6094
[13 empty] | C Choked w/ reducers | 5 |  | 46.2688 |  |  | 89.9821 |  |  | 514.4163 |  |  | 296.7501 |  |  | 122.2991 |  |  | 80.5064 |  |  | 63.3905 |  |  | 56.8747 |  |  | 49.6861 |  |  | 70.6664
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 52.7042 |  |  | 109.0178 |  |  | #NUM! |  |  | 296.7501 |  |  | 122.2991 |  |  | 80.5064 |  |  | 63.3905 |  |  | 56.8747 |  |  | 49.6861 |  |  | 70.6664
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 47.9742 | 9484.5036 |  | 97.4178 | 17089.1635 |  | 18000 | 41845.0842 |  | 18000 | 81503.5433 |  | 18000 | 136737.5916 |  | 18000 | 199572.2391 |  | 18000 | 263692.9968 |  | 18000 | 324973.124 |  | 18000 | 377283.7083 |  | 18000 | 442394.8194
[13 empty] | Next iteration flow rate |  |  | 9674.1937 | Abs Value of | Flow this | 17260.0552 | Abs Value of | Flow this | 42263.535 | Abs Value of | Flow this | 82318.5787 | Abs Value of | Flow this | 138104.9675 | Abs Value of | Flow this | 201567.9615 | Abs Value of | Flow this | 266329.9268 | Abs Value of | Flow this | 328222.8552 | Abs Value of | Flow this | 381056.5454 | Abs Value of | Flow this | 446818.7676 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.2751 |  |  | 80.8238 |  |  | 33.8314 |  |  | -123.7305 |  |  | -511.9921 |  |  | -1192.6356 |  |  | -2149.4096 |  |  | -3311.312 |  |  | -4494.5348 |  |  | -6213.5497
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42099 |  |  | 0.38987 |  |  | 0.16319 |  |  | -0.59684 |  |  | -2.4697 |  |  | -5.753 |  |  | -10.3682 |  |  | -15.9729 |  |  | -21.6805 |  |  | -29.9726
[13 empty] | Delta P at this iteration flow rate |  |  | 27.2751 |  |  | 20.8238 |  |  | -26.1686 |  |  | -183.7305 |  |  | -571.9921 |  |  | -1252.6356 |  |  | -2209.4096 |  |  | -3371.312 |  |  | -4554.5348 |  |  | -6273.5497
[13 empty] | Press drop ratio this iteration |  |  | 0.31252 |  |  | 0.25764 |  |  | -0.7735 |  |  | 1.4849 |  |  | 1.1172 |  |  | 1.0503 |  |  | 1.0279 |  |  | 1.0181 |  |  | 1.0133 |  |  | 1.0097
[13 empty] | Expansion factor | 12 |  | 0.83724 |  |  | 0.86585 |  |  | 1.4066 |  |  | 0.20845 |  |  | 0.386 |  |  | 0.38812 |  |  | 0.35574 |  |  | 0.28653 |  |  | 0.42801 |  |  | 0.10655
[13 empty] | C Non choked w/ reducers | 5 |  | 53.8764 |  |  | 110.6106 |  |  | #NUM! |  |  | 601.1457 |  |  | 153.621 |  |  | 100.9511 |  |  | 84.5742 |  |  | 89.5506 |  |  | 58.4998 |  |  | 267.4398
[13 empty] | C Choked w/ reducers | 5 |  | 47.2562 |  |  | 91.0903 |  |  | 536.6268 |  |  | 289.5053 |  |  | 120.6593 |  |  | 79.5881 |  |  | 62.71 |  |  | 56.2808 |  |  | 49.1743 |  |  | 69.9463
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 53.8764 |  |  | 110.6106 |  |  | #NUM! |  |  | 289.5053 |  |  | 120.6593 |  |  | 79.5881 |  |  | 62.71 |  |  | 56.2808 |  |  | 49.1743 |  |  | 69.9463
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 49.1464 | 9674.1937 |  | 99.0106 | 17260.0552 |  | 18000 | 42263.535 |  | 18000 | 82318.5787 |  | 18000 | 138104.9675 |  | 18000 | 201567.9615 |  | 18000 | 266329.9268 |  | 18000 | 328222.8552 |  | 18000 | 381056.5454 |  | 18000 | 446818.7676
[13 empty] | Next iteration flow rate |  |  | 9867.6775 | Abs Value of | Flow this | 17432.6557 | Abs Value of | Flow this | 42686.1704 | Abs Value of | Flow this | 83141.7645 | Abs Value of | Flow this | 139486.0172 | Abs Value of | Flow this | 203583.6411 | Abs Value of | Flow this | 268993.226 | Abs Value of | Flow this | 331505.0838 | Abs Value of | Flow this | 384867.1108 | Abs Value of | Flow this | 451286.9553 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.1557 |  |  | 80.6347 |  |  | 32.6978 |  |  | -128.0311 |  |  | -524.0968 |  |  | -1218.4212 |  |  | -2194.4263 |  |  | -3379.683 |  |  | -4586.6885 |  |  | -6340.2556
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.42042 |  |  | 0.38896 |  |  | 0.15773 |  |  | -0.61759 |  |  | -2.5281 |  |  | -5.8774 |  |  | -10.5854 |  |  | -16.3027 |  |  | -22.125 |  |  | -30.5838
[13 empty] | Delta P at this iteration flow rate |  |  | 27.1557 |  |  | 20.6347 |  |  | -27.3022 |  |  | -188.0311 |  |  | -584.0968 |  |  | -1278.4212 |  |  | -2254.4263 |  |  | -3439.683 |  |  | -4646.6885 |  |  | -6400.2556
[13 empty] | Press drop ratio this iteration |  |  | 0.31158 |  |  | 0.2559 |  |  | -0.83499 |  |  | 1.4686 |  |  | 1.1145 |  |  | 1.0492 |  |  | 1.0273 |  |  | 1.0178 |  |  | 1.0131 |  |  | 1.0095
[13 empty] | Expansion factor | 12 |  | 0.83773 |  |  | 0.86675 |  |  | 1.4389 |  |  | 0.21713 |  |  | 0.38749 |  |  | 0.38874 |  |  | 0.3561 |  |  | 0.28679 |  |  | 0.42816 |  |  | 0.10672
[13 empty] | C Non choked w/ reducers | 5 |  | 55.08 |  |  | 112.2414 |  |  | #NUM! |  |  | 566.4139 |  |  | 151.1751 |  |  | 99.6941 |  |  | 83.6066 |  |  | 88.5529 |  |  | 57.8849 |  |  | 264.3179
[13 empty] | C Choked w/ reducers | 5 |  | 48.2674 |  |  | 92.2169 |  |  | 560.7837 |  |  | 282.5785 |  |  | 119.0512 |  |  | 78.6828 |  |  | 62.0377 |  |  | 55.6936 |  |  | 48.6681 |  |  | 69.234
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 55.08 |  |  | 112.2414 |  |  | #NUM! |  |  | 282.5785 |  |  | 119.0512 |  |  | 78.6828 |  |  | 62.0377 |  |  | 55.6936 |  |  | 48.6681 |  |  | 69.234
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 50.35 | 9867.6775 |  | 100.6414 | 17432.6557 |  | 18000 | 42686.1704 |  | 18000 | 83141.7645 |  | 18000 | 139486.0172 |  | 18000 | 203583.6411 |  | 18000 | 268993.226 |  | 18000 | 331505.0838 |  | 18000 | 384867.1108 |  | 18000 | 451286.9553
[13 empty] | Next iteration flow rate |  |  | 10065.0311 | Abs Value of | Flow this | 17606.9823 | Abs Value of | Flow this | 43113.0321 | Abs Value of | Flow this | 83973.1821 | Abs Value of | Flow this | 140880.8774 | Abs Value of | Flow this | 205619.4776 | Abs Value of | Flow this | 271683.1583 | Abs Value of | Flow this | 334820.1346 | Abs Value of | Flow this | 388715.7819 | Abs Value of | Flow this | 455799.8248 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 87.0315 |  |  | 80.4419 |  |  | 31.5414 |  |  | -132.4182 |  |  | -536.4447 |  |  | -1244.7251 |  |  | -2240.3479 |  |  | -3449.4283 |  |  | -4680.6946 |  |  | -6469.5084
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41982 |  |  | 0.38803 |  |  | 0.15215 |  |  | -0.63875 |  |  | -2.5877 |  |  | -6.0042 |  |  | -10.8069 |  |  | -16.6392 |  |  | -22.5785 |  |  | -31.2073
[13 empty] | Delta P at this iteration flow rate |  |  | 27.0315 |  |  | 20.4419 |  |  | -28.4586 |  |  | -192.4182 |  |  | -596.4447 |  |  | -1304.7251 |  |  | -2300.3479 |  |  | -3509.4283 |  |  | -4740.6946 |  |  | -6529.5084
[13 empty] | Press drop ratio this iteration |  |  | 0.31059 |  |  | 0.25412 |  |  | -0.90226 |  |  | 1.4531 |  |  | 1.1118 |  |  | 1.0482 |  |  | 1.0268 |  |  | 1.0174 |  |  | 1.0128 |  |  | 1.0093
[13 empty] | Expansion factor | 12 |  | 0.83824 |  |  | 0.86768 |  |  | 1.4743 |  |  | 0.22541 |  |  | 0.38894 |  |  | 0.38935 |  |  | 0.35645 |  |  | 0.28704 |  |  | 0.42831 |  |  | 0.10689
[13 empty] | C Non choked w/ reducers | 5 |  | 56.3163 |  |  | 113.9117 |  |  | #NUM! |  |  | 535.655 |  |  | 148.7928 |  |  | 98.4586 |  |  | 82.6528 |  |  | 87.5687 |  |  | 57.2771 |  |  | 261.2425
[13 empty] | C Choked w/ reducers | 5 |  | 49.303 |  |  | 93.3624 |  |  | 587.1572 |  |  | 275.9488 |  |  | 117.474 |  |  | 77.7902 |  |  | 61.3738 |  |  | 55.1132 |  |  | 48.1676 |  |  | 68.5293
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 56.3163 |  |  | 113.9117 |  |  | #NUM! |  |  | 275.9488 |  |  | 117.474 |  |  | 77.7902 |  |  | 61.3738 |  |  | 55.1132 |  |  | 48.1676 |  |  | 68.5293
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 51.5863 | 10065.0311 |  | 102.3117 | 17606.9823 |  | 18000 | 43113.0321 |  | 18000 | 83973.1821 |  | 18000 | 140880.8774 |  | 18000 | 205619.4776 |  | 18000 | 271683.1583 |  | 18000 | 334820.1346 |  | 18000 | 388715.7819 |  | 18000 | 455799.8248
[13 empty] | Next iteration flow rate |  |  | 10266.3317 | Abs Value of | Flow this | 17783.0521 | Abs Value of | Flow this | 43544.1624 | Abs Value of | Flow this | 84812.9139 | Abs Value of | Flow this | 142289.6861 | Abs Value of | Flow this | 207675.6723 | Abs Value of | Flow this | 274399.9899 | Abs Value of | Flow this | 338168.336 | Abs Value of | Flow this | 392602.9398 | Abs Value of | Flow this | 460357.8231 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.9023 |  |  | 80.2451 |  |  | 30.3617 |  |  | -136.8934 |  |  | -549.0409 |  |  | -1271.5577 |  |  | -2287.1925 |  |  | -3520.5754 |  |  | -4776.5902 |  |  | -6601.3591
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41919 |  |  | 0.38708 |  |  | 0.14646 |  |  | -0.66034 |  |  | -2.6484 |  |  | -6.1337 |  |  | -11.0328 |  |  | -16.9824 |  |  | -23.0411 |  |  | -31.8433
[13 empty] | Delta P at this iteration flow rate |  |  | 26.9023 |  |  | 20.2451 |  |  | -29.6383 |  |  | -196.8934 |  |  | -609.0409 |  |  | -1331.5577 |  |  | -2347.1925 |  |  | -3580.5754 |  |  | -4836.5902 |  |  | -6661.3591
[13 empty] | Press drop ratio this iteration |  |  | 0.30957 |  |  | 0.25229 |  |  | -0.97617 |  |  | 1.4383 |  |  | 1.1093 |  |  | 1.0472 |  |  | 1.0262 |  |  | 1.017 |  |  | 1.0126 |  |  | 1.0091
[13 empty] | Expansion factor | 12 |  | 0.83877 |  |  | 0.86864 |  |  | 1.5131 |  |  | 0.23331 |  |  | 0.39035 |  |  | 0.38994 |  |  | 0.35679 |  |  | 0.28728 |  |  | 0.42846 |  |  | 0.10706
[13 empty] | C Non choked w/ reducers | 5 |  | 57.5866 |  |  | 115.6232 |  |  | #NUM! |  |  | 508.2105 |  |  | 146.4716 |  |  | 97.244 |  |  | 81.7126 |  |  | 86.5977 |  |  | 56.6765 |  |  | 258.2126
[13 empty] | C Choked w/ reducers | 5 |  | 50.3639 |  |  | 94.5272 |  |  | 616.0697 |  |  | 269.5969 |  |  | 115.9267 |  |  | 76.9102 |  |  | 60.7179 |  |  | 54.5394 |  |  | 47.6726 |  |  | 67.8322
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 57.5866 |  |  | 115.6232 |  |  | #NUM! |  |  | 269.5969 |  |  | 115.9267 |  |  | 76.9102 |  |  | 60.7179 |  |  | 54.5394 |  |  | 47.6726 |  |  | 67.8322
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 52.8566 | 10266.3317 |  | 104.0232 | 17783.0521 |  | 18000 | 43544.1624 |  | 18000 | 84812.9139 |  | 18000 | 142289.6861 |  | 18000 | 207675.6723 |  | 18000 | 274399.9899 |  | 18000 | 338168.336 |  | 18000 | 392602.9398 |  | 18000 | 460357.8231
[13 empty] | Next iteration flow rate |  |  | 10471.6584 | Abs Value of | Flow this | 17960.8826 | Abs Value of | Flow this | 43979.604 | Abs Value of | Flow this | 85661.0431 | Abs Value of | Flow this | 143712.583 | Abs Value of | Flow this | 209752.4291 | Abs Value of | Flow this | 277143.9898 | Abs Value of | Flow this | 341550.0193 | Abs Value of | Flow this | 396528.9692 | Abs Value of | Flow this | 464961.4013 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.7678 |  |  | 80.0444 |  |  | 29.1584 |  |  | -141.4586 |  |  | -561.8903 |  |  | -1298.9297 |  |  | -2334.9787 |  |  | -3593.1526 |  |  | -4874.4133 |  |  | -6735.8601
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41855 |  |  | 0.38611 |  |  | 0.14065 |  |  | -0.68236 |  |  | -2.7104 |  |  | -6.2657 |  |  | -11.2634 |  |  | -17.3325 |  |  | -23.513 |  |  | -32.4921
[13 empty] | Delta P at this iteration flow rate |  |  | 26.7678 |  |  | 20.0444 |  |  | -30.8416 |  |  | -201.4586 |  |  | -621.8903 |  |  | -1358.9297 |  |  | -2394.9787 |  |  | -3653.1526 |  |  | -4934.4133 |  |  | -6795.8601
[13 empty] | Press drop ratio this iteration |  |  | 0.3085 |  |  | 0.25042 |  |  | -1.0577 |  |  | 1.4242 |  |  | 1.1068 |  |  | 1.0462 |  |  | 1.0257 |  |  | 1.0167 |  |  | 1.0123 |  |  | 1.0089
[13 empty] | Expansion factor | 12 |  | 0.83933 |  |  | 0.86961 |  |  | 1.556 |  |  | 0.24085 |  |  | 0.39172 |  |  | 0.39052 |  |  | 0.35713 |  |  | 0.28753 |  |  | 0.4286 |  |  | 0.10722
[13 empty] | C Non choked w/ reducers | 5 |  | 58.8921 |  |  | 117.3778 |  |  | #NUM! |  |  | 483.5605 |  |  | 144.209 |  |  | 96.0497 |  |  | 80.7857 |  |  | 85.6396 |  |  | 56.0828 |  |  | 255.2273
[13 empty] | C Choked w/ reducers | 5 |  | 51.4507 |  |  | 95.7119 |  |  | 647.9097 |  |  | 263.5054 |  |  | 114.4084 |  |  | 76.0423 |  |  | 60.0701 |  |  | 53.9722 |  |  | 47.183 |  |  | 67.1425
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 58.8921 |  |  | 117.3778 |  |  | #NUM! |  |  | 263.5054 |  |  | 114.4084 |  |  | 76.0423 |  |  | 60.0701 |  |  | 53.9722 |  |  | 47.183 |  |  | 67.1425
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 54.1621 | 10471.6584 |  | 105.7778 | 17960.8826 |  | 18000 | 43979.604 |  | 18000 | 85661.0431 |  | 18000 | 143712.583 |  | 18000 | 209752.4291 |  | 18000 | 277143.9898 |  | 18000 | 341550.0193 |  | 18000 | 396528.9692 |  | 18000 | 464961.4013
[13 empty] | Next iteration flow rate |  |  | 10681.0915 | Abs Value of | Flow this | 18140.4914 | Abs Value of | Flow this | 44419.4001 | Abs Value of | Flow this | 86517.6535 | Abs Value of | Flow this | 145149.7088 | Abs Value of | Flow this | 211849.9533 | Abs Value of | Flow this | 279915.4297 | Abs Value of | Flow this | 344965.5195 | Abs Value of | Flow this | 400494.2588 | Abs Value of | Flow this | 469611.0153 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.628 |  |  | 79.8397 |  |  | 27.9308 |  |  | -146.1155 |  |  | -574.9979 |  |  | -1326.8518 |  |  | -2383.7254 |  |  | -3667.1886 |  |  | -4974.2026 |  |  | -6873.0645
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41787 |  |  | 0.38513 |  |  | 0.13473 |  |  | -0.70482 |  |  | -2.7736 |  |  | -6.4004 |  |  | -11.4985 |  |  | -17.6896 |  |  | -23.9943 |  |  | -33.1539
[13 empty] | Delta P at this iteration flow rate |  |  | 26.628 |  |  | 19.8397 |  |  | -32.0692 |  |  | -206.1155 |  |  | -634.9979 |  |  | -1386.8518 |  |  | -2443.7254 |  |  | -3727.1886 |  |  | -5034.2026 |  |  | -6933.0645
[13 empty] | Press drop ratio this iteration |  |  | 0.30738 |  |  | 0.24849 |  |  | -1.1482 |  |  | 1.4106 |  |  | 1.1043 |  |  | 1.0452 |  |  | 1.0252 |  |  | 1.0164 |  |  | 1.0121 |  |  | 1.0087
[13 empty] | Expansion factor | 12 |  | 0.83991 |  |  | 0.87061 |  |  | 1.6035 |  |  | 0.24805 |  |  | 0.39306 |  |  | 0.39109 |  |  | 0.35746 |  |  | 0.28776 |  |  | 0.42874 |  |  | 0.10737
[13 empty] | C Non choked w/ reducers | 5 |  | 60.2344 |  |  | 119.1772 |  |  | #NUM! |  |  | 461.2885 |  |  | 142.0026 |  |  | 94.8753 |  |  | 79.8718 |  |  | 84.6942 |  |  | 55.496 |  |  | 252.2856
[13 empty] | C Choked w/ reducers | 5 |  | 52.5645 |  |  | 96.9169 |  |  | 683.1488 |  |  | 257.6581 |  |  | 112.9184 |  |  | 75.1865 |  |  | 59.4301 |  |  | 53.4114 |  |  | 46.6988 |  |  | 66.4601
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 60.2344 |  |  | 119.1772 |  |  | #NUM! |  |  | 257.6581 |  |  | 112.9184 |  |  | 75.1865 |  |  | 59.4301 |  |  | 53.4114 |  |  | 46.6988 |  |  | 66.4601
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 55.5044 | 10681.0915 |  | 107.5772 | 18140.4914 |  | 18000 | 44419.4001 |  | 18000 | 86517.6535 |  | 18000 | 145149.7088 |  | 18000 | 211849.9533 |  | 18000 | 279915.4297 |  | 18000 | 344965.5195 |  | 18000 | 400494.2588 |  | 18000 | 469611.0153
[13 empty] | Next iteration flow rate |  |  | 10894.7133 | Abs Value of | Flow this | 18321.8964 | Abs Value of | Flow this | 44863.5941 | Abs Value of | Flow this | 87382.8301 | Abs Value of | Flow this | 146601.2059 | Abs Value of | Flow this | 213968.4529 | Abs Value of | Flow this | 282714.584 | Abs Value of | Flow this | 348415.1747 | Abs Value of | Flow this | 404499.2014 | Abs Value of | Flow this | 474307.1255 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.4824 |  |  | 79.6308 |  |  | 26.6786 |  |  | -150.8661 |  |  | -588.369 |  |  | -1355.3351 |  |  | -2433.4519 |  |  | -3742.7127 |  |  | -5075.9977 |  |  | -7013.0267
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41717 |  |  | 0.38412 |  |  | 0.12869 |  |  | -0.72774 |  |  | -2.8381 |  |  | -6.5378 |  |  | -11.7384 |  |  | -18.0539 |  |  | -24.4853 |  |  | -33.8291
[13 empty] | Delta P at this iteration flow rate |  |  | 26.4824 |  |  | 19.6308 |  |  | -33.3214 |  |  | -210.8661 |  |  | -648.369 |  |  | -1415.3351 |  |  | -2493.4519 |  |  | -3802.7127 |  |  | -5135.9977 |  |  | -7073.0267
[13 empty] | Press drop ratio this iteration |  |  | 0.30622 |  |  | 0.24652 |  |  | -1.249 |  |  | 1.3977 |  |  | 1.102 |  |  | 1.0443 |  |  | 1.0247 |  |  | 1.016 |  |  | 1.0118 |  |  | 1.0086
[13 empty] | Expansion factor | 12 |  | 0.84052 |  |  | 0.87164 |  |  | 1.6565 |  |  | 0.25494 |  |  | 0.39437 |  |  | 0.39164 |  |  | 0.35778 |  |  | 0.28799 |  |  | 0.42887 |  |  | 0.10753
[13 empty] | C Non choked w/ reducers | 5 |  | 61.6149 |  |  | 121.0235 |  |  | #NUM! |  |  | 441.0577 |  |  | 139.8503 |  |  | 93.7203 |  |  | 78.9707 |  |  | 83.7613 |  |  | 54.916 |  |  | 249.3867
[13 empty] | C Choked w/ reducers | 5 |  | 53.706 |  |  | 98.1428 |  |  | 722.366 |  |  | 252.0403 |  |  | 111.4557 |  |  | 74.3425 |  |  | 58.7978 |  |  | 52.8569 |  |  | 46.2199 |  |  | 65.7851
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 61.6149 |  |  | 121.0235 |  |  | #NUM! |  |  | 252.0403 |  |  | 111.4557 |  |  | 74.3425 |  |  | 58.7978 |  |  | 52.8569 |  |  | 46.2199 |  |  | 65.7851
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 56.8849 | 10894.7133 |  | 109.4235 | 18321.8964 |  | 18000 | 44863.5941 |  | 18000 | 87382.8301 |  | 18000 | 146601.2059 |  | 18000 | 213968.4529 |  | 18000 | 282714.584 |  | 18000 | 348415.1747 |  | 18000 | 404499.2014 |  | 18000 | 474307.1255
[13 empty] | Next iteration flow rate |  |  | 11112.6076 | Abs Value of | Flow this | 18505.1153 | Abs Value of | Flow this | 45312.23 | Abs Value of | Flow this | 88256.6584 | Abs Value of | Flow this | 148067.218 | Abs Value of | Flow this | 216108.1374 | Abs Value of | Flow this | 285541.7298 | Abs Value of | Flow this | 351899.3265 | Abs Value of | Flow this | 408544.1934 | Abs Value of | Flow this | 479050.1967 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.331 |  |  | 79.4178 |  |  | 25.4012 |  |  | -155.7121 |  |  | -602.0088 |  |  | -1384.391 |  |  | -2484.1779 |  |  | -3819.7549 |  |  | -5179.8389 |  |  | -7155.8022
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41644 |  |  | 0.38309 |  |  | 0.12253 |  |  | -0.75112 |  |  | -2.9039 |  |  | -6.678 |  |  | -11.9831 |  |  | -18.4255 |  |  | -24.9862 |  |  | -34.5178
[13 empty] | Delta P at this iteration flow rate |  |  | 26.331 |  |  | 19.4178 |  |  | -34.5988 |  |  | -215.7121 |  |  | -662.0088 |  |  | -1444.391 |  |  | -2544.1779 |  |  | -3879.7549 |  |  | -5239.8389 |  |  | -7215.8022
[13 empty] | Press drop ratio this iteration |  |  | 0.305 |  |  | 0.2445 |  |  | -1.3621 |  |  | 1.3853 |  |  | 1.0997 |  |  | 1.0433 |  |  | 1.0242 |  |  | 1.0157 |  |  | 1.0116 |  |  | 1.0084
[13 empty] | Expansion factor | 12 |  | 0.84115 |  |  | 0.87269 |  |  | 1.716 |  |  | 0.26154 |  |  | 0.39564 |  |  | 0.39218 |  |  | 0.3581 |  |  | 0.28822 |  |  | 0.42901 |  |  | 0.10768
[13 empty] | C Non choked w/ reducers | 5 |  | 63.0354 |  |  | 122.9188 |  |  | #NUM! |  |  | 422.5919 |  |  | 137.7499 |  |  | 92.5841 |  |  | 78.082 |  |  | 82.8406 |  |  | 54.3426 |  |  | 246.5295
[13 empty] | C Choked w/ reducers | 5 |  | 54.8762 |  |  | 99.3901 |  |  | 766.2795 |  |  | 246.6383 |  |  | 110.0198 |  |  | 73.51 |  |  | 58.1731 |  |  | 52.3087 |  |  | 45.7463 |  |  | 65.1173
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 63.0354 |  |  | 122.9188 |  |  | #NUM! |  |  | 246.6383 |  |  | 110.0198 |  |  | 73.51 |  |  | 58.1731 |  |  | 52.3087 |  |  | 45.7463 |  |  | 65.1173
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 58.3054 | 11112.6076 |  | 111.3188 | 18505.1153 |  | 18000 | 45312.23 |  | 18000 | 88256.6584 |  | 18000 | 148067.218 |  | 18000 | 216108.1374 |  | 18000 | 285541.7298 |  | 18000 | 351899.3265 |  | 18000 | 408544.1934 |  | 18000 | 479050.1967
[13 empty] | Next iteration flow rate |  |  | 11334.8598 | Abs Value of | Flow this | 18690.1665 | Abs Value of | Flow this | 45765.3523 | Abs Value of | Flow this | 89139.2249 | Abs Value of | Flow this | 149547.8901 | Abs Value of | Flow this | 218269.2188 | Abs Value of | Flow this | 288397.1471 | Abs Value of | Flow this | 355418.3197 | Abs Value of | Flow this | 412629.6354 | Abs Value of | Flow this | 483840.6987 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.1735 |  |  | 79.2005 |  |  | 24.0982 |  |  | -160.6555 |  |  | -615.9228 |  |  | -1414.0309 |  |  | -2535.9235 |  |  | -3898.3456 |  |  | -5285.7673 |  |  | -7301.4474
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41568 |  |  | 0.38204 |  |  | 0.11624 |  |  | -0.77496 |  |  | -2.9711 |  |  | -6.8209 |  |  | -12.2327 |  |  | -18.8046 |  |  | -25.4972 |  |  | -35.2204
[13 empty] | Delta P at this iteration flow rate |  |  | 26.1735 |  |  | 19.2005 |  |  | -35.9018 |  |  | -220.6555 |  |  | -675.9228 |  |  | -1474.0309 |  |  | -2595.9235 |  |  | -3958.3456 |  |  | -5345.7673 |  |  | -7361.4474
[13 empty] | Press drop ratio this iteration |  |  | 0.30373 |  |  | 0.24243 |  |  | -1.4898 |  |  | 1.3735 |  |  | 1.0974 |  |  | 1.0424 |  |  | 1.0237 |  |  | 1.0154 |  |  | 1.0114 |  |  | 1.0082
[13 empty] | Expansion factor | 12 |  | 0.84181 |  |  | 0.87377 |  |  | 1.7831 |  |  | 0.26786 |  |  | 0.39687 |  |  | 0.39271 |  |  | 0.35841 |  |  | 0.28844 |  |  | 0.42914 |  |  | 0.10783
[13 empty] | C Non choked w/ reducers | 5 |  | 64.4975 |  |  | 124.8653 |  |  | #NUM! |  |  | 405.6632 |  |  | 135.6995 |  |  | 91.4663 |  |  | 77.2056 |  |  | 81.932 |  |  | 53.7759 |  |  | 243.7132
[13 empty] | C Choked w/ reducers | 5 |  | 56.076 |  |  | 100.6595 |  |  | 815.7918 |  |  | 241.4396 |  |  | 108.6097 |  |  | 72.6888 |  |  | 57.556 |  |  | 51.7667 |  |  | 45.2778 |  |  | 64.4565
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 64.4975 |  |  | 124.8653 |  |  | #NUM! |  |  | 241.4396 |  |  | 108.6097 |  |  | 72.6888 |  |  | 57.556 |  |  | 51.7667 |  |  | 45.2778 |  |  | 64.4565
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 59.7675 | 11334.8598 |  | 113.2653 | 18690.1665 |  | 18000 | 45765.3523 |  | 18000 | 89139.2249 |  | 18000 | 149547.8901 |  | 18000 | 218269.2188 |  | 18000 | 288397.1471 |  | 18000 | 355418.3197 |  | 18000 | 412629.6354 |  | 18000 | 483840.6987
[13 empty] | Next iteration flow rate |  |  | 11561.557 | Abs Value of | Flow this | 18877.0681 | Abs Value of | Flow this | 46223.0059 | Abs Value of | Flow this | 90030.6172 | Abs Value of | Flow this | 151043.369 | Abs Value of | Flow this | 220451.911 | Abs Value of | Flow this | 291281.1186 | Abs Value of | Flow this | 358972.5029 | Abs Value of | Flow this | 416755.9317 | Abs Value of | Flow this | 488679.1057 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 86.0096 |  |  | 78.9788 |  |  | 22.7689 |  |  | -165.6983 |  |  | -630.1165 |  |  | -1444.2665 |  |  | -2588.7092 |  |  | -3978.5159 |  |  | -5393.8248 |  |  | -7450.0202
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41489 |  |  | 0.38097 |  |  | 0.10983 |  |  | -0.79929 |  |  | -3.0395 |  |  | -6.9668 |  |  | -12.4873 |  |  | -19.1914 |  |  | -26.0185 |  |  | -35.937
[13 empty] | Delta P at this iteration flow rate |  |  | 26.0096 |  |  | 18.9788 |  |  | -37.2311 |  |  | -225.6983 |  |  | -690.1165 |  |  | -1504.2665 |  |  | -2648.7092 |  |  | -4038.5159 |  |  | -5453.8248 |  |  | -7510.0202
[13 empty] | Press drop ratio this iteration |  |  | 0.3024 |  |  | 0.2403 |  |  | -1.6352 |  |  | 1.3621 |  |  | 1.0952 |  |  | 1.0415 |  |  | 1.0232 |  |  | 1.0151 |  |  | 1.0111 |  |  | 1.0081
[13 empty] | Expansion factor | 12 |  | 0.84251 |  |  | 0.87488 |  |  | 1.8595 |  |  | 0.27392 |  |  | 0.39808 |  |  | 0.39323 |  |  | 0.35871 |  |  | 0.28866 |  |  | 0.42927 |  |  | 0.10797
[13 empty] | C Non choked w/ reducers | 5 |  | 66.003 |  |  | 126.8656 |  |  | #NUM! |  |  | 390.0814 |  |  | 133.6971 |  |  | 90.3664 |  |  | 76.3413 |  |  | 81.0351 |  |  | 53.2156 |  |  | 240.937
[13 empty] | C Choked w/ reducers | 5 |  | 57.3065 |  |  | 101.9515 |  |  | 872.0521 |  |  | 236.4327 |  |  | 107.2249 |  |  | 71.8788 |  |  | 56.9462 |  |  | 51.2308 |  |  | 44.8145 |  |  | 63.8028
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 66.003 |  |  | 126.8656 |  |  | #NUM! |  |  | 236.4327 |  |  | 107.2249 |  |  | 71.8788 |  |  | 56.9462 |  |  | 51.2308 |  |  | 44.8145 |  |  | 63.8028
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 61.273 | 11561.557 |  | 115.2656 | 18877.0681 |  | 18000 | 46223.0059 |  | 18000 | 90030.6172 |  | 18000 | 151043.369 |  | 18000 | 220451.911 |  | 18000 | 291281.1186 |  | 18000 | 358972.5029 |  | 18000 | 416755.9317 |  | 18000 | 488679.1057
[13 empty] | Next iteration flow rate |  |  | 11792.7881 | Abs Value of | Flow this | 19065.8388 | Abs Value of | Flow this | 46685.2359 | Abs Value of | Flow this | 90930.9234 | Abs Value of | Flow this | 152553.8027 | Abs Value of | Flow this | 222656.4301 | Abs Value of | Flow this | 294193.9298 | Abs Value of | Flow this | 362562.228 | Abs Value of | Flow this | 420923.4911 | Abs Value of | Flow this | 493565.8968 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.8391 |  |  | 78.7526 |  |  | 21.4129 |  |  | -170.8425 |  |  | -644.5955 |  |  | -1475.1099 |  |  | -2642.5559 |  |  | -4060.2977 |  |  | -5504.0544 |  |  | -7601.5792
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41407 |  |  | 0.37988 |  |  | 0.10329 |  |  | -0.8241 |  |  | -3.1094 |  |  | -7.1156 |  |  | -12.747 |  |  | -19.5859 |  |  | -26.5502 |  |  | -36.6681
[13 empty] | Delta P at this iteration flow rate |  |  | 25.8391 |  |  | 18.7526 |  |  | -38.5871 |  |  | -230.8425 |  |  | -704.5955 |  |  | -1535.1099 |  |  | -2702.5559 |  |  | -4120.2977 |  |  | -5564.0544 |  |  | -7661.5792
[13 empty] | Press drop ratio this iteration |  |  | 0.30102 |  |  | 0.23812 |  |  | -1.802 |  |  | 1.3512 |  |  | 1.0931 |  |  | 1.0407 |  |  | 1.0227 |  |  | 1.0148 |  |  | 1.0109 |  |  | 1.0079
[13 empty] | Expansion factor | 12 |  | 0.84323 |  |  | 0.87601 |  |  | 1.9472 |  |  | 0.27973 |  |  | 0.39925 |  |  | 0.39374 |  |  | 0.35901 |  |  | 0.28887 |  |  | 0.42939 |  |  | 0.10811
[13 empty] | C Non choked w/ reducers | 5 |  | 67.554 |  |  | 128.9221 |  |  | #NUM! |  |  | 375.6865 |  |  | 131.741 |  |  | 89.2841 |  |  | 75.4887 |  |  | 80.1498 |  |  | 52.6617 |  |  | 238.2001
[13 empty] | C Choked w/ reducers | 5 |  | 58.5688 |  |  | 103.2667 |  |  | 936.5475 |  |  | 231.6067 |  |  | 105.8645 |  |  | 71.0796 |  |  | 56.3437 |  |  | 50.7009 |  |  | 44.3561 |  |  | 63.156
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 67.554 |  |  | 128.9221 |  |  | #NUM! |  |  | 231.6067 |  |  | 105.8645 |  |  | 71.0796 |  |  | 56.3437 |  |  | 50.7009 |  |  | 44.3561 |  |  | 63.156
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 62.824 | 11792.7881 |  | 117.3221 | 19065.8388 |  | 18000 | 46685.2359 |  | 18000 | 90930.9234 |  | 18000 | 152553.8027 |  | 18000 | 222656.4301 |  | 18000 | 294193.9298 |  | 18000 | 362562.228 |  | 18000 | 420923.4911 |  | 18000 | 493565.8968
[13 empty] | Next iteration flow rate |  |  | 12028.6439 | Abs Value of | Flow this | 19256.4972 | Abs Value of | Flow this | 47152.0883 | Abs Value of | Flow this | 91840.2326 | Abs Value of | Flow this | 154079.3408 | Abs Value of | Flow this | 224882.9944 | Abs Value of | Flow this | 297135.8691 | Abs Value of | Flow this | 366187.8502 | Abs Value of | Flow this | 425132.726 | Abs Value of | Flow this | 498501.5557 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.6617 |  |  | 78.5219 |  |  | 20.0297 |  |  | -176.0901 |  |  | -659.3655 |  |  | -1506.5732 |  |  | -2697.4849 |  |  | -4143.7233 |  |  | -5616.4995 |  |  | -7756.1846
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41321 |  |  | 0.37877 |  |  | 0.096618 |  |  | -0.84941 |  |  | -3.1806 |  |  | -7.2673 |  |  | -13.012 |  |  | -19.9883 |  |  | -27.0926 |  |  | -37.4139
[13 empty] | Delta P at this iteration flow rate |  |  | 25.6617 |  |  | 18.5219 |  |  | -39.9703 |  |  | -236.0901 |  |  | -719.3655 |  |  | -1566.5732 |  |  | -2757.4849 |  |  | -4203.7233 |  |  | -5676.4995 |  |  | -7816.1846
[13 empty] | Press drop ratio this iteration |  |  | 0.29957 |  |  | 0.23588 |  |  | -1.9956 |  |  | 1.3407 |  |  | 1.091 |  |  | 1.0398 |  |  | 1.0222 |  |  | 1.0145 |  |  | 1.0107 |  |  | 1.0077
[13 empty] | Expansion factor | 12 |  | 0.84398 |  |  | 0.87718 |  |  | 2.049 |  |  | 0.28531 |  |  | 0.4004 |  |  | 0.39423 |  |  | 0.3593 |  |  | 0.28908 |  |  | 0.42952 |  |  | 0.10825
[13 empty] | C Non choked w/ reducers | 5 |  | 69.1526 |  |  | 131.0377 |  |  | #NUM! |  |  | 362.3434 |  |  | 129.8294 |  |  | 88.2189 |  |  | 74.6477 |  |  | 79.2759 |  |  | 52.1142 |  |  | 235.5017
[13 empty] | C Choked w/ reducers | 5 |  | 59.8639 |  |  | 104.6058 |  |  | 1011.2366 |  |  | 226.9518 |  |  | 104.5281 |  |  | 70.2911 |  |  | 55.7483 |  |  | 50.177 |  |  | 43.9028 |  |  | 62.5161
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 69.1526 |  |  | 131.0377 |  |  | #NUM! |  |  | 226.9518 |  |  | 104.5281 |  |  | 70.2911 |  |  | 55.7483 |  |  | 50.177 |  |  | 43.9028 |  |  | 62.5161
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 64.4226 | 12028.6439 |  | 119.4377 | 19256.4972 |  | 18000 | 47152.0883 |  | 18000 | 91840.2326 |  | 18000 | 154079.3408 |  | 18000 | 224882.9944 |  | 18000 | 297135.8691 |  | 18000 | 366187.8502 |  | 18000 | 425132.726 |  | 18000 | 498501.5557
[13 empty] | Next iteration flow rate |  |  | 12269.2167 | Abs Value of | Flow this | 19449.0622 | Abs Value of | Flow this | 47623.6092 | Abs Value of | Flow this | 92758.6349 | Abs Value of | Flow this | 155620.1342 | Abs Value of | Flow this | 227131.8243 | Abs Value of | Flow this | 300107.2278 | Abs Value of | Flow this | 369849.7287 | Abs Value of | Flow this | 429384.0532 | Abs Value of | Flow this | 503486.5713 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.4771 |  |  | 78.2866 |  |  | 18.6187 |  |  | -181.4431 |  |  | -674.4323 |  |  | -1538.669 |  |  | -2753.518 |  |  | -4228.8258 |  |  | -5731.2047 |  |  | -7913.8975
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41232 |  |  | 0.37763 |  |  | 0.089812 |  |  | -0.87524 |  |  | -3.2533 |  |  | -7.4222 |  |  | -13.2823 |  |  | -20.3988 |  |  | -27.6459 |  |  | -38.1747
[13 empty] | Delta P at this iteration flow rate |  |  | 25.4771 |  |  | 18.2866 |  |  | -41.3813 |  |  | -241.4431 |  |  | -734.4323 |  |  | -1598.669 |  |  | -2813.518 |  |  | -4288.8258 |  |  | -5791.2047 |  |  | -7973.8975
[13 empty] | Press drop ratio this iteration |  |  | 0.29806 |  |  | 0.23359 |  |  | -2.2226 |  |  | 1.3307 |  |  | 1.089 |  |  | 1.039 |  |  | 1.0218 |  |  | 1.0142 |  |  | 1.0105 |  |  | 1.0076
[13 empty] | Expansion factor | 12 |  | 0.84477 |  |  | 0.87838 |  |  | 2.1683 |  |  | 0.29067 |  |  | 0.40152 |  |  | 0.39471 |  |  | 0.35958 |  |  | 0.28928 |  |  | 0.42964 |  |  | 0.10839
[13 empty] | C Non choked w/ reducers | 5 |  | 70.801 |  |  | 133.2154 |  |  | #NUM! |  |  | 349.9366 |  |  | 127.9609 |  |  | 87.1703 |  |  | 73.818 |  |  | 78.4133 |  |  | 51.5728 |  |  | 232.841
[13 empty] | C Choked w/ reducers | 5 |  | 61.193 |  |  | 105.9694 |  |  | 1098.7526 |  |  | 222.4587 |  |  | 103.2148 |  |  | 69.5131 |  |  | 55.16 |  |  | 49.6589 |  |  | 43.4543 |  |  | 61.8829
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 70.801 |  |  | 133.2154 |  |  | #NUM! |  |  | 222.4587 |  |  | 103.2148 |  |  | 69.5131 |  |  | 55.16 |  |  | 49.6589 |  |  | 43.4543 |  |  | 61.8829
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 66.071 | 12269.2167 |  | 121.6154 | 19449.0622 |  | 18000 | 47623.6092 |  | 18000 | 92758.6349 |  | 18000 | 155620.1342 |  | 18000 | 227131.8243 |  | 18000 | 300107.2278 |  | 18000 | 369849.7287 |  | 18000 | 429384.0532 |  | 18000 | 503486.5713
[13 empty] | Next iteration flow rate |  |  | 12514.6011 | Abs Value of | Flow this | 19643.5528 | Abs Value of | Flow this | 48099.8452 | Abs Value of | Flow this | 93686.2213 | Abs Value of | Flow this | 157176.3355 | Abs Value of | Flow this | 229403.1426 | Abs Value of | Flow this | 303108.3 | Abs Value of | Flow this | 373548.226 | Abs Value of | Flow this | 433677.8938 | Abs Value of | Flow this | 508521.437 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.2851 |  |  | 78.0465 |  |  | 17.1793 |  |  | -186.9037 |  |  | -689.802 |  |  | -1571.4099 |  |  | -2810.6773 |  |  | -4315.6388 |  |  | -5848.2156 |  |  | -8074.7805
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41139 |  |  | 0.37648 |  |  | 0.082869 |  |  | -0.90158 |  |  | -3.3274 |  |  | -7.5801 |  |  | -13.558 |  |  | -20.8176 |  |  | -28.2103 |  |  | -38.9507
[13 empty] | Delta P at this iteration flow rate |  |  | 25.2851 |  |  | 18.0465 |  |  | -42.8207 |  |  | -246.9037 |  |  | -749.802 |  |  | -1631.4099 |  |  | -2870.6773 |  |  | -4375.6388 |  |  | -5908.2156 |  |  | -8134.7805
[13 empty] | Press drop ratio this iteration |  |  | 0.29648 |  |  | 0.23123 |  |  | -2.4926 |  |  | 1.321 |  |  | 1.087 |  |  | 1.0382 |  |  | 1.0213 |  |  | 1.0139 |  |  | 1.0103 |  |  | 1.0074
[13 empty] | Expansion factor | 12 |  | 0.84559 |  |  | 0.8796 |  |  | 2.3102 |  |  | 0.29582 |  |  | 0.40261 |  |  | 0.39519 |  |  | 0.35986 |  |  | 0.28948 |  |  | 0.42976 |  |  | 0.10852
[13 empty] | C Non choked w/ reducers | 5 |  | 72.5017 |  |  | 135.4584 |  |  | #NUM! |  |  | 338.3671 |  |  | 126.1338 |  |  | 86.1381 |  |  | 72.9994 |  |  | 77.5616 |  |  | 51.0376 |  |  | 230.2172
[13 empty] | C Choked w/ reducers | 5 |  | 62.5574 |  |  | 107.3584 |  |  | 1202.7214 |  |  | 218.1188 |  |  | 101.9242 |  |  | 68.7455 |  |  | 54.5786 |  |  | 49.1465 |  |  | 43.0108 |  |  | 61.2565
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 72.5017 |  |  | 135.4584 |  |  | #NUM! |  |  | 218.1188 |  |  | 101.9242 |  |  | 68.7455 |  |  | 54.5786 |  |  | 49.1465 |  |  | 43.0108 |  |  | 61.2565
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 67.7717 | 12514.6011 |  | 123.8584 | 19643.5528 |  | 18000 | 48099.8452 |  | 18000 | 93686.2213 |  | 18000 | 157176.3355 |  | 18000 | 229403.1426 |  | 18000 | 303108.3 |  | 18000 | 373548.226 |  | 18000 | 433677.8938 |  | 18000 | 508521.437
[13 empty] | Next iteration flow rate |  |  | 12764.8931 | Abs Value of | Flow this | 19839.9883 | Abs Value of | Flow this | 48580.8437 | Abs Value of | Flow this | 94623.0835 | Abs Value of | Flow this | 158748.0989 | Abs Value of | Flow this | 231697.174 | Abs Value of | Flow this | 306139.383 | Abs Value of | Flow this | 377283.7083 | Abs Value of | Flow this | 438014.6727 | Abs Value of | Flow this | 513606.6514 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 85.0853 |  |  | 77.8016 |  |  | 15.711 |  |  | -192.4741 |  |  | -705.4807 |  |  | -1604.8088 |  |  | -2868.9856 |  |  | -4404.1968 |  |  | -5967.5783 |  |  | -8238.8972
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.41043 |  |  | 0.3753 |  |  | 0.075786 |  |  | -0.92845 |  |  | -3.4031 |  |  | -7.7412 |  |  | -13.8393 |  |  | -21.2447 |  |  | -28.7861 |  |  | -39.7424
[13 empty] | Delta P at this iteration flow rate |  |  | 25.0853 |  |  | 17.8016 |  |  | -44.289 |  |  | -252.4741 |  |  | -765.4807 |  |  | -1664.8088 |  |  | -2928.9856 |  |  | -4464.1968 |  |  | -6027.5783 |  |  | -8298.8972
[13 empty] | Press drop ratio this iteration |  |  | 0.29483 |  |  | 0.22881 |  |  | -2.819 |  |  | 1.3117 |  |  | 1.085 |  |  | 1.0374 |  |  | 1.0209 |  |  | 1.0136 |  |  | 1.0101 |  |  | 1.0073
[13 empty] | Expansion factor | 12 |  | 0.84645 |  |  | 0.88086 |  |  | 2.4818 |  |  | 0.30077 |  |  | 0.40367 |  |  | 0.39565 |  |  | 0.36013 |  |  | 0.28968 |  |  | 0.42987 |  |  | 0.10865
[13 empty] | C Non choked w/ reducers | 5 |  | 74.2571 |  |  | 137.7701 |  |  | #NUM! |  |  | 327.5497 |  |  | 124.3466 |  |  | 85.1217 |  |  | 72.1917 |  |  | 76.7207 |  |  | 50.5085 |  |  | 227.6297
[13 empty] | C Choked w/ reducers | 5 |  | 63.9584 |  |  | 108.7732 |  |  | 1328.2772 |  |  | 213.9243 |  |  | 100.6556 |  |  | 67.9879 |  |  | 54.0041 |  |  | 48.6399 |  |  | 42.572 |  |  | 60.6366
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 74.2571 |  |  | 137.7701 |  |  | #NUM! |  |  | 213.9243 |  |  | 100.6556 |  |  | 67.9879 |  |  | 54.0041 |  |  | 48.6399 |  |  | 42.572 |  |  | 60.6366
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 69.5271 | 12764.8931 |  | 126.1701 | 19839.9883 |  | 18000 | 48580.8437 |  | 18000 | 94623.0835 |  | 18000 | 158748.0989 |  | 18000 | 231697.174 |  | 18000 | 306139.383 |  | 18000 | 377283.7083 |  | 18000 | 438014.6727 |  | 18000 | 513606.6514
[13 empty] | Next iteration flow rate |  |  | 13020.191 | Abs Value of | Flow this | 20038.3882 | Abs Value of | Flow this | 49066.6521 | Abs Value of | Flow this | 95569.3143 | Abs Value of | Flow this | 160335.5799 | Abs Value of | Flow this | 234014.1457 | Abs Value of | Flow this | 309200.7769 | Abs Value of | Flow this | 381056.5454 | Abs Value of | Flow this | 442394.8194 | Abs Value of | Flow this | 518742.7179 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 84.8775 |  |  | 77.5518 |  |  | 14.2131 |  |  | -198.1565 |  |  | -721.4745 |  |  | -1638.8791 |  |  | -2928.4658 |  |  | -4494.5348 |  |  | -6089.3403 |  |  | -8406.3126
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.40943 |  |  | 0.37409 |  |  | 0.068561 |  |  | -0.95586 |  |  | -3.4802 |  |  | -7.9055 |  |  | -14.1262 |  |  | -21.6805 |  |  | -29.3735 |  |  | -40.55
[13 empty] | Delta P at this iteration flow rate |  |  | 24.8775 |  |  | 17.5518 |  |  | -45.7869 |  |  | -258.1565 |  |  | -781.4745 |  |  | -1698.8791 |  |  | -2988.4658 |  |  | -4554.5348 |  |  | -6149.3403 |  |  | -8466.3126
[13 empty] | Press drop ratio this iteration |  |  | 0.2931 |  |  | 0.22632 |  |  | -3.2215 |  |  | 1.3028 |  |  | 1.0832 |  |  | 1.0366 |  |  | 1.0205 |  |  | 1.0133 |  |  | 1.0099 |  |  | 1.0071
[13 empty] | Expansion factor | 12 |  | 0.84735 |  |  | 0.88216 |  |  | 2.6933 |  |  | 0.30554 |  |  | 0.40471 |  |  | 0.3961 |  |  | 0.3604 |  |  | 0.28987 |  |  | 0.42998 |  |  | 0.10878
[13 empty] | C Non choked w/ reducers | 5 |  | 76.0703 |  |  | 140.1542 |  |  | #NUM! |  |  | 317.4103 |  |  | 122.5981 |  |  | 84.121 |  |  | 71.3948 |  |  | 75.8904 |  |  | 49.9853 |  |  | 225.0777
[13 empty] | C Choked w/ reducers | 5 |  | 65.3973 |  |  | 110.2149 |  |  | 1482.9391 |  |  | 209.8677 |  |  | 99.4085 |  |  | 67.2403 |  |  | 53.4363 |  |  | 48.1389 |  |  | 42.1379 |  |  | 60.0233
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 76.0703 |  |  | 140.1542 |  |  | #NUM! |  |  | 209.8677 |  |  | 99.4085 |  |  | 67.2403 |  |  | 53.4363 |  |  | 48.1389 |  |  | 42.1379 |  |  | 60.0233
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 71.3403 | 13020.191 |  | 128.5542 | 20038.3882 |  | 18000 | 49066.6521 |  | 18000 | 95569.3143 |  | 18000 | 160335.5799 |  | 18000 | 234014.1457 |  | 18000 | 309200.7769 |  | 18000 | 381056.5454 |  | 18000 | 442394.8194 |  | 18000 | 518742.7179
[13 empty] | Next iteration flow rate |  |  | 13280.5948 | Abs Value of | Flow this | 20238.7721 | Abs Value of | Flow this | 49557.3187 | Abs Value of | Flow this | 96525.0075 | Abs Value of | Flow this | 161938.9357 | Abs Value of | Flow this | 236354.2872 | Abs Value of | Flow this | 312292.7846 | Abs Value of | Flow this | 384867.1108 | Abs Value of | Flow this | 446818.7676 | Abs Value of | Flow this | 523930.1451 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 84.6612 |  |  | 77.297 |  |  | 12.6852 |  |  | -203.9531 |  |  | -737.7897 |  |  | -1673.6342 |  |  | -2989.1416 |  |  | -4586.6885 |  |  | -6213.5497 |  |  | -8577.0931
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.40838 |  |  | 0.37286 |  |  | 0.06119 |  |  | -0.98382 |  |  | -3.5589 |  |  | -8.0732 |  |  | -14.4189 |  |  | -22.125 |  |  | -29.9726 |  |  | -41.3738
[13 empty] | Delta P at this iteration flow rate |  |  | 24.6612 |  |  | 17.297 |  |  | -47.3148 |  |  | -263.9531 |  |  | -797.7897 |  |  | -1733.6342 |  |  | -3049.1416 |  |  | -4646.6885 |  |  | -6273.5497 |  |  | -8637.0931
[13 empty] | Press drop ratio this iteration |  |  | 0.29129 |  |  | 0.22377 |  |  | -3.7299 |  |  | 1.2942 |  |  | 1.0813 |  |  | 1.0359 |  |  | 1.0201 |  |  | 1.0131 |  |  | 1.0097 |  |  | 1.007
[13 empty] | Expansion factor | 12 |  | 0.84829 |  |  | 0.88348 |  |  | 2.9606 |  |  | 0.31013 |  |  | 0.40572 |  |  | 0.39655 |  |  | 0.36066 |  |  | 0.29006 |  |  | 0.4301 |  |  | 0.10891
[13 empty] | C Non choked w/ reducers | 5 |  | 77.9441 |  |  | 142.6149 |  |  | #NUM! |  |  | 307.8844 |  |  | 120.8869 |  |  | 83.1354 |  |  | 70.6083 |  |  | 75.0705 |  |  | 49.4679 |  |  | 222.5605
[13 empty] | C Choked w/ reducers | 5 |  | 66.8756 |  |  | 111.684 |  |  | 1678.1763 |  |  | 205.9421 |  |  | 98.1823 |  |  | 66.5024 |  |  | 52.8751 |  |  | 47.6434 |  |  | 41.7085 |  |  | 59.4164
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 77.9441 |  |  | 142.6149 |  |  | #NUM! |  |  | 205.9421 |  |  | 98.1823 |  |  | 66.5024 |  |  | 52.8751 |  |  | 47.6434 |  |  | 41.7085 |  |  | 59.4164
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 73.2141 | 13280.5948 |  | 131.0149 | 20238.7721 |  | 18000 | 49557.3187 |  | 18000 | 96525.0075 |  | 18000 | 161938.9357 |  | 18000 | 236354.2872 |  | 18000 | 312292.7846 |  | 18000 | 384867.1108 |  | 18000 | 446818.7676 |  | 18000 | 523930.1451
[13 empty] | Next iteration flow rate |  |  | 13546.2067 | Abs Value of | Flow this | 20441.1598 | Abs Value of | Flow this | 50052.8918 | Abs Value of | Flow this | 97490.2575 | Abs Value of | Flow this | 163558.325 | Abs Value of | Flow this | 238717.8301 | Abs Value of | Flow this | 315415.7125 | Abs Value of | Flow this | 388715.7819 | Abs Value of | Flow this | 451286.9553 | Abs Value of | Flow this | 529169.4465 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 84.4362 |  |  | 77.037 |  |  | 11.1265 |  |  | -209.8661 |  |  | -754.4329 |  |  | -1709.0879 |  |  | -3051.037 |  |  | -4680.6946 |  |  | -6340.2556 |  |  | -8751.3063
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4073 |  |  | 0.37161 |  |  | 0.053672 |  |  | -1.0123 |  |  | -3.6392 |  |  | -8.2442 |  |  | -14.7174 |  |  | -22.5785 |  |  | -30.5838 |  |  | -42.2141
[13 empty] | Delta P at this iteration flow rate |  |  | 24.4362 |  |  | 17.037 |  |  | -48.8735 |  |  | -269.8661 |  |  | -814.4329 |  |  | -1769.0879 |  |  | -3111.037 |  |  | -4740.6946 |  |  | -6400.2556 |  |  | -8811.3063
[13 empty] | Press drop ratio this iteration |  |  | 0.2894 |  |  | 0.22115 |  |  | -4.3925 |  |  | 1.2859 |  |  | 1.0795 |  |  | 1.0351 |  |  | 1.0197 |  |  | 1.0128 |  |  | 1.0095 |  |  | 1.0069
[13 empty] | Expansion factor | 12 |  | 0.84928 |  |  | 0.88485 |  |  | 3.3089 |  |  | 0.31454 |  |  | 0.4067 |  |  | 0.39698 |  |  | 0.36091 |  |  | 0.29024 |  |  | 0.4302 |  |  | 0.10903
[13 empty] | C Non choked w/ reducers | 5 |  | 79.8819 |  |  | 145.1564 |  |  | #NUM! |  |  | 298.9154 |  |  | 119.2118 |  |  | 82.1647 |  |  | 69.8322 |  |  | 74.261 |  |  | 48.9564 |  |  | 220.0775
[13 empty] | C Choked w/ reducers | 5 |  | 68.3949 |  |  | 113.1815 |  |  | 1932.3957 |  |  | 202.1409 |  |  | 96.9765 |  |  | 65.7741 |  |  | 52.3205 |  |  | 47.1534 |  |  | 41.2838 |  |  | 58.816
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 79.8819 |  |  | 145.1564 |  |  | #NUM! |  |  | 202.1409 |  |  | 96.9765 |  |  | 65.7741 |  |  | 52.3205 |  |  | 47.1534 |  |  | 41.2838 |  |  | 58.816
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 75.1519 | 13546.2067 |  | 133.5564 | 20441.1598 |  | 18000 | 50052.8918 |  | 18000 | 97490.2575 |  | 18000 | 163558.325 |  | 18000 | 238717.8301 |  | 18000 | 315415.7125 |  | 18000 | 388715.7819 |  | 18000 | 451286.9553 |  | 18000 | 529169.4465
[13 empty] | Next iteration flow rate |  |  | 13817.1308 | Abs Value of | Flow this | 20645.5714 | Abs Value of | Flow this | 50553.4208 | Abs Value of | Flow this | 98465.1601 | Abs Value of | Flow this | 165193.9083 | Abs Value of | Flow this | 241105.0084 | Abs Value of | Flow this | 318569.8696 | Abs Value of | Flow this | 392602.9398 | Abs Value of | Flow this | 455799.8248 | Abs Value of | Flow this | 534461.141 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 84.2022 |  |  | 76.7718 |  |  | 9.5365 |  |  | -215.8981 |  |  | -771.4107 |  |  | -1745.2542 |  |  | -3114.1764 |  |  | -4776.5902 |  |  | -6469.5084 |  |  | -8929.0212
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.40617 |  |  | 0.37033 |  |  | 0.046002 |  |  | -1.0414 |  |  | -3.7211 |  |  | -8.4187 |  |  | -15.022 |  |  | -23.0411 |  |  | -31.2073 |  |  | -43.0714
[13 empty] | Delta P at this iteration flow rate |  |  | 24.2022 |  |  | 16.7718 |  |  | -50.4635 |  |  | -275.8981 |  |  | -831.4107 |  |  | -1805.2542 |  |  | -3174.1764 |  |  | -4836.5902 |  |  | -6529.5084 |  |  | -8989.0212
[13 empty] | Press drop ratio this iteration |  |  | 0.28743 |  |  | 0.21846 |  |  | -5.2916 |  |  | 1.2779 |  |  | 1.0778 |  |  | 1.0344 |  |  | 1.0193 |  |  | 1.0126 |  |  | 1.0093 |  |  | 1.0067
[13 empty] | Expansion factor | 12 |  | 0.8503 |  |  | 0.88625 |  |  | 3.7815 |  |  | 0.3188 |  |  | 0.40766 |  |  | 0.3974 |  |  | 0.36116 |  |  | 0.29042 |  |  | 0.43031 |  |  | 0.10915
[13 empty] | C Non choked w/ reducers | 5 |  | 81.8871 |  |  | 147.7835 |  |  | #NUM! |  |  | 290.4537 |  |  | 117.5714 |  |  | 81.2085 |  |  | 69.0662 |  |  | 73.4615 |  |  | 48.4506 |  |  | 217.628
[13 empty] | C Choked w/ reducers | 5 |  | 69.9567 |  |  | 114.7082 |  |  | 2277.121 |  |  | 198.4583 |  |  | 95.7906 |  |  | 65.0552 |  |  | 51.7723 |  |  | 46.6688 |  |  | 40.8635 |  |  | 58.2218
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 81.8871 |  |  | 147.7835 |  |  | #NUM! |  |  | 198.4583 |  |  | 95.7906 |  |  | 65.0552 |  |  | 51.7723 |  |  | 46.6688 |  |  | 40.8635 |  |  | 58.2218
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 77.1571 | 13817.1308 |  | 136.1835 | 20645.5714 |  | 18000 | 50553.4208 |  | 18000 | 98465.1601 |  | 18000 | 165193.9083 |  | 18000 | 241105.0084 |  | 18000 | 318569.8696 |  | 18000 | 392602.9398 |  | 18000 | 455799.8248 |  | 18000 | 534461.141
[13 empty] | Next iteration flow rate |  |  | 14093.4734 | Abs Value of | Flow this | 20852.0271 | Abs Value of | Flow this | 51058.955 | Abs Value of | Flow this | 99449.8117 | Abs Value of | Flow this | 166845.8473 | Abs Value of | Flow this | 243516.0584 | Abs Value of | Flow this | 321755.5683 | Abs Value of | Flow this | 396528.9692 | Abs Value of | Flow this | 460357.8231 | Abs Value of | Flow this | 539805.7524 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 83.9586 |  |  | 76.5013 |  |  | 7.9146 |  |  | -222.0512 |  |  | -788.7297 |  |  | -1782.1474 |  |  | -3178.585 |  |  | -4874.4133 |  |  | -6601.3591 |  |  | -9110.3082
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.405 |  |  | 0.36902 |  |  | 0.038178 |  |  | -1.0711 |  |  | -3.8046 |  |  | -8.5966 |  |  | -15.3327 |  |  | -23.513 |  |  | -31.8433 |  |  | -43.9458
[13 empty] | Delta P at this iteration flow rate |  |  | 23.9586 |  |  | 16.5013 |  |  | -52.0854 |  |  | -282.0512 |  |  | -848.7297 |  |  | -1842.1474 |  |  | -3238.585 |  |  | -4934.4133 |  |  | -6661.3591 |  |  | -9170.3082
[13 empty] | Press drop ratio this iteration |  |  | 0.28536 |  |  | 0.2157 |  |  | -6.5809 |  |  | 1.2702 |  |  | 1.0761 |  |  | 1.0337 |  |  | 1.0189 |  |  | 1.0123 |  |  | 1.0091 |  |  | 1.0066
[13 empty] | Expansion factor | 12 |  | 0.85138 |  |  | 0.88769 |  |  | 4.4592 |  |  | 0.32291 |  |  | 0.4086 |  |  | 0.39782 |  |  | 0.36141 |  |  | 0.2906 |  |  | 0.43042 |  |  | 0.10927
[13 empty] | C Non choked w/ reducers | 5 |  | 83.9636 |  |  | 150.5012 |  |  | #NUM! |  |  | 282.4554 |  |  | 115.9648 |  |  | 80.2666 |  |  | 68.3102 |  |  | 72.6719 |  |  | 47.9505 |  |  | 215.2113
[13 empty] | C Choked w/ reducers | 5 |  | 71.5628 |  |  | 116.2649 |  |  | 2771.2104 |  |  | 194.8885 |  |  | 94.6241 |  |  | 64.3455 |  |  | 51.2304 |  |  | 46.1896 |  |  | 40.4478 |  |  | 57.6339
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 83.9636 |  |  | 150.5012 |  |  | #NUM! |  |  | 194.8885 |  |  | 94.6241 |  |  | 64.3455 |  |  | 51.2304 |  |  | 46.1896 |  |  | 40.4478 |  |  | 57.6339
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 79.2336 | 14093.4734 |  | 138.9012 | 20852.0271 |  | 18000 | 51058.955 |  | 18000 | 99449.8117 |  | 18000 | 166845.8473 |  | 18000 | 243516.0584 |  | 18000 | 321755.5683 |  | 18000 | 396528.9692 |  | 18000 | 460357.8231 |  | 18000 | 539805.7524
[13 empty] | Next iteration flow rate |  |  | 14375.3429 | Abs Value of | Flow this | 21060.5474 | Abs Value of | Flow this | 51569.5445 | Abs Value of | Flow this | 100444.3098 | Abs Value of | Flow this | 168514.3058 | Abs Value of | Flow this | 245951.219 | Abs Value of | Flow this | 324973.124 | Abs Value of | Flow this | 400494.2588 | Abs Value of | Flow this | 464961.4013 | Abs Value of | Flow this | 545203.8099 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 83.7053 |  |  | 76.2254 |  |  | 6.2601 |  |  | -228.3281 |  |  | -806.3967 |  |  | -1819.7822 |  |  | -3244.2882 |  |  | -4974.2026 |  |  | -6735.8601 |  |  | -9295.239
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.40377 |  |  | 0.36769 |  |  | 0.030197 |  |  | -1.1014 |  |  | -3.8899 |  |  | -8.7782 |  |  | -15.6496 |  |  | -23.9943 |  |  | -32.4921 |  |  | -44.8379
[13 empty] | Delta P at this iteration flow rate |  |  | 23.7053 |  |  | 16.2254 |  |  | -53.7399 |  |  | -288.3281 |  |  | -866.3967 |  |  | -1879.7822 |  |  | -3304.2882 |  |  | -5034.2026 |  |  | -6795.8601 |  |  | -9355.239
[13 empty] | Press drop ratio this iteration |  |  | 0.2832 |  |  | 0.21286 |  |  | -8.5846 |  |  | 1.2628 |  |  | 1.0744 |  |  | 1.033 |  |  | 1.0185 |  |  | 1.0121 |  |  | 1.0089 |  |  | 1.0065
[13 empty] | Expansion factor | 12 |  | 0.85251 |  |  | 0.88917 |  |  | 5.5125 |  |  | 0.32687 |  |  | 0.40952 |  |  | 0.39822 |  |  | 0.36165 |  |  | 0.29077 |  |  | 0.43052 |  |  | 0.10939
[13 empty] | C Non choked w/ reducers | 5 |  | 86.1156 |  |  | 153.3153 |  |  | #NUM! |  |  | 274.8815 |  |  | 114.3908 |  |  | 79.3385 |  |  | 67.564 |  |  | 71.8921 |  |  | 47.4559 |  |  | 212.827
[13 empty] | C Choked w/ reducers | 5 |  | 73.215 |  |  | 117.8527 |  |  | 3538.6829 |  |  | 191.4262 |  |  | 93.4765 |  |  | 63.6449 |  |  | 50.6948 |  |  | 45.7156 |  |  | 40.0366 |  |  | 57.0521
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 86.1156 |  |  | 153.3153 |  |  | #NUM! |  |  | 191.4262 |  |  | 93.4765 |  |  | 63.6449 |  |  | 50.6948 |  |  | 45.7156 |  |  | 40.0366 |  |  | 57.0521
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 81.3856 | 14375.3429 |  | 141.7153 | 21060.5474 |  | 18000 | 51569.5445 |  | 18000 | 100444.3098 |  | 18000 | 168514.3058 |  | 18000 | 245951.219 |  | 18000 | 324973.124 |  | 18000 | 400494.2588 |  | 18000 | 464961.4013 |  | 18000 | 545203.8099
[13 empty] | Next iteration flow rate |  |  | 14662.8498 | Abs Value of | Flow this | 21271.1529 | Abs Value of | Flow this | 52085.24 | Abs Value of | Flow this | 101448.7529 | Abs Value of | Flow this | 170199.4489 | Abs Value of | Flow this | 248410.7312 | Abs Value of | Flow this | 328222.8552 | Abs Value of | Flow this | 404499.2014 | Abs Value of | Flow this | 469611.0153 | Abs Value of | Flow this | 550655.848 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 83.4417 |  |  | 75.9439 |  |  | 4.5723 |  |  | -234.7311 |  |  | -824.4189 |  |  | -1858.1735 |  |  | -3311.312 |  |  | -5075.9977 |  |  | -6873.0645 |  |  | -9483.8869
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.4025 |  |  | 0.36633 |  |  | 0.022055 |  |  | -1.1323 |  |  | -3.9768 |  |  | -8.9634 |  |  | -15.9729 |  |  | -24.4853 |  |  | -33.1539 |  |  | -45.7479
[13 empty] | Delta P at this iteration flow rate |  |  | 23.4417 |  |  | 15.9439 |  |  | -55.4277 |  |  | -294.7311 |  |  | -884.4189 |  |  | -1918.1735 |  |  | -3371.312 |  |  | -5135.9977 |  |  | -6933.0645 |  |  | -9543.8869
[13 empty] | Press drop ratio this iteration |  |  | 0.28093 |  |  | 0.20994 |  |  | -12.1226 |  |  | 1.2556 |  |  | 1.0728 |  |  | 1.0323 |  |  | 1.0181 |  |  | 1.0118 |  |  | 1.0087 |  |  | 1.0063
[13 empty] | Expansion factor | 12 |  | 0.85369 |  |  | 0.89069 |  |  | 7.3722 |  |  | 0.33069 |  |  | 0.41041 |  |  | 0.39862 |  |  | 0.36188 |  |  | 0.29094 |  |  | 0.43062 |  |  | 0.1095
[13 empty] | C Non choked w/ reducers | 5 |  | 88.3477 |  |  | 156.2317 |  |  | #NUM! |  |  | 267.6975 |  |  | 112.8484 |  |  | 78.424 |  |  | 66.8273 |  |  | 71.122 |  |  | 46.9669 |  |  | 210.4743
[13 empty] | C Choked w/ reducers | 5 |  | 74.9153 |  |  | 119.4724 |  |  | 4893.4008 |  |  | 188.0665 |  |  | 92.3474 |  |  | 62.9533 |  |  | 50.1654 |  |  | 45.2468 |  |  | 39.6297 |  |  | 56.4764
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 88.3477 |  |  | 156.2317 |  |  | #NUM! |  |  | 188.0665 |  |  | 92.3474 |  |  | 62.9533 |  |  | 50.1654 |  |  | 45.2468 |  |  | 39.6297 |  |  | 56.4764
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 83.6177 | 14662.8498 |  | 144.6317 | 21271.1529 |  | 18000 | 52085.24 |  | 18000 | 101448.7529 |  | 18000 | 170199.4489 |  | 18000 | 248410.7312 |  | 18000 | 328222.8552 |  | 18000 | 404499.2014 |  | 18000 | 469611.0153 |  | 18000 | 550655.848
[13 empty] | Next iteration flow rate |  |  | 14956.1067 | Abs Value of | Flow this | 21483.8644 | Abs Value of | Flow this | 52606.0924 | Abs Value of | Flow this | 102463.2405 | Abs Value of | Flow this | 171901.4434 | Abs Value of | Flow this | 250894.8385 | Abs Value of | Flow this | 331505.0838 | Abs Value of | Flow this | 408544.1934 | Abs Value of | Flow this | 474307.1255 | Abs Value of | Flow this | 556162.4065 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 83.1674 |  |  | 75.6567 |  |  | 2.8505 |  |  | -241.2628 |  |  | -842.8034 |  |  | -1897.3364 |  |  | -3379.683 |  |  | -5179.8389 |  |  | -7013.0267 |  |  | -9676.3267
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.40118 |  |  | 0.36495 |  |  | 0.01375 |  |  | -1.1638 |  |  | -4.0655 |  |  | -9.1523 |  |  | -16.3027 |  |  | -24.9862 |  |  | -33.8291 |  |  | -46.6762
[13 empty] | Delta P at this iteration flow rate |  |  | 23.1674 |  |  | 15.6567 |  |  | -57.1495 |  |  | -301.2628 |  |  | -902.8034 |  |  | -1957.3364 |  |  | -3439.683 |  |  | -5239.8389 |  |  | -7073.0267 |  |  | -9736.3267
[13 empty] | Press drop ratio this iteration |  |  | 0.27856 |  |  | 0.20694 |  |  | -20.0487 |  |  | 1.2487 |  |  | 1.0712 |  |  | 1.0316 |  |  | 1.0178 |  |  | 1.0116 |  |  | 1.0086 |  |  | 1.0062
[13 empty] | Expansion factor | 12 |  | 0.85492 |  |  | 0.89225 |  |  | 11.5386 |  |  | 0.33438 |  |  | 0.41128 |  |  | 0.39901 |  |  | 0.36211 |  |  | 0.29111 |  |  | 0.43072 |  |  | 0.10961
[13 empty] | C Non choked w/ reducers | 5 |  | 90.6646 |  |  | 159.2572 |  |  | #NUM! |  |  | 260.8725 |  |  | 111.3365 |  |  | 77.5229 |  |  | 66.1001 |  |  | 70.3612 |  |  | 46.4832 |  |  | 208.1527
[13 empty] | C Choked w/ reducers | 5 |  | 76.6656 |  |  | 121.1251 |  |  | 7927.5154 |  |  | 184.8047 |  |  | 91.2363 |  |  | 62.2704 |  |  | 49.6421 |  |  | 44.7831 |  |  | 39.2272 |  |  | 55.9068
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 90.6646 |  |  | 159.2572 |  |  | #NUM! |  |  | 184.8047 |  |  | 91.2363 |  |  | 62.2704 |  |  | 49.6421 |  |  | 44.7831 |  |  | 39.2272 |  |  | 55.9068
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 85.9346 | 14956.1067 |  | 147.6572 | 21483.8644 |  | 18000 | 52606.0924 |  | 18000 | 102463.2405 |  | 18000 | 171901.4434 |  | 18000 | 250894.8385 |  | 18000 | 331505.0838 |  | 18000 | 408544.1934 |  | 18000 | 474307.1255 |  | 18000 | 556162.4065
[13 empty] | Next iteration flow rate |  |  | 15255.2289 | Abs Value of | Flow this | 21698.703 | Abs Value of | Flow this | 53132.1533 | Abs Value of | Flow this | 103487.8729 | Abs Value of | Flow this | 173620.4578 | Abs Value of | Flow this | 253403.7869 | Abs Value of | Flow this | 334820.1346 | Abs Value of | Flow this | 412629.6354 | Abs Value of | Flow this | 479050.1967 | Abs Value of | Flow this | 561724.0305 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 82.8821 |  |  | 75.3638 |  |  | 1.0942 |  |  | -247.9259 |  |  | -861.5574 |  |  | -1937.2865 |  |  | -3449.4283 |  |  | -5285.7673 |  |  | -7155.8022 |  |  | -9872.6345
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.3998 |  |  | 0.36354 |  |  | 0.0052781 |  |  | -1.1959 |  |  | -4.1559 |  |  | -9.345 |  |  | -16.6392 |  |  | -25.4972 |  |  | -34.5178 |  |  | -47.6231
[13 empty] | Delta P at this iteration flow rate |  |  | 22.8821 |  |  | 15.3638 |  |  | -58.9058 |  |  | -307.9259 |  |  | -921.5574 |  |  | -1997.2865 |  |  | -3509.4283 |  |  | -5345.7673 |  |  | -7215.8022 |  |  | -9932.6345
[13 empty] | Press drop ratio this iteration |  |  | 0.27608 |  |  | 0.20386 |  |  | -53.8348 |  |  | 1.242 |  |  | 1.0696 |  |  | 1.031 |  |  | 1.0174 |  |  | 1.0114 |  |  | 1.0084 |  |  | 1.0061
[13 empty] | Expansion factor | 12 |  | 0.85622 |  |  | 0.89385 |  |  | 29.2981 |  |  | 0.33794 |  |  | 0.41214 |  |  | 0.39939 |  |  | 0.36233 |  |  | 0.29127 |  |  | 0.43081 |  |  | 0.10972
[13 empty] | C Non choked w/ reducers | 5 |  | 93.0719 |  |  | 162.3991 |  |  | #NUM! |  |  | 254.3787 |  |  | 109.8543 |  |  | 76.6347 |  |  | 65.3821 |  |  | 69.6097 |  |  | 46.0049 |  |  | 205.8617
[13 empty] | C Choked w/ reducers | 5 |  | 78.4681 |  |  | 122.8119 |  |  | 20858.7586 |  |  | 181.6365 |  |  | 90.1429 |  |  | 61.5961 |  |  | 49.1247 |  |  | 44.3245 |  |  | 38.829 |  |  | 55.3431
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 93.0719 |  |  | 162.3991 |  |  | #NUM! |  |  | 181.6365 |  |  | 90.1429 |  |  | 61.5961 |  |  | 49.1247 |  |  | 44.3245 |  |  | 38.829 |  |  | 55.3431
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 88.3419 | 15255.2289 |  | 150.7991 | 21698.703 |  | 18000 | 53132.1533 |  | 18000 | 103487.8729 |  | 18000 | 173620.4578 |  | 18000 | 253403.7869 |  | 18000 | 334820.1346 |  | 18000 | 412629.6354 |  | 18000 | 479050.1967 |  | 18000 | 561724.0305
[13 empty] | Next iteration flow rate |  |  | 15560.3335 | Abs Value of | Flow this | 21915.6901 | Abs Value of | Flow this | 53663.4748 | Abs Value of | Flow this | 104522.7516 | Abs Value of | Flow this | 175356.6624 | Abs Value of | Flow this | 255937.8248 | Abs Value of | Flow this | 338168.336 | Abs Value of | Flow this | 416755.9317 | Abs Value of | Flow this | 483840.6987 | Abs Value of | Flow this | 567341.2709 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 82.5852 |  |  | 75.065 |  |  | -0.69744 |  |  | -254.7228 |  |  | -880.6883 |  |  | -1978.0395 |  |  | -3520.5754 |  |  | -5393.8248 |  |  | -7301.4474 |  |  | -10072.8881
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.39837 |  |  | 0.36209 |  |  | -0.0033643 |  |  | -1.2287 |  |  | -4.2482 |  |  | -9.5416 |  |  | -16.9824 |  |  | -26.0185 |  |  | -35.2204 |  |  | -48.5891
[13 empty] | Delta P at this iteration flow rate |  |  | 22.5852 |  |  | 15.065 |  |  | -60.6974 |  |  | -314.7228 |  |  | -940.6883 |  |  | -2038.0395 |  |  | -3580.5754 |  |  | -5453.8248 |  |  | -7361.4474 |  |  | -10132.8881
[13 empty] | Press drop ratio this iteration |  |  | 0.27348 |  |  | 0.20069 |  |  | 87.0293 |  |  | 1.2356 |  |  | 1.0681 |  |  | 1.0303 |  |  | 1.017 |  |  | 1.0111 |  |  | 1.0082 |  |  | 1.006
[13 empty] | Expansion factor | 12 |  | 0.85757 |  |  | 0.8955 |  |  | -44.7467 |  |  | 0.34138 |  |  | 0.41297 |  |  | 0.39976 |  |  | 0.36255 |  |  | 0.29143 |  |  | 0.43091 |  |  | 0.10983
[13 empty] | C Non choked w/ reducers | 5 |  | 95.5755 |  |  | 165.6653 |  |  | -42.0556 |  |  | 248.1914 |  |  | 108.4008 |  |  | 75.7594 |  |  | 64.6733 |  |  | 68.8674 |  |  | 45.5319 |  |  | 203.6006
[13 empty] | C Choked w/ reducers | 5 |  | 80.3251 |  |  | 124.5338 |  |  | 33052.1716 |  |  | 178.5576 |  |  | 89.0666 |  |  | 60.9303 |  |  | 48.6133 |  |  | 43.8709 |  |  | 38.435 |  |  | 54.7853
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 95.5755 |  |  | 165.6653 |  |  | 33052.1716 |  |  | 178.5576 |  |  | 89.0666 |  |  | 60.9303 |  |  | 48.6133 |  |  | 43.8709 |  |  | 38.435 |  |  | 54.7853
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 90.8455 | 15560.3335 |  | 154.0653 | 21915.6901 |  | 18000 | 53663.4748 |  | 18000 | 104522.7516 |  | 18000 | 175356.6624 |  | 18000 | 255937.8248 |  | 18000 | 338168.336 |  | 18000 | 416755.9317 |  | 18000 | 483840.6987 |  | 18000 | 567341.2709
[13 empty] | Next iteration flow rate |  |  | 15871.5401 | Abs Value of | Flow this | 22134.847 | Abs Value of | Flow this | 54200.1096 | Abs Value of | Flow this | 105567.9791 | Abs Value of | Flow this | 177110.229 | Abs Value of | Flow this | 258497.203 | Abs Value of | Flow this | 341550.0193 | Abs Value of | Flow this | 420923.4911 | Abs Value of | Flow this | 488679.1057 | Abs Value of | Flow this | 573014.6836 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 82.2763 |  |  | 74.7601 |  |  | -2.5251 |  |  | -261.6563 |  |  | -900.2038 |  |  | -2019.6118 |  |  | -3593.1526 |  |  | -5504.0544 |  |  | -7450.0202 |  |  | -10277.1667
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.39688 |  |  | 0.36062 |  |  | -0.01218 |  |  | -1.2622 |  |  | -4.3424 |  |  | -9.7421 |  |  | -17.3325 |  |  | -26.5502 |  |  | -35.937 |  |  | -49.5745
[13 empty] | Delta P at this iteration flow rate |  |  | 22.2763 |  |  | 14.7601 |  |  | -62.5251 |  |  | -321.6563 |  |  | -960.2038 |  |  | -2079.6118 |  |  | -3653.1526 |  |  | -5564.0544 |  |  | -7510.0202 |  |  | -10337.1667
[13 empty] | Press drop ratio this iteration |  |  | 0.27075 |  |  | 0.19743 |  |  | 24.7616 |  |  | 1.2293 |  |  | 1.0667 |  |  | 1.0297 |  |  | 1.0167 |  |  | 1.0109 |  |  | 1.0081 |  |  | 1.0058
[13 empty] | Expansion factor | 12 |  | 0.85899 |  |  | 0.8972 |  |  | -12.0159 |  |  | 0.34471 |  |  | 0.41378 |  |  | 0.40012 |  |  | 0.36277 |  |  | 0.29159 |  |  | 0.431 |  |  | 0.10993
[13 empty] | C Non choked w/ reducers | 5 |  | 98.182 |  |  | 169.0648 |  |  | -81.9076 |  |  | 242.2881 |  |  | 106.9752 |  |  | 74.8965 |  |  | 63.9734 |  |  | 68.1341 |  |  | 45.0641 |  |  | 201.3689
[13 empty] | C Choked w/ reducers | 5 |  | 82.2392 |  |  | 126.2919 |  |  | 9220.4239 |  |  | 175.5644 |  |  | 88.007 |  |  | 60.2729 |  |  | 48.1077 |  |  | 43.4222 |  |  | 38.0452 |  |  | 54.2333
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 98.182 |  |  | 169.0648 |  |  | 9220.4239 |  |  | 175.5644 |  |  | 88.007 |  |  | 60.2729 |  |  | 48.1077 |  |  | 43.4222 |  |  | 38.0452 |  |  | 54.2333
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 93.452 | 15871.5401 |  | 157.4648 | 22134.847 |  | 18000 | 54200.1096 |  | 18000 | 105567.9791 |  | 18000 | 177110.229 |  | 18000 | 258497.203 |  | 18000 | 341550.0193 |  | 18000 | 420923.4911 |  | 18000 | 488679.1057 |  | 18000 | 573014.6836
[13 empty] | Next iteration flow rate |  |  | 16188.9709 | Abs Value of | Flow this | 22356.1955 | Abs Value of | Flow this | 54742.1107 | Abs Value of | Flow this | 106623.6589 | Abs Value of | Flow this | 178881.3313 | Abs Value of | Flow this | 261082.1751 | Abs Value of | Flow this | 344965.5195 | Abs Value of | Flow this | 425132.726 | Abs Value of | Flow this | 493565.8968 | Abs Value of | Flow this | 578744.8304 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 81.955 |  |  | 74.4492 |  |  | -4.3895 |  |  | -268.7293 |  |  | -920.1115 |  |  | -2062.0196 |  |  | -3667.1886 |  |  | -5616.4995 |  |  | -7601.5792 |  |  | -10485.5514
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.39533 |  |  | 0.35912 |  |  | -0.021174 |  |  | -1.2963 |  |  | -4.4384 |  |  | -9.9467 |  |  | -17.6896 |  |  | -27.0926 |  |  | -36.6681 |  |  | -50.5797
[13 empty] | Delta P at this iteration flow rate |  |  | 21.955 |  |  | 14.4492 |  |  | -64.3895 |  |  | -328.7293 |  |  | -980.1115 |  |  | -2122.0196 |  |  | -3727.1886 |  |  | -5676.4995 |  |  | -7661.5792 |  |  | -10545.5514
[13 empty] | Press drop ratio this iteration |  |  | 0.26789 |  |  | 0.19408 |  |  | 14.6691 |  |  | 1.2233 |  |  | 1.0652 |  |  | 1.0291 |  |  | 1.0164 |  |  | 1.0107 |  |  | 1.0079 |  |  | 1.0057
[13 empty] | Expansion factor | 12 |  | 0.86048 |  |  | 0.89894 |  |  | -6.7108 |  |  | 0.34793 |  |  | 0.41457 |  |  | 0.40048 |  |  | 0.36298 |  |  | 0.29174 |  |  | 0.43109 |  |  | 0.11004
[13 empty] | C Non choked w/ reducers | 5 |  | 100.8985 |  |  | 172.6072 |  |  | -110.7083 |  |  | 236.6486 |  |  | 105.5765 |  |  | 74.0458 |  |  | 63.2823 |  |  | 67.4097 |  |  | 44.6015 |  |  | 199.1662
[13 empty] | C Choked w/ reducers | 5 |  | 84.2129 |  |  | 128.0876 |  |  | 5357.1819 |  |  | 172.653 |  |  | 86.9639 |  |  | 59.6237 |  |  | 47.6078 |  |  | 42.9784 |  |  | 37.6595 |  |  | 53.687
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 100.8985 |  |  | 172.6072 |  |  | 5357.1819 |  |  | 172.653 |  |  | 86.9639 |  |  | 59.6237 |  |  | 47.6078 |  |  | 42.9784 |  |  | 37.6595 |  |  | 53.687
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 96.1685 | 16188.9709 |  | 161.0072 | 22356.1955 |  | 18000 | 54742.1107 |  | 18000 | 106623.6589 |  | 18000 | 178881.3313 |  | 18000 | 261082.1751 |  | 18000 | 344965.5195 |  | 18000 | 425132.726 |  | 18000 | 493565.8968 |  | 18000 | 578744.8304
[13 empty] | Next iteration flow rate |  |  | 16512.7504 | Abs Value of | Flow this | 22579.7574 | Abs Value of | Flow this | 55289.5318 | Abs Value of | Flow this | 107689.8955 | Abs Value of | Flow this | 180670.1446 | Abs Value of | Flow this | 263692.9968 | Abs Value of | Flow this | 348415.1747 | Abs Value of | Flow this | 429384.0532 | Abs Value of | Flow this | 498501.5557 | Abs Value of | Flow this | 584532.2787 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 81.6207 |  |  | 74.132 |  |  | -6.2913 |  |  | -275.9444 |  |  | -940.4193 |  |  | -2105.2798 |  |  | -3742.7127 |  |  | -5731.2047 |  |  | -7756.1846 |  |  | -10698.1246
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.39372 |  |  | 0.35759 |  |  | -0.030348 |  |  | -1.3311 |  |  | -4.5363 |  |  | -10.1553 |  |  | -18.0539 |  |  | -27.6459 |  |  | -37.4139 |  |  | -51.6051
[13 empty] | Delta P at this iteration flow rate |  |  | 21.6207 |  |  | 14.132 |  |  | -66.2913 |  |  | -335.9444 |  |  | -1000.4193 |  |  | -2165.2798 |  |  | -3802.7127 |  |  | -5791.2047 |  |  | -7816.1846 |  |  | -10758.1246
[13 empty] | Press drop ratio this iteration |  |  | 0.26489 |  |  | 0.19063 |  |  | 10.537 |  |  | 1.2174 |  |  | 1.0638 |  |  | 1.0285 |  |  | 1.016 |  |  | 1.0105 |  |  | 1.0077 |  |  | 1.0056
[13 empty] | Expansion factor | 12 |  | 0.86204 |  |  | 0.90074 |  |  | -4.5387 |  |  | 0.35104 |  |  | 0.41535 |  |  | 0.40083 |  |  | 0.36319 |  |  | 0.29189 |  |  | 0.43118 |  |  | 0.11014
[13 empty] | C Non choked w/ reducers | 5 |  | 103.733 |  |  | 176.3035 |  |  | -136.0989 |  |  | 231.2546 |  |  | 104.2041 |  |  | 73.2072 |  |  | 62.5999 |  |  | 66.6939 |  |  | 44.1439 |  |  | 196.9918
[13 empty] | C Choked w/ reducers | 5 |  | 86.249 |  |  | 129.922 |  |  | 3775.0919 |  |  | 169.82 |  |  | 85.9369 |  |  | 58.9825 |  |  | 47.1136 |  |  | 42.5394 |  |  | 37.2779 |  |  | 53.1465
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 103.733 |  |  | 176.3035 |  |  | 3775.0919 |  |  | 169.82 |  |  | 85.9369 |  |  | 58.9825 |  |  | 47.1136 |  |  | 42.5394 |  |  | 37.2779 |  |  | 53.1465
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 99.003 | 16512.7504 |  | 164.7035 | 22579.7574 |  | 18000 | 55289.5318 |  | 18000 | 107689.8955 |  | 18000 | 180670.1446 |  | 18000 | 263692.9968 |  | 18000 | 348415.1747 |  | 18000 | 429384.0532 |  | 18000 | 498501.5557 |  | 18000 | 584532.2787
[13 empty] | Next iteration flow rate |  |  | 16843.0054 | Abs Value of | Flow this | 22805.555 | Abs Value of | Flow this | 55842.4271 | Abs Value of | Flow this | 108766.7944 | Abs Value of | Flow this | 182476.8461 | Abs Value of | Flow this | 266329.9268 | Abs Value of | Flow this | 351899.3265 | Abs Value of | Flow this | 433677.8938 | Abs Value of | Flow this | 503486.5713 | Abs Value of | Flow this | 590377.6015 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 81.2729 |  |  | 73.8084 |  |  | -8.2314 |  |  | -283.3045 |  |  | -961.1354 |  |  | -2149.4096 |  |  | -3819.7549 |  |  | -5848.2156 |  |  | -7913.8975 |  |  | -10914.9706
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.39204 |  |  | 0.35603 |  |  | -0.039706 |  |  | -1.3666 |  |  | -4.6363 |  |  | -10.3682 |  |  | -18.4255 |  |  | -28.2103 |  |  | -38.1747 |  |  | -52.6511
[13 empty] | Delta P at this iteration flow rate |  |  | 21.2729 |  |  | 13.8084 |  |  | -68.2314 |  |  | -343.3045 |  |  | -1021.1354 |  |  | -2209.4096 |  |  | -3879.7549 |  |  | -5908.2156 |  |  | -7973.8975 |  |  | -10974.9706
[13 empty] | Press drop ratio this iteration |  |  | 0.26175 |  |  | 0.18708 |  |  | 8.2892 |  |  | 1.2118 |  |  | 1.0624 |  |  | 1.0279 |  |  | 1.0157 |  |  | 1.0103 |  |  | 1.0076 |  |  | 1.0055
[13 empty] | Expansion factor | 12 |  | 0.86368 |  |  | 0.90259 |  |  | -3.3572 |  |  | 0.35405 |  |  | 0.4161 |  |  | 0.40117 |  |  | 0.36339 |  |  | 0.29204 |  |  | 0.43127 |  |  | 0.11023
[13 empty] | C Non choked w/ reducers | 5 |  | 106.6944 |  |  | 180.1657 |  |  | -160.1421 |  |  | 226.0895 |  |  | 102.8572 |  |  | 72.3802 |  |  | 61.926 |  |  | 65.9868 |  |  | 43.6913 |  |  | 194.8454
[13 empty] | C Choked w/ reducers | 5 |  | 88.3505 |  |  | 131.7965 |  |  | 2914.183 |  |  | 167.0622 |  |  | 84.9254 |  |  | 58.3492 |  |  | 46.625 |  |  | 42.1051 |  |  | 36.9004 |  |  | 52.6115
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 106.6944 |  |  | 180.1657 |  |  | 2914.183 |  |  | 167.0622 |  |  | 84.9254 |  |  | 58.3492 |  |  | 46.625 |  |  | 42.1051 |  |  | 36.9004 |  |  | 52.6115
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 101.9644 | 16843.0054 |  | 168.5657 | 22805.555 |  | 18000 | 55842.4271 |  | 18000 | 108766.7944 |  | 18000 | 182476.8461 |  | 18000 | 266329.9268 |  | 18000 | 351899.3265 |  | 18000 | 433677.8938 |  | 18000 | 503486.5713 |  | 18000 | 590377.6015
[13 empty] | Next iteration flow rate |  |  | 17179.8655 | Abs Value of | Flow this | 23033.6105 | Abs Value of | Flow this | 56400.8514 | Abs Value of | Flow this | 109854.4624 | Abs Value of | Flow this | 184301.6145 | Abs Value of | Flow this | 268993.226 | Abs Value of | Flow this | 355418.3197 | Abs Value of | Flow this | 438014.6727 | Abs Value of | Flow this | 508521.437 | Abs Value of | Flow this | 596281.3775 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 80.911 |  |  | 73.4783 |  |  | -10.2105 |  |  | -290.8125 |  |  | -982.2679 |  |  | -2194.4263 |  |  | -3898.3456 |  |  | -5967.5783 |  |  | -8074.7805 |  |  | -11136.1751
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.39029 |  |  | 0.35444 |  |  | -0.049253 |  |  | -1.4028 |  |  | -4.7382 |  |  | -10.5854 |  |  | -18.8046 |  |  | -28.7861 |  |  | -38.9507 |  |  | -53.7181
[13 empty] | Delta P at this iteration flow rate |  |  | 20.911 |  |  | 13.4783 |  |  | -70.2105 |  |  | -350.8125 |  |  | -1042.2679 |  |  | -2254.4263 |  |  | -3958.3456 |  |  | -6027.5783 |  |  | -8134.7805 |  |  | -11196.1751
[13 empty] | Press drop ratio this iteration |  |  | 0.25844 |  |  | 0.18343 |  |  | 6.8763 |  |  | 1.2063 |  |  | 1.0611 |  |  | 1.0273 |  |  | 1.0154 |  |  | 1.0101 |  |  | 1.0074 |  |  | 1.0054
[13 empty] | Expansion factor | 12 |  | 0.8654 |  |  | 0.90449 |  |  | -2.6145 |  |  | 0.35696 |  |  | 0.41684 |  |  | 0.4015 |  |  | 0.36359 |  |  | 0.29218 |  |  | 0.43135 |  |  | 0.11033
[13 empty] | C Non choked w/ reducers | 5 |  | 109.7925 |  |  | 184.2071 |  |  | -183.8291 |  |  | 221.1381 |  |  | 101.535 |  |  | 71.5648 |  |  | 61.2604 |  |  | 65.2881 |  |  | 43.2437 |  |  | 192.7264
[13 empty] | C Choked w/ reducers | 5 |  | 90.5205 |  |  | 133.7125 |  |  | 2372.8257 |  |  | 164.3766 |  |  | 83.9293 |  |  | 57.7237 |  |  | 46.1419 |  |  | 41.6756 |  |  | 36.5268 |  |  | 52.0821
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 109.7925 |  |  | 184.2071 |  |  | 2372.8257 |  |  | 164.3766 |  |  | 83.9293 |  |  | 57.7237 |  |  | 46.1419 |  |  | 41.6756 |  |  | 36.5268 |  |  | 52.0821
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 105.0625 | 17179.8655 |  | 172.6071 | 23033.6105 |  | 18000 | 56400.8514 |  | 18000 | 109854.4624 |  | 18000 | 184301.6145 |  | 18000 | 268993.226 |  | 18000 | 355418.3197 |  | 18000 | 438014.6727 |  | 18000 | 508521.437 |  | 18000 | 596281.3775
[13 empty] | Next iteration flow rate |  |  | 17523.4628 | Abs Value of | Flow this | 23263.9466 | Abs Value of | Flow this | 56964.8599 | Abs Value of | Flow this | 110953.007 | Abs Value of | Flow this | 186144.6307 | Abs Value of | Flow this | 271683.1583 | Abs Value of | Flow this | 358972.5029 | Abs Value of | Flow this | 442394.8194 | Abs Value of | Flow this | 513606.6514 | Abs Value of | Flow this | 602244.1913 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 80.5345 |  |  | 73.1416 |  |  | -12.2293 |  |  | -298.4715 |  |  | -1003.8251 |  |  | -2240.3479 |  |  | -3978.5159 |  |  | -6089.3403 |  |  | -8238.8972 |  |  | -11361.8258
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.38848 |  |  | 0.35282 |  |  | -0.058991 |  |  | -1.4398 |  |  | -4.8422 |  |  | -10.8069 |  |  | -19.1914 |  |  | -29.3735 |  |  | -39.7424 |  |  | -54.8066
[13 empty] | Delta P at this iteration flow rate |  |  | 20.5345 |  |  | 13.1416 |  |  | -72.2293 |  |  | -358.4715 |  |  | -1063.8251 |  |  | -2300.3479 |  |  | -4038.5159 |  |  | -6149.3403 |  |  | -8298.8972 |  |  | -11421.8258
[13 empty] | Press drop ratio this iteration |  |  | 0.25498 |  |  | 0.17967 |  |  | 5.9062 |  |  | 1.201 |  |  | 1.0598 |  |  | 1.0268 |  |  | 1.0151 |  |  | 1.0099 |  |  | 1.0073 |  |  | 1.0053
[13 empty] | Expansion factor | 12 |  | 0.86721 |  |  | 0.90645 |  |  | -2.1046 |  |  | 0.35979 |  |  | 0.41756 |  |  | 0.40183 |  |  | 0.36378 |  |  | 0.29232 |  |  | 0.43144 |  |  | 0.11043
[13 empty] | C Non choked w/ reducers | 5 |  | 113.0383 |  |  | 188.443 |  |  | -207.7897 |  |  | 216.3865 |  |  | 100.2368 |  |  | 70.7607 |  |  | 60.6031 |  |  | 64.5977 |  |  | 42.801 |  |  | 190.6343
[13 empty] | C Choked w/ reducers | 5 |  | 92.7626 |  |  | 135.6713 |  |  | 2000.9233 |  |  | 161.7602 |  |  | 82.9482 |  |  | 57.106 |  |  | 45.6642 |  |  | 41.2507 |  |  | 36.1572 |  |  | 51.5582
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 113.0383 |  |  | 188.443 |  |  | 2000.9233 |  |  | 161.7602 |  |  | 82.9482 |  |  | 57.106 |  |  | 45.6642 |  |  | 41.2507 |  |  | 36.1572 |  |  | 51.5582
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 108.3083 | 17523.4628 |  | 176.843 | 23263.9466 |  | 18000 | 56964.8599 |  | 18000 | 110953.007 |  | 18000 | 186144.6307 |  | 18000 | 271683.1583 |  | 18000 | 358972.5029 |  | 18000 | 442394.8194 |  | 18000 | 513606.6514 |  | 18000 | 602244.1913
[13 empty] | Next iteration flow rate |  |  | 17873.932 | Abs Value of | Flow this | 23496.5861 | Abs Value of | Flow this | 57534.5085 | Abs Value of | Flow this | 112062.5371 | Abs Value of | Flow this | 188006.077 | Abs Value of | Flow this | 274399.9899 | Abs Value of | Flow this | 362562.228 | Abs Value of | Flow this | 446818.7676 | Abs Value of | Flow this | 518742.7179 | Abs Value of | Flow this | 608266.6332 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 80.1428 |  |  | 72.7982 |  |  | -14.2888 |  |  | -306.2844 |  |  | -1025.8156 |  |  | -2287.1925 |  |  | -4060.2977 |  |  | -6213.5497 |  |  | -8406.3126 |  |  | -11592.0122
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.38659 |  |  | 0.35116 |  |  | -0.068925 |  |  | -1.4774 |  |  | -4.9483 |  |  | -11.0328 |  |  | -19.5859 |  |  | -29.9726 |  |  | -40.55 |  |  | -55.917
[13 empty] | Delta P at this iteration flow rate |  |  | 20.1428 |  |  | 12.7982 |  |  | -74.2888 |  |  | -366.2844 |  |  | -1085.8156 |  |  | -2347.1925 |  |  | -4120.2977 |  |  | -6273.5497 |  |  | -8466.3126 |  |  | -11652.0122
[13 empty] | Press drop ratio this iteration |  |  | 0.25134 |  |  | 0.1758 |  |  | 5.1991 |  |  | 1.1959 |  |  | 1.0585 |  |  | 1.0262 |  |  | 1.0148 |  |  | 1.0097 |  |  | 1.0071 |  |  | 1.0052
[13 empty] | Expansion factor | 12 |  | 0.8691 |  |  | 0.90846 |  |  | -1.7329 |  |  | 0.36252 |  |  | 0.41827 |  |  | 0.40215 |  |  | 0.36397 |  |  | 0.29246 |  |  | 0.43152 |  |  | 0.11052
[13 empty] | C Non choked w/ reducers | 5 |  | 116.4443 |  |  | 192.8901 |  |  | -232.51 |  |  | 211.8223 |  |  | 98.9619 |  |  | 69.9676 |  |  | 59.9539 |  |  | 63.9155 |  |  | 42.3631 |  |  | 188.5687
[13 empty] | C Choked w/ reducers | 5 |  | 95.0803 |  |  | 137.6745 |  |  | 1729.6561 |  |  | 159.2103 |  |  | 81.9818 |  |  | 56.4957 |  |  | 45.1919 |  |  | 40.8303 |  |  | 35.7915 |  |  | 51.0398
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 116.4443 |  |  | 192.8901 |  |  | 1729.6561 |  |  | 159.2103 |  |  | 81.9818 |  |  | 56.4957 |  |  | 45.1919 |  |  | 40.8303 |  |  | 35.7915 |  |  | 51.0398
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 111.7143 | 17873.932 |  | 181.2901 | 23496.5861 |  | 18000 | 57534.5085 |  | 18000 | 112062.5371 |  | 18000 | 188006.077 |  | 18000 | 274399.9899 |  | 18000 | 362562.228 |  | 18000 | 446818.7676 |  | 18000 | 518742.7179 |  | 18000 | 608266.6332
[13 empty] | Next iteration flow rate |  |  | 18231.4107 | Abs Value of | Flow this | 23731.552 | Abs Value of | Flow this | 58109.8536 | Abs Value of | Flow this | 113183.1624 | Abs Value of | Flow this | 189886.1377 | Abs Value of | Flow this | 277143.9898 | Abs Value of | Flow this | 366187.8502 | Abs Value of | Flow this | 451286.9553 | Abs Value of | Flow this | 523930.1451 | Abs Value of | Flow this | 614349.2995 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 79.7353 |  |  | 72.4478 |  |  | -16.3896 |  |  | -314.2543 |  |  | -1048.2481 |  |  | -2334.9787 |  |  | -4143.7233 |  |  | -6340.2556 |  |  | -8577.0931 |  |  | -11826.8252
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.38462 |  |  | 0.34947 |  |  | -0.079059 |  |  | -1.5159 |  |  | -5.0565 |  |  | -11.2634 |  |  | -19.9883 |  |  | -30.5838 |  |  | -41.3738 |  |  | -57.0496
[13 empty] | Delta P at this iteration flow rate |  |  | 19.7353 |  |  | 12.4478 |  |  | -76.3896 |  |  | -374.2543 |  |  | -1108.2481 |  |  | -2394.9787 |  |  | -4203.7233 |  |  | -6400.2556 |  |  | -8637.0931 |  |  | -11886.8252
[13 empty] | Press drop ratio this iteration |  |  | 0.24751 |  |  | 0.17182 |  |  | 4.6609 |  |  | 1.1909 |  |  | 1.0572 |  |  | 1.0257 |  |  | 1.0145 |  |  | 1.0095 |  |  | 1.007 |  |  | 1.0051
[13 empty] | Expansion factor | 12 |  | 0.87109 |  |  | 0.91054 |  |  | -1.45 |  |  | 0.36517 |  |  | 0.41895 |  |  | 0.40246 |  |  | 0.36416 |  |  | 0.2926 |  |  | 0.4316 |  |  | 0.11061
[13 empty] | C Non choked w/ reducers | 5 |  | 120.0242 |  |  | 197.5677 |  |  | -258.4249 |  |  | 207.4338 |  |  | 97.7098 |  |  | 69.1853 |  |  | 59.3126 |  |  | 63.2414 |  |  | 41.93 |  |  | 186.5291
[13 empty] | C Choked w/ reducers | 5 |  | 97.4776 |  |  | 139.7238 |  |  | 1523.027 |  |  | 156.7242 |  |  | 81.0296 |  |  | 55.8929 |  |  | 44.7248 |  |  | 40.4145 |  |  | 35.4296 |  |  | 50.5267
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 120.0242 |  |  | 197.5677 |  |  | 1523.027 |  |  | 156.7242 |  |  | 81.0296 |  |  | 55.8929 |  |  | 44.7248 |  |  | 40.4145 |  |  | 35.4296 |  |  | 50.5267
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 115.2942 | 18231.4107 |  | 185.9677 | 23731.552 |  | 18000 | 58109.8536 |  | 18000 | 113183.1624 |  | 18000 | 189886.1377 |  | 18000 | 277143.9898 |  | 18000 | 366187.8502 |  | 18000 | 451286.9553 |  | 18000 | 523930.1451 |  | 18000 | 614349.2995
[13 empty] | Next iteration flow rate |  |  | 18596.0389 | Abs Value of | Flow this | 23968.8675 | Abs Value of | Flow this | 58690.9521 | Abs Value of | Flow this | 114314.9941 | Abs Value of | Flow this | 191784.9991 | Abs Value of | Flow this | 279915.4297 | Abs Value of | Flow this | 369849.7287 | Abs Value of | Flow this | 455799.8248 | Abs Value of | Flow this | 529169.4465 | Abs Value of | Flow this | 620492.7925 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 79.3113 |  |  | 72.0903 |  |  | -18.5327 |  |  | -322.3844 |  |  | -1071.1315 |  |  | -2383.7254 |  |  | -4228.8258 |  |  | -6469.5084 |  |  | -8751.3063 |  |  | -12066.358
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.38258 |  |  | 0.34775 |  |  | -0.089397 |  |  | -1.5551 |  |  | -5.1669 |  |  | -11.4985 |  |  | -20.3988 |  |  | -31.2073 |  |  | -42.2141 |  |  | -58.2051
[13 empty] | Delta P at this iteration flow rate |  |  | 19.3113 |  |  | 12.0903 |  |  | -78.5327 |  |  | -382.3844 |  |  | -1131.1315 |  |  | -2443.7254 |  |  | -4288.8258 |  |  | -6529.5084 |  |  | -8811.3063 |  |  | -12126.358
[13 empty] | Press drop ratio this iteration |  |  | 0.24349 |  |  | 0.16771 |  |  | 4.2375 |  |  | 1.1861 |  |  | 1.056 |  |  | 1.0252 |  |  | 1.0142 |  |  | 1.0093 |  |  | 1.0069 |  |  | 1.005
[13 empty] | Expansion factor | 12 |  | 0.87319 |  |  | 0.91267 |  |  | -1.2274 |  |  | 0.36773 |  |  | 0.41963 |  |  | 0.40277 |  |  | 0.36434 |  |  | 0.29273 |  |  | 0.43168 |  |  | 0.1107
[13 empty] | C Non choked w/ reducers | 5 |  | 123.794 |  |  | 202.4972 |  |  | -285.9692 |  |  | 203.2104 |  |  | 96.4797 |  |  | 68.4137 |  |  | 58.6791 |  |  | 62.5752 |  |  | 41.5015 |  |  | 184.5151
[13 empty] | C Choked w/ reducers | 5 |  | 99.9586 |  |  | 141.8207 |  |  | 1360.3781 |  |  | 154.2995 |  |  | 80.0915 |  |  | 55.2974 |  |  | 44.263 |  |  | 40.0031 |  |  | 35.0716 |  |  | 50.0189
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 123.794 |  |  | 202.4972 |  |  | 1360.3781 |  |  | 154.2995 |  |  | 80.0915 |  |  | 55.2974 |  |  | 44.263 |  |  | 40.0031 |  |  | 35.0716 |  |  | 50.0189
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 119.064 | 18596.0389 |  | 190.8972 | 23968.8675 |  | 18000 | 58690.9521 |  | 18000 | 114314.9941 |  | 18000 | 191784.9991 |  | 18000 | 279915.4297 |  | 18000 | 369849.7287 |  | 18000 | 455799.8248 |  | 18000 | 529169.4465 |  | 18000 | 620492.7925
[13 empty] | Next iteration flow rate |  |  | 18967.9597 | Abs Value of | Flow this | 24208.5562 | Abs Value of | Flow this | 59277.8616 | Abs Value of | Flow this | 115458.144 | Abs Value of | Flow this | 193702.8491 | Abs Value of | Flow this | 282714.584 | Abs Value of | Flow this | 373548.226 | Abs Value of | Flow this | 460357.8231 | Abs Value of | Flow this | 534461.141 | Abs Value of | Flow this | 626697.7204 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 78.8701 |  |  | 71.7257 |  |  | -20.7188 |  |  | -330.678 |  |  | -1094.4749 |  |  | -2433.4519 |  |  | -4315.6388 |  |  | -6601.3591 |  |  | -8929.0212 |  |  | -12310.7055
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.38045 |  |  | 0.34599 |  |  | -0.099942 |  |  | -1.5951 |  |  | -5.2795 |  |  | -11.7384 |  |  | -20.8176 |  |  | -31.8433 |  |  | -43.0714 |  |  | -59.3838
[13 empty] | Delta P at this iteration flow rate |  |  | 18.8701 |  |  | 11.7257 |  |  | -80.7188 |  |  | -390.678 |  |  | -1154.4749 |  |  | -2493.4519 |  |  | -4375.6388 |  |  | -6661.3591 |  |  | -8989.0212 |  |  | -12370.7055
[13 empty] | Press drop ratio this iteration |  |  | 0.23926 |  |  | 0.16348 |  |  | 3.8959 |  |  | 1.1814 |  |  | 1.0548 |  |  | 1.0247 |  |  | 1.0139 |  |  | 1.0091 |  |  | 1.0067 |  |  | 1.0049
[13 empty] | Expansion factor | 12 |  | 0.87539 |  |  | 0.91488 |  |  | -1.0479 |  |  | 0.37022 |  |  | 0.42028 |  |  | 0.40307 |  |  | 0.36452 |  |  | 0.29286 |  |  | 0.43175 |  |  | 0.11079
[13 empty] | C Non choked w/ reducers | 5 |  | 127.7715 |  |  | 207.7035 |  |  | -315.6133 |  |  | 199.1423 |  |  | 95.2711 |  |  | 67.6525 |  |  | 58.0534 |  |  | 61.9168 |  |  | 41.0777 |  |  | 182.5262
[13 empty] | C Choked w/ reducers | 5 |  | 102.5281 |  |  | 143.9671 |  |  | 1229.0069 |  |  | 151.9339 |  |  | 79.1671 |  |  | 54.7091 |  |  | 43.8064 |  |  | 39.5962 |  |  | 34.7173 |  |  | 49.5163
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 127.7715 |  |  | 207.7035 |  |  | 1229.0069 |  |  | 151.9339 |  |  | 79.1671 |  |  | 54.7091 |  |  | 43.8064 |  |  | 39.5962 |  |  | 34.7173 |  |  | 49.5163
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 123.0415 | 18967.9597 |  | 196.1035 | 24208.5562 |  | 18000 | 59277.8616 |  | 18000 | 115458.144 |  | 18000 | 193702.8491 |  | 18000 | 282714.584 |  | 18000 | 373548.226 |  | 18000 | 460357.8231 |  | 18000 | 534461.141 |  | 18000 | 626697.7204
[13 empty] | Next iteration flow rate |  |  | 19347.3189 | Abs Value of | Flow this | 24450.6417 | Abs Value of | Flow this | 59870.6402 | Abs Value of | Flow this | 116612.7255 | Abs Value of | Flow this | 195639.8776 | Abs Value of | Flow this | 285541.7298 | Abs Value of | Flow this | 377283.7083 | Abs Value of | Flow this | 464961.4013 | Abs Value of | Flow this | 539805.7524 | Abs Value of | Flow this | 632964.6977 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 78.4112 |  |  | 71.3538 |  |  | -22.9489 |  |  | -339.1383 |  |  | -1118.2874 |  |  | -2484.1779 |  |  | -4404.1968 |  |  | -6735.8601 |  |  | -9110.3082 |  |  | -12559.9643
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.37824 |  |  | 0.34419 |  |  | -0.1107 |  |  | -1.6359 |  |  | -5.3943 |  |  | -11.9831 |  |  | -21.2447 |  |  | -32.4921 |  |  | -43.9458 |  |  | -60.5861
[13 empty] | Delta P at this iteration flow rate |  |  | 18.4112 |  |  | 11.3538 |  |  | -82.9489 |  |  | -399.1383 |  |  | -1178.2874 |  |  | -2544.1779 |  |  | -4464.1968 |  |  | -6795.8601 |  |  | -9170.3082 |  |  | -12619.9643
[13 empty] | Press drop ratio this iteration |  |  | 0.2348 |  |  | 0.15912 |  |  | 3.6145 |  |  | 1.1769 |  |  | 1.0537 |  |  | 1.0242 |  |  | 1.0136 |  |  | 1.0089 |  |  | 1.0066 |  |  | 1.0048
[13 empty] | Expansion factor | 12 |  | 0.87771 |  |  | 0.91715 |  |  | -0.89996 |  |  | 0.37264 |  |  | 0.42092 |  |  | 0.40336 |  |  | 0.3647 |  |  | 0.29298 |  |  | 0.43183 |  |  | 0.11087
[13 empty] | C Non choked w/ reducers | 5 |  | 131.9773 |  |  | 213.2147 |  |  | -347.897 |  |  | 195.2207 |  |  | 94.0833 |  |  | 66.9016 |  |  | 57.4353 |  |  | 61.2662 |  |  | 40.6585 |  |  | 180.5622
[13 empty] | C Choked w/ reducers | 5 |  | 105.1907 |  |  | 146.1647 |  |  | 1120.673 |  |  | 149.6251 |  |  | 78.2562 |  |  | 54.1279 |  |  | 43.3548 |  |  | 39.1936 |  |  | 34.3667 |  |  | 49.019
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 131.9773 |  |  | 213.2147 |  |  | 1120.673 |  |  | 149.6251 |  |  | 78.2562 |  |  | 54.1279 |  |  | 43.3548 |  |  | 39.1936 |  |  | 34.3667 |  |  | 49.019
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 127.2473 | 19347.3189 |  | 201.6147 | 24450.6417 |  | 18000 | 59870.6402 |  | 18000 | 116612.7255 |  | 18000 | 195639.8776 |  | 18000 | 285541.7298 |  | 18000 | 377283.7083 |  | 18000 | 464961.4013 |  | 18000 | 539805.7524 |  | 18000 | 632964.6977
[13 empty] | Next iteration flow rate |  |  | 19734.2652 | Abs Value of | Flow this | 24695.1481 | Abs Value of | Flow this | 60469.3466 | Abs Value of | Flow this | 117778.8527 | Abs Value of | Flow this | 197596.2764 | Abs Value of | Flow this | 288397.1471 | Abs Value of | Flow this | 381056.5454 | Abs Value of | Flow this | 469611.0153 | Abs Value of | Flow this | 545203.8099 | Abs Value of | Flow this | 639294.3446 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 77.9337 |  |  | 70.9744 |  |  | -25.2238 |  |  | -347.7686 |  |  | -1142.5787 |  |  | -2535.9235 |  |  | -4494.5348 |  |  | -6873.0645 |  |  | -9295.239 |  |  | -12814.2332
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.37593 |  |  | 0.34236 |  |  | -0.12167 |  |  | -1.6775 |  |  | -5.5115 |  |  | -12.2327 |  |  | -21.6805 |  |  | -33.1539 |  |  | -44.8379 |  |  | -61.8127
[13 empty] | Delta P at this iteration flow rate |  |  | 17.9337 |  |  | 10.9744 |  |  | -85.2238 |  |  | -407.7686 |  |  | -1202.5787 |  |  | -2595.9235 |  |  | -4554.5348 |  |  | -6933.0645 |  |  | -9355.239 |  |  | -12874.2332
[13 empty] | Press drop ratio this iteration |  |  | 0.23012 |  |  | 0.15462 |  |  | 3.3787 |  |  | 1.1725 |  |  | 1.0525 |  |  | 1.0237 |  |  | 1.0133 |  |  | 1.0087 |  |  | 1.0065 |  |  | 1.0047
[13 empty] | Expansion factor | 12 |  | 0.88015 |  |  | 0.91949 |  |  | -0.77601 |  |  | 0.37498 |  |  | 0.42155 |  |  | 0.40365 |  |  | 0.36487 |  |  | 0.29311 |  |  | 0.4319 |  |  | 0.11096
[13 empty] | C Non choked w/ reducers | 5 |  | 136.4348 |  |  | 219.0635 |  |  | -383.4663 |  |  | 191.4371 |  |  | 92.916 |  |  | 66.1606 |  |  | 56.8246 |  |  | 60.6232 |  |  | 40.2438 |  |  | 178.6224
[13 empty] | C Choked w/ reducers | 5 |  | 107.9519 |  |  | 148.4155 |  |  | 1029.7969 |  |  | 147.3711 |  |  | 77.3584 |  |  | 53.5536 |  |  | 42.9082 |  |  | 38.7953 |  |  | 34.0198 |  |  | 48.5268
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 136.4348 |  |  | 219.0635 |  |  | 1029.7969 |  |  | 147.3711 |  |  | 77.3584 |  |  | 53.5536 |  |  | 42.9082 |  |  | 38.7953 |  |  | 34.0198 |  |  | 48.5268
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 131.7048 | 19734.2652 |  | 207.4635 | 24695.1481 |  | 18000 | 60469.3466 |  | 18000 | 117778.8527 |  | 18000 | 197596.2764 |  | 18000 | 288397.1471 |  | 18000 | 381056.5454 |  | 18000 | 469611.0153 |  | 18000 | 545203.8099 |  | 18000 | 639294.3446
[13 empty] | Next iteration flow rate |  |  | 20128.9505 | Abs Value of | Flow this | 24942.0996 | Abs Value of | Flow this | 61074.0401 | Abs Value of | Flow this | 118956.6412 | Abs Value of | Flow this | 199572.2391 | Abs Value of | Flow this | 291281.1186 | Abs Value of | Flow this | 384867.1108 | Abs Value of | Flow this | 474307.1255 | Abs Value of | Flow this | 550655.848 | Abs Value of | Flow this | 645687.2881 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 77.4369 |  |  | 70.5873 |  |  | -27.5444 |  |  | -356.5723 |  |  | -1167.3581 |  |  | -2588.7092 |  |  | -4586.6885 |  |  | -7013.0267 |  |  | -9483.8869 |  |  | -13073.6129
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.37354 |  |  | 0.3405 |  |  | -0.13287 |  |  | -1.72 |  |  | -5.631 |  |  | -12.4873 |  |  | -22.125 |  |  | -33.8291 |  |  | -45.7479 |  |  | -63.0638
[13 empty] | Delta P at this iteration flow rate |  |  | 17.4369 |  |  | 10.5873 |  |  | -87.5444 |  |  | -416.5723 |  |  | -1227.3581 |  |  | -2648.7092 |  |  | -4646.6885 |  |  | -7073.0267 |  |  | -9543.8869 |  |  | -13133.6129
[13 empty] | Press drop ratio this iteration |  |  | 0.22518 |  |  | 0.14999 |  |  | 3.1783 |  |  | 1.1683 |  |  | 1.0514 |  |  | 1.0232 |  |  | 1.0131 |  |  | 1.0086 |  |  | 1.0063 |  |  | 1.0046
[13 empty] | Expansion factor | 12 |  | 0.88273 |  |  | 0.9219 |  |  | -0.67067 |  |  | 0.37725 |  |  | 0.42216 |  |  | 0.40393 |  |  | 0.36504 |  |  | 0.29323 |  |  | 0.43198 |  |  | 0.11104
[13 empty] | C Non choked w/ reducers | 5 |  | 141.1714 |  |  | 225.2874 |  |  | -423.1203 |  |  | 187.784 |  |  | 91.7684 |  |  | 65.4296 |  |  | 56.2213 |  |  | 59.9876 |  |  | 39.8336 |  |  | 176.7066
[13 empty] | C Choked w/ reducers | 5 |  | 110.8174 |  |  | 150.7216 |  |  | 952.4665 |  |  | 145.1699 |  |  | 76.4734 |  |  | 52.9863 |  |  | 42.4666 |  |  | 38.4013 |  |  | 33.6765 |  |  | 48.0397
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 141.1714 |  |  | 225.2874 |  |  | 952.4665 |  |  | 145.1699 |  |  | 76.4734 |  |  | 52.9863 |  |  | 42.4666 |  |  | 38.4013 |  |  | 33.6765 |  |  | 48.0397
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 136.4414 | 20128.9505 |  | 213.6874 | 24942.0996 |  | 18000 | 61074.0401 |  | 18000 | 118956.6412 |  | 18000 | 199572.2391 |  | 18000 | 291281.1186 |  | 18000 | 384867.1108 |  | 18000 | 474307.1255 |  | 18000 | 550655.848 |  | 18000 | 645687.2881
[13 empty] | Next iteration flow rate |  |  | 20531.5295 | Abs Value of | Flow this | 25191.5206 | Abs Value of | Flow this | 61684.7805 | Abs Value of | Flow this | 120146.2076 | Abs Value of | Flow this | 201567.9615 | Abs Value of | Flow this | 294193.9298 | Abs Value of | Flow this | 388715.7819 | Abs Value of | Flow this | 479050.1967 | Abs Value of | Flow this | 556162.4065 | Abs Value of | Flow this | 652144.161 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 76.9201 |  |  | 70.1925 |  |  | -29.9117 |  |  | -365.5531 |  |  | -1192.6356 |  |  | -2642.5559 |  |  | -4680.6946 |  |  | -7155.8022 |  |  | -9676.3267 |  |  | -13338.2061
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.37104 |  |  | 0.33859 |  |  | -0.14429 |  |  | -1.7633 |  |  | -5.753 |  |  | -12.747 |  |  | -22.5785 |  |  | -34.5178 |  |  | -46.6762 |  |  | -64.3402
[13 empty] | Delta P at this iteration flow rate |  |  | 16.9201 |  |  | 10.1925 |  |  | -89.9117 |  |  | -425.5531 |  |  | -1252.6356 |  |  | -2702.5559 |  |  | -4740.6946 |  |  | -7215.8022 |  |  | -9736.3267 |  |  | -13398.2061
[13 empty] | Press drop ratio this iteration |  |  | 0.21997 |  |  | 0.14521 |  |  | 3.0059 |  |  | 1.1641 |  |  | 1.0503 |  |  | 1.0227 |  |  | 1.0128 |  |  | 1.0084 |  |  | 1.0062 |  |  | 1.0045
[13 empty] | Expansion factor | 12 |  | 0.88544 |  |  | 0.92439 |  |  | -0.58005 |  |  | 0.37945 |  |  | 0.42276 |  |  | 0.4042 |  |  | 0.3652 |  |  | 0.29335 |  |  | 0.43205 |  |  | 0.11112
[13 empty] | C Non choked w/ reducers | 5 |  | 146.2186 |  |  | 231.9304 |  |  | -467.8761 |  |  | 184.2542 |  |  | 90.6401 |  |  | 64.7082 |  |  | 55.6252 |  |  | 59.3594 |  |  | 39.4278 |  |  | 174.8143
[13 empty] | C Choked w/ reducers | 5 |  | 113.7932 |  |  | 153.0851 |  |  | 885.8573 |  |  | 143.0194 |  |  | 75.6011 |  |  | 52.4256 |  |  | 42.0298 |  |  | 38.0114 |  |  | 33.3368 |  |  | 47.5576
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 146.2186 |  |  | 231.9304 |  |  | 885.8573 |  |  | 143.0194 |  |  | 75.6011 |  |  | 52.4256 |  |  | 42.0298 |  |  | 38.0114 |  |  | 33.3368 |  |  | 47.5576
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 141.4886 | 20531.5295 |  | 220.3304 | 25191.5206 |  | 18000 | 61684.7805 |  | 18000 | 120146.2076 |  | 18000 | 201567.9615 |  | 18000 | 294193.9298 |  | 18000 | 388715.7819 |  | 18000 | 479050.1967 |  | 18000 | 556162.4065 |  | 18000 | 652144.161
[13 empty] | Next iteration flow rate |  |  | 20942.1601 | Abs Value of | Flow this | 25443.4358 | Abs Value of | Flow this | 62301.6283 | Abs Value of | Flow this | 121347.6697 | Abs Value of | Flow this | 203583.6411 | Abs Value of | Flow this | 297135.8691 | Abs Value of | Flow this | 392602.9398 | Abs Value of | Flow this | 483840.6987 | Abs Value of | Flow this | 561724.0305 | Abs Value of | Flow this | 658665.6026 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 76.3824 |  |  | 69.7898 |  |  | -32.3265 |  |  | -374.7143 |  |  | -1218.4212 |  |  | -2697.4849 |  |  | -4776.5902 |  |  | -7301.4474 |  |  | -9872.6345 |  |  | -13608.1177
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.36845 |  |  | 0.33665 |  |  | -0.15594 |  |  | -1.8075 |  |  | -5.8774 |  |  | -13.012 |  |  | -23.0411 |  |  | -35.2204 |  |  | -47.6231 |  |  | -65.6422
[13 empty] | Delta P at this iteration flow rate |  |  | 16.3824 |  |  | 9.7898 |  |  | -92.3265 |  |  | -434.7143 |  |  | -1278.4212 |  |  | -2757.4849 |  |  | -4836.5902 |  |  | -7361.4474 |  |  | -9932.6345 |  |  | -13668.1177
[13 empty] | Press drop ratio this iteration |  |  | 0.21448 |  |  | 0.14028 |  |  | 2.8561 |  |  | 1.1601 |  |  | 1.0492 |  |  | 1.0222 |  |  | 1.0126 |  |  | 1.0082 |  |  | 1.0061 |  |  | 1.0044
[13 empty] | Expansion factor | 12 |  | 0.8883 |  |  | 0.92696 |  |  | -0.50128 |  |  | 0.38159 |  |  | 0.42335 |  |  | 0.40447 |  |  | 0.36536 |  |  | 0.29347 |  |  | 0.43212 |  |  | 0.1112
[13 empty] | C Non choked w/ reducers | 5 |  | 151.6138 |  |  | 239.0442 |  |  | -519.0623 |  |  | 180.8412 |  |  | 89.5306 |  |  | 63.9962 |  |  | 55.0362 |  |  | 58.7385 |  |  | 39.0264 |  |  | 172.9452
[13 empty] | C Choked w/ reducers | 5 |  | 116.8862 |  |  | 155.5082 |  |  | 827.8789 |  |  | 140.918 |  |  | 74.7412 |  |  | 51.8717 |  |  | 41.5979 |  |  | 37.6257 |  |  | 33.0007 |  |  | 47.0804
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 151.6138 |  |  | 239.0442 |  |  | 827.8789 |  |  | 140.918 |  |  | 74.7412 |  |  | 51.8717 |  |  | 41.5979 |  |  | 37.6257 |  |  | 33.0007 |  |  | 47.0804
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 146.8838 | 20942.1601 |  | 227.4442 | 25443.4358 |  | 18000 | 62301.6283 |  | 18000 | 121347.6697 |  | 18000 | 203583.6411 |  | 18000 | 297135.8691 |  | 18000 | 392602.9398 |  | 18000 | 483840.6987 |  | 18000 | 561724.0305 |  | 18000 | 658665.6026
[13 empty] | Next iteration flow rate |  |  | 21361.0033 | Abs Value of | Flow this | 25697.8702 | Abs Value of | Flow this | 62924.6446 | Abs Value of | Flow this | 122561.1464 | Abs Value of | Flow this | 205619.4776 | Abs Value of | Flow this | 300107.2278 | Abs Value of | Flow this | 396528.9692 | Abs Value of | Flow this | 488679.1057 | Abs Value of | Flow this | 567341.2709 | Abs Value of | Flow this | 665252.2586 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 75.8229 |  |  | 69.3789 |  |  | -34.7899 |  |  | -384.0597 |  |  | -1244.7251 |  |  | -2753.518 |  |  | -4874.4133 |  |  | -7450.0202 |  |  | -10072.8881 |  |  | -13883.4545
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.36575 |  |  | 0.33467 |  |  | -0.16782 |  |  | -1.8526 |  |  | -6.0042 |  |  | -13.2823 |  |  | -23.513 |  |  | -35.937 |  |  | -48.5891 |  |  | -66.9703
[13 empty] | Delta P at this iteration flow rate |  |  | 15.8229 |  |  | 9.3789 |  |  | -94.7899 |  |  | -444.0597 |  |  | -1304.7251 |  |  | -2813.518 |  |  | -4934.4133 |  |  | -7510.0202 |  |  | -10132.8881 |  |  | -13943.4545
[13 empty] | Press drop ratio this iteration |  |  | 0.20868 |  |  | 0.13518 |  |  | 2.7246 |  |  | 1.1562 |  |  | 1.0482 |  |  | 1.0218 |  |  | 1.0123 |  |  | 1.0081 |  |  | 1.006 |  |  | 1.0043
[13 empty] | Expansion factor | 12 |  | 0.89132 |  |  | 0.92961 |  |  | -0.4322 |  |  | 0.38367 |  |  | 0.42392 |  |  | 0.40474 |  |  | 0.36552 |  |  | 0.29358 |  |  | 0.43218 |  |  | 0.11127
[13 empty] | C Non choked w/ reducers | 5 |  | 157.4009 |  |  | 246.6899 |  |  | -578.4604 |  |  | 177.5388 |  |  | 88.4395 |  |  | 63.2936 |  |  | 54.4543 |  |  | 58.1248 |  |  | 38.6292 |  |  | 171.0989
[13 empty] | C Choked w/ reducers | 5 |  | 120.1036 |  |  | 157.9934 |  |  | 776.9514 |  |  | 138.8639 |  |  | 73.8934 |  |  | 51.3243 |  |  | 41.1707 |  |  | 37.2441 |  |  | 32.6681 |  |  | 46.6082
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 157.4009 |  |  | 246.6899 |  |  | 776.9514 |  |  | 138.8639 |  |  | 73.8934 |  |  | 51.3243 |  |  | 41.1707 |  |  | 37.2441 |  |  | 32.6681 |  |  | 46.6082
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 152.6709 | 21361.0033 |  | 235.0899 | 25697.8702 |  | 18000 | 62924.6446 |  | 18000 | 122561.1464 |  | 18000 | 205619.4776 |  | 18000 | 300107.2278 |  | 18000 | 396528.9692 |  | 18000 | 488679.1057 |  | 18000 | 567341.2709 |  | 18000 | 665252.2586
[13 empty] | Next iteration flow rate |  |  | 21788.2234 | Abs Value of | Flow this | 25954.8489 | Abs Value of | Flow this | 63553.891 | Abs Value of | Flow this | 123786.7579 | Abs Value of | Flow this | 207675.6723 | Abs Value of | Flow this | 303108.3 | Abs Value of | Flow this | 400494.2588 | Abs Value of | Flow this | 493565.8968 | Abs Value of | Flow this | 573014.6836 | Abs Value of | Flow this | 671904.7812 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 75.2409 |  |  | 68.9598 |  |  | -37.3028 |  |  | -393.5929 |  |  | -1271.5577 |  |  | -2810.6773 |  |  | -4974.2026 |  |  | -7601.5792 |  |  | -10277.1667 |  |  | -14164.3256
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.36294 |  |  | 0.33264 |  |  | -0.17994 |  |  | -1.8986 |  |  | -6.1337 |  |  | -13.558 |  |  | -23.9943 |  |  | -36.6681 |  |  | -49.5745 |  |  | -68.3252
[13 empty] | Delta P at this iteration flow rate |  |  | 15.2409 |  |  | 8.9598 |  |  | -97.3028 |  |  | -453.5929 |  |  | -1331.5577 |  |  | -2870.6773 |  |  | -5034.2026 |  |  | -7661.5792 |  |  | -10337.1667 |  |  | -14224.3256
[13 empty] | Press drop ratio this iteration |  |  | 0.20256 |  |  | 0.12993 |  |  | 2.6085 |  |  | 1.1524 |  |  | 1.0472 |  |  | 1.0213 |  |  | 1.0121 |  |  | 1.0079 |  |  | 1.0058 |  |  | 1.0042
[13 empty] | Expansion factor | 12 |  | 0.8945 |  |  | 0.93235 |  |  | -0.37113 |  |  | 0.38568 |  |  | 0.42448 |  |  | 0.405 |  |  | 0.36568 |  |  | 0.2937 |  |  | 0.43225 |  |  | 0.11135
[13 empty] | C Non choked w/ reducers | 5 |  | 163.6321 |  |  | 254.9405 |  |  | -648.5268 |  |  | 174.3415 |  |  | 87.3662 |  |  | 62.6002 |  |  | 53.8792 |  |  | 57.5181 |  |  | 38.2364 |  |  | 169.275
[13 empty] | C Choked w/ reducers | 5 |  | 123.4534 |  |  | 160.5431 |  |  | 731.8582 |  |  | 136.8555 |  |  | 73.0574 |  |  | 50.7833 |  |  | 40.7482 |  |  | 36.8666 |  |  | 32.3389 |  |  | 46.1408
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 163.6321 |  |  | 254.9405 |  |  | 731.8582 |  |  | 136.8555 |  |  | 73.0574 |  |  | 50.7833 |  |  | 40.7482 |  |  | 36.8666 |  |  | 32.3389 |  |  | 46.1408
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 158.9021 | 21788.2234 |  | 243.3405 | 25954.8489 |  | 18000 | 63553.891 |  | 18000 | 123786.7579 |  | 18000 | 207675.6723 |  | 18000 | 303108.3 |  | 18000 | 400494.2588 |  | 18000 | 493565.8968 |  | 18000 | 573014.6836 |  | 18000 | 671904.7812
[13 empty] | Next iteration flow rate |  |  | 22223.9879 | Abs Value of | Flow this | 26214.3974 | Abs Value of | Flow this | 64189.4299 | Abs Value of | Flow this | 125024.6255 | Abs Value of | Flow this | 209752.4291 | Abs Value of | Flow this | 306139.383 | Abs Value of | Flow this | 404499.2014 | Abs Value of | Flow this | 498501.5557 | Abs Value of | Flow this | 578744.8304 | Abs Value of | Flow this | 678623.829 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 74.6353 |  |  | 68.5323 |  |  | -39.8662 |  |  | -403.3178 |  |  | -1298.9297 |  |  | -2868.9856 |  |  | -5075.9977 |  |  | -7756.1846 |  |  | -10485.5514 |  |  | -14450.8421
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.36002 |  |  | 0.33058 |  |  | -0.1923 |  |  | -1.9455 |  |  | -6.2657 |  |  | -13.8393 |  |  | -24.4853 |  |  | -37.4139 |  |  | -50.5797 |  |  | -69.7072
[13 empty] | Delta P at this iteration flow rate |  |  | 14.6353 |  |  | 8.5323 |  |  | -99.8662 |  |  | -463.3178 |  |  | -1358.9297 |  |  | -2928.9856 |  |  | -5135.9977 |  |  | -7816.1846 |  |  | -10545.5514 |  |  | -14510.8421
[13 empty] | Press drop ratio this iteration |  |  | 0.19609 |  |  | 0.1245 |  |  | 2.505 |  |  | 1.1488 |  |  | 1.0462 |  |  | 1.0209 |  |  | 1.0118 |  |  | 1.0077 |  |  | 1.0057 |  |  | 1.0042
[13 empty] | Expansion factor | 12 |  | 0.89787 |  |  | 0.93517 |  |  | -0.31676 |  |  | 0.38764 |  |  | 0.42502 |  |  | 0.40525 |  |  | 0.36583 |  |  | 0.29381 |  |  | 0.43232 |  |  | 0.11142
[13 empty] | C Non choked w/ reducers | 5 |  | 170.3705 |  |  | 263.8841 |  |  | -732.7565 |  |  | 171.2439 |  |  | 86.3103 |  |  | 61.9157 |  |  | 53.311 |  |  | 56.9184 |  |  | 37.8477 |  |  | 167.4733
[13 empty] | C Choked w/ reducers | 5 |  | 126.9441 |  |  | 163.1601 |  |  | 691.6474 |  |  | 134.8912 |  |  | 72.2331 |  |  | 50.2487 |  |  | 40.3303 |  |  | 36.493 |  |  | 32.0132 |  |  | 45.6782
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 170.3705 |  |  | 263.8841 |  |  | 691.6474 |  |  | 134.8912 |  |  | 72.2331 |  |  | 50.2487 |  |  | 40.3303 |  |  | 36.493 |  |  | 32.0132 |  |  | 45.6782
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 165.6405 | 22223.9879 |  | 252.2841 | 26214.3974 |  | 18000 | 64189.4299 |  | 18000 | 125024.6255 |  | 18000 | 209752.4291 |  | 18000 | 306139.383 |  | 18000 | 404499.2014 |  | 18000 | 498501.5557 |  | 18000 | 578744.8304 |  | 18000 | 678623.829
[13 empty] | Next iteration flow rate |  |  | 22668.4676 | Abs Value of | Flow this | 26476.5413 | Abs Value of | Flow this | 64831.3242 | Abs Value of | Flow this | 126274.8717 | Abs Value of | Flow this | 211849.9533 | Abs Value of | Flow this | 309200.7769 | Abs Value of | Flow this | 408544.1934 | Abs Value of | Flow this | 503486.5713 | Abs Value of | Flow this | 584532.2787 | Abs Value of | Flow this | 685410.0673 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 74.0053 |  |  | 68.0961 |  |  | -42.4812 |  |  | -413.2381 |  |  | -1326.8518 |  |  | -2928.4658 |  |  | -5179.8389 |  |  | -7913.8975 |  |  | -10698.1246 |  |  | -14743.1177
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.35698 |  |  | 0.32848 |  |  | -0.20492 |  |  | -1.9934 |  |  | -6.4004 |  |  | -14.1262 |  |  | -24.9862 |  |  | -38.1747 |  |  | -51.6051 |  |  | -71.1171
[13 empty] | Delta P at this iteration flow rate |  |  | 14.0053 |  |  | 8.0961 |  |  | -102.4812 |  |  | -473.2381 |  |  | -1386.8518 |  |  | -2988.4658 |  |  | -5239.8389 |  |  | -7973.8975 |  |  | -10758.1246 |  |  | -14803.1177
[13 empty] | Press drop ratio this iteration |  |  | 0.18925 |  |  | 0.11889 |  |  | 2.4124 |  |  | 1.1452 |  |  | 1.0452 |  |  | 1.0205 |  |  | 1.0116 |  |  | 1.0076 |  |  | 1.0056 |  |  | 1.0041
[13 empty] | Expansion factor | 12 |  | 0.90144 |  |  | 0.93809 |  |  | -0.26807 |  |  | 0.38955 |  |  | 0.42556 |  |  | 0.4055 |  |  | 0.36598 |  |  | 0.29391 |  |  | 0.43238 |  |  | 0.1115
[13 empty] | C Non choked w/ reducers | 5 |  | 177.6928 |  |  | 273.6279 |  |  | -836.307 |  |  | 168.241 |  |  | 85.2715 |  |  | 61.2401 |  |  | 52.7494 |  |  | 56.3255 |  |  | 37.4632 |  |  | 165.6932
[13 empty] | C Choked w/ reducers | 5 |  | 130.5853 |  |  | 165.8472 |  |  | 655.5636 |  |  | 132.9695 |  |  | 71.4201 |  |  | 49.7204 |  |  | 39.9171 |  |  | 36.1234 |  |  | 31.6909 |  |  | 45.2204
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 177.6928 |  |  | 273.6279 |  |  | 655.5636 |  |  | 132.9695 |  |  | 71.4201 |  |  | 49.7204 |  |  | 39.9171 |  |  | 36.1234 |  |  | 31.6909 |  |  | 45.2204
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 172.9628 | 22668.4676 |  | 262.0279 | 26476.5413 |  | 18000 | 64831.3242 |  | 18000 | 126274.8717 |  | 18000 | 211849.9533 |  | 18000 | 309200.7769 |  | 18000 | 408544.1934 |  | 18000 | 503486.5713 |  | 18000 | 584532.2787 |  | 18000 | 685410.0673
[13 empty] | Next iteration flow rate |  |  | 23121.837 | Abs Value of | Flow this | 26741.3068 | Abs Value of | Flow this | 65479.6375 | Abs Value of | Flow this | 127537.6204 | Abs Value of | Flow this | 213968.4529 | Abs Value of | Flow this | 312292.7846 | Abs Value of | Flow this | 412629.6354 | Abs Value of | Flow this | 508521.437 | Abs Value of | Flow this | 590377.6015 | Abs Value of | Flow this | 692264.1679 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 73.3498 |  |  | 67.6512 |  |  | -45.1487 |  |  | -423.3578 |  |  | -1355.3351 |  |  | -2989.1416 |  |  | -5285.7673 |  |  | -8074.7805 |  |  | -10914.9706 |  |  | -15041.268
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.35382 |  |  | 0.32633 |  |  | -0.21779 |  |  | -2.0422 |  |  | -6.5378 |  |  | -14.4189 |  |  | -25.4972 |  |  | -38.9507 |  |  | -52.6511 |  |  | -72.5553
[13 empty] | Delta P at this iteration flow rate |  |  | 13.3498 |  |  | 7.6512 |  |  | -105.1487 |  |  | -483.3578 |  |  | -1415.3351 |  |  | -3049.1416 |  |  | -5345.7673 |  |  | -8134.7805 |  |  | -10974.9706 |  |  | -15101.268
[13 empty] | Press drop ratio this iteration |  |  | 0.182 |  |  | 0.1131 |  |  | 2.3289 |  |  | 1.1417 |  |  | 1.0443 |  |  | 1.0201 |  |  | 1.0114 |  |  | 1.0074 |  |  | 1.0055 |  |  | 1.004
[13 empty] | Expansion factor | 12 |  | 0.90521 |  |  | 0.94111 |  |  | -0.2242 |  |  | 0.3914 |  |  | 0.42608 |  |  | 0.40574 |  |  | 0.36612 |  |  | 0.29402 |  |  | 0.43244 |  |  | 0.11157
[13 empty] | C Non choked w/ reducers | 5 |  | 185.6934 |  |  | 284.3043 |  |  | -967.1305 |  |  | 165.3284 |  |  | 84.2492 |  |  | 60.5731 |  |  | 52.1945 |  |  | 55.7394 |  |  | 37.0827 |  |  | 163.9345
[13 empty] | C Choked w/ reducers | 5 |  | 134.3874 |  |  | 168.6072 |  |  | 622.9995 |  |  | 131.089 |  |  | 70.6184 |  |  | 49.1982 |  |  | 39.5083 |  |  | 35.7577 |  |  | 31.3719 |  |  | 44.7673
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 185.6934 |  |  | 284.3043 |  |  | 622.9995 |  |  | 131.089 |  |  | 70.6184 |  |  | 49.1982 |  |  | 39.5083 |  |  | 35.7577 |  |  | 31.3719 |  |  | 44.7673
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 180.9634 | 23121.837 |  | 272.7043 | 26741.3068 |  | 18000 | 65479.6375 |  | 18000 | 127537.6204 |  | 18000 | 213968.4529 |  | 18000 | 312292.7846 |  | 18000 | 412629.6354 |  | 18000 | 508521.437 |  | 18000 | 590377.6015 |  | 18000 | 692264.1679
[13 empty] | Next iteration flow rate |  |  | 23584.2737 | Abs Value of | Flow this | 27008.7198 | Abs Value of | Flow this | 66134.4339 | Abs Value of | Flow this | 128812.9966 | Abs Value of | Flow this | 216108.1374 | Abs Value of | Flow this | 315415.7125 | Abs Value of | Flow this | 416755.9317 | Abs Value of | Flow this | 513606.6514 | Abs Value of | Flow this | 596281.3775 | Abs Value of | Flow this | 699186.8096 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 72.6678 |  |  | 67.1974 |  |  | -47.8698 |  |  | -433.6809 |  |  | -1384.391 |  |  | -3051.037 |  |  | -5393.8248 |  |  | -8238.8972 |  |  | -11136.1751 |  |  | -15345.4111
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.35053 |  |  | 0.32414 |  |  | -0.23091 |  |  | -2.092 |  |  | -6.678 |  |  | -14.7174 |  |  | -26.0185 |  |  | -39.7424 |  |  | -53.7181 |  |  | -74.0224
[13 empty] | Delta P at this iteration flow rate |  |  | 12.6678 |  |  | 7.1974 |  |  | -107.8698 |  |  | -493.6809 |  |  | -1444.391 |  |  | -3111.037 |  |  | -5453.8248 |  |  | -8298.8972 |  |  | -11196.1751 |  |  | -15405.4111
[13 empty] | Press drop ratio this iteration |  |  | 0.17432 |  |  | 0.10711 |  |  | 2.2534 |  |  | 1.1384 |  |  | 1.0433 |  |  | 1.0197 |  |  | 1.0111 |  |  | 1.0073 |  |  | 1.0054 |  |  | 1.0039
[13 empty] | Expansion factor | 12 |  | 0.90921 |  |  | 0.94423 |  |  | -0.18449 |  |  | 0.39319 |  |  | 0.42659 |  |  | 0.40598 |  |  | 0.36626 |  |  | 0.29412 |  |  | 0.43251 |  |  | 0.11164
[13 empty] | C Non choked w/ reducers | 5 |  | 194.49 |  |  | 296.079 |  |  | -1138.1746 |  |  | 162.5017 |  |  | 83.2431 |  |  | 59.9147 |  |  | 51.646 |  |  | 55.16 |  |  | 36.7064 |  |  | 162.1969
[13 empty] | C Choked w/ reducers | 5 |  | 138.3615 |  |  | 171.4434 |  |  | 593.4615 |  |  | 129.2483 |  |  | 69.8276 |  |  | 48.6822 |  |  | 39.104 |  |  | 35.3959 |  |  | 31.0562 |  |  | 44.3188
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 194.49 |  |  | 296.079 |  |  | 593.4615 |  |  | 129.2483 |  |  | 69.8276 |  |  | 48.6822 |  |  | 39.104 |  |  | 35.3959 |  |  | 31.0562 |  |  | 44.3188
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 189.76 | 23584.2737 |  | 284.479 | 27008.7198 |  | 18000 | 66134.4339 |  | 18000 | 128812.9966 |  | 18000 | 216108.1374 |  | 18000 | 315415.7125 |  | 18000 | 416755.9317 |  | 18000 | 513606.6514 |  | 18000 | 596281.3775 |  | 18000 | 699186.8096
[13 empty] | Next iteration flow rate |  |  | 24055.9592 | Abs Value of | Flow this | 27278.807 | Abs Value of | Flow this | 66795.7782 | Abs Value of | Flow this | 130101.1266 | Abs Value of | Flow this | 218269.2188 | Abs Value of | Flow this | 318569.8696 | Abs Value of | Flow this | 420923.4911 | Abs Value of | Flow this | 518742.7179 | Abs Value of | Flow this | 602244.1913 | Abs Value of | Flow this | 706178.6777 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 71.9583 |  |  | 66.7344 |  |  | -50.6456 |  |  | -444.2115 |  |  | -1414.0309 |  |  | -3114.1764 |  |  | -5504.0544 |  |  | -8406.3126 |  |  | -11361.8258 |  |  | -15655.6675
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.34711 |  |  | 0.32191 |  |  | -0.2443 |  |  | -2.1428 |  |  | -6.8209 |  |  | -15.022 |  |  | -26.5502 |  |  | -40.55 |  |  | -54.8066 |  |  | -75.519
[13 empty] | Delta P at this iteration flow rate |  |  | 11.9583 |  |  | 6.7344 |  |  | -110.6456 |  |  | -504.2115 |  |  | -1474.0309 |  |  | -3174.1764 |  |  | -5564.0544 |  |  | -8466.3126 |  |  | -11421.8258 |  |  | -15715.6675
[13 empty] | Press drop ratio this iteration |  |  | 0.16618 |  |  | 0.10091 |  |  | 2.1847 |  |  | 1.1351 |  |  | 1.0424 |  |  | 1.0193 |  |  | 1.0109 |  |  | 1.0071 |  |  | 1.0053 |  |  | 1.0038
[13 empty] | Expansion factor | 12 |  | 0.91345 |  |  | 0.94746 |  |  | -0.14838 |  |  | 0.39494 |  |  | 0.42709 |  |  | 0.40621 |  |  | 0.3664 |  |  | 0.29423 |  |  | 0.43257 |  |  | 0.11171
[13 empty] | C Non choked w/ reducers | 5 |  | 204.232 |  |  | 309.1621 |  |  | -1372.0481 |  |  | 159.7569 |  |  | 82.2527 |  |  | 59.2646 |  |  | 51.104 |  |  | 54.5871 |  |  | 36.334 |  |  | 160.48
[13 empty] | C Choked w/ reducers | 5 |  | 142.5203 |  |  | 174.3591 |  |  | 566.5441 |  |  | 127.4461 |  |  | 69.0475 |  |  | 48.1721 |  |  | 38.704 |  |  | 35.0379 |  |  | 30.7438 |  |  | 43.8749
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 204.232 |  |  | 309.1621 |  |  | 566.5441 |  |  | 127.4461 |  |  | 69.0475 |  |  | 48.1721 |  |  | 38.704 |  |  | 35.0379 |  |  | 30.7438 |  |  | 43.8749
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 199.502 | 24055.9592 |  | 297.5621 | 27278.807 |  | 18000 | 66795.7782 |  | 18000 | 130101.1266 |  | 18000 | 218269.2188 |  | 18000 | 318569.8696 |  | 18000 | 420923.4911 |  | 18000 | 518742.7179 |  | 18000 | 602244.1913 |  | 18000 | 706178.6777
[13 empty] | Next iteration flow rate |  |  | 24537.0784 | Abs Value of | Flow this | 27551.5951 | Abs Value of | Flow this | 67463.736 | Abs Value of | Flow this | 131402.1379 | Abs Value of | Flow this | 220451.911 | Abs Value of | Flow this | 321755.5683 | Abs Value of | Flow this | 425132.726 | Abs Value of | Flow this | 523930.1451 | Abs Value of | Flow this | 608266.6332 | Abs Value of | Flow this | 713240.4645 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 71.2201 |  |  | 66.2622 |  |  | -53.4772 |  |  | -454.9538 |  |  | -1444.2665 |  |  | -3178.585 |  |  | -5616.4995 |  |  | -8577.0931 |  |  | -11592.0122 |  |  | -15972.16
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.34355 |  |  | 0.31963 |  |  | -0.25796 |  |  | -2.1946 |  |  | -6.9668 |  |  | -15.3327 |  |  | -27.0926 |  |  | -41.3738 |  |  | -55.917 |  |  | -77.0457
[13 empty] | Delta P at this iteration flow rate |  |  | 11.2201 |  |  | 6.2622 |  |  | -113.4772 |  |  | -514.9538 |  |  | -1504.2665 |  |  | -3238.585 |  |  | -5676.4995 |  |  | -8637.0931 |  |  | -11652.0122 |  |  | -16032.16
[13 empty] | Press drop ratio this iteration |  |  | 0.15754 |  |  | 0.094506 |  |  | 2.122 |  |  | 1.1319 |  |  | 1.0415 |  |  | 1.0189 |  |  | 1.0107 |  |  | 1.007 |  |  | 1.0052 |  |  | 1.0038
[13 empty] | Expansion factor | 12 |  | 0.91795 |  |  | 0.95079 |  |  | -0.11541 |  |  | 0.39664 |  |  | 0.42758 |  |  | 0.40644 |  |  | 0.36654 |  |  | 0.29432 |  |  | 0.43262 |  |  | 0.11177
[13 empty] | C Non choked w/ reducers | 5 |  | 215.1119 |  |  | 323.8256 |  |  | -1712.1148 |  |  | 157.0902 |  |  | 81.2779 |  |  | 58.6227 |  |  | 50.5682 |  |  | 54.0207 |  |  | 35.9656 |  |  | 158.7836
[13 empty] | C Choked w/ reducers | 5 |  | 146.8774 |  |  | 177.3578 |  |  | 541.9112 |  |  | 125.6813 |  |  | 68.2781 |  |  | 47.6679 |  |  | 38.3084 |  |  | 34.6836 |  |  | 30.4347 |  |  | 43.4356
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 215.1119 |  |  | 323.8256 |  |  | 541.9112 |  |  | 125.6813 |  |  | 68.2781 |  |  | 47.6679 |  |  | 38.3084 |  |  | 34.6836 |  |  | 30.4347 |  |  | 43.4356
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 210.3819 | 24537.0784 |  | 312.2256 | 27551.5951 |  | 18000 | 67463.736 |  | 18000 | 131402.1379 |  | 18000 | 220451.911 |  | 18000 | 321755.5683 |  | 18000 | 425132.726 |  | 18000 | 523930.1451 |  | 18000 | 608266.6332 |  | 18000 | 713240.4645
[13 empty] | Next iteration flow rate |  |  | 25027.82 | Abs Value of | Flow this | 27827.111 | Abs Value of | Flow this | 68138.3733 | Abs Value of | Flow this | 132716.1593 | Abs Value of | Flow this | 222656.4301 | Abs Value of | Flow this | 324973.124 | Abs Value of | Flow this | 429384.0532 | Abs Value of | Flow this | 529169.4465 | Abs Value of | Flow this | 614349.2995 | Abs Value of | Flow this | 720372.8691 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 70.4521 |  |  | 65.7804 |  |  | -56.3657 |  |  | -465.912 |  |  | -1475.1099 |  |  | -3244.2882 |  |  | -5731.2047 |  |  | -8751.3063 |  |  | -11826.8252 |  |  | -16295.0141
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.33984 |  |  | 0.31731 |  |  | -0.27189 |  |  | -2.2474 |  |  | -7.1156 |  |  | -15.6496 |  |  | -27.6459 |  |  | -42.2141 |  |  | -57.0496 |  |  | -78.6031
[13 empty] | Delta P at this iteration flow rate |  |  | 10.4521 |  |  | 5.7804 |  |  | -116.3657 |  |  | -525.912 |  |  | -1535.1099 |  |  | -3304.2882 |  |  | -5791.2047 |  |  | -8811.3063 |  |  | -11886.8252 |  |  | -16355.0141
[13 empty] | Press drop ratio this iteration |  |  | 0.14836 |  |  | 0.087875 |  |  | 2.0645 |  |  | 1.1288 |  |  | 1.0407 |  |  | 1.0185 |  |  | 1.0105 |  |  | 1.0069 |  |  | 1.0051 |  |  | 1.0037
[13 empty] | Expansion factor | 12 |  | 0.92273 |  |  | 0.95424 |  |  | -0.085187 |  |  | 0.3983 |  |  | 0.42806 |  |  | 0.40666 |  |  | 0.36668 |  |  | 0.29442 |  |  | 0.43268 |  |  | 0.11184
[13 empty] | C Non choked w/ reducers | 5 |  | 227.3833 |  |  | 340.4283 |  |  | -2253.4243 |  |  | 154.498 |  |  | 80.3181 |  |  | 57.989 |  |  | 50.0387 |  |  | 53.4608 |  |  | 35.6011 |  |  | 157.1072
[13 empty] | C Choked w/ reducers | 5 |  | 151.4482 |  |  | 180.4433 |  |  | 519.2818 |  |  | 123.9525 |  |  | 67.5189 |  |  | 47.1696 |  |  | 37.9171 |  |  | 34.3331 |  |  | 30.1287 |  |  | 43.0007
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 227.3833 |  |  | 340.4283 |  |  | 519.2818 |  |  | 123.9525 |  |  | 67.5189 |  |  | 47.1696 |  |  | 37.9171 |  |  | 34.3331 |  |  | 30.1287 |  |  | 43.0007
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 222.6533 | 25027.82 |  | 328.8283 | 27827.111 |  | 18000 | 68138.3733 |  | 18000 | 132716.1593 |  | 18000 | 222656.4301 |  | 18000 | 324973.124 |  | 18000 | 429384.0532 |  | 18000 | 529169.4465 |  | 18000 | 614349.2995 |  | 18000 | 720372.8691
[13 empty] | Next iteration flow rate |  |  | 25528.3763 | Abs Value of | Flow this | 28105.3822 | Abs Value of | Flow this | 68819.7571 | Abs Value of | Flow this | 134043.3208 | Abs Value of | Flow this | 224882.9944 | Abs Value of | Flow this | 328222.8552 | Abs Value of | Flow this | 433677.8938 | Abs Value of | Flow this | 534461.141 | Abs Value of | Flow this | 620492.7925 | Abs Value of | Flow this | 727576.5978 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 69.6531 |  |  | 65.289 |  |  | -59.3123 |  |  | -477.0905 |  |  | -1506.5732 |  |  | -3311.312 |  |  | -5848.2156 |  |  | -8929.0212 |  |  | -12066.358 |  |  | -16624.3575
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.33599 |  |  | 0.31494 |  |  | -0.28611 |  |  | -2.3014 |  |  | -7.2673 |  |  | -15.9729 |  |  | -28.2103 |  |  | -43.0714 |  |  | -58.2051 |  |  | -80.1917
[13 empty] | Delta P at this iteration flow rate |  |  | 9.6531 |  |  | 5.289 |  |  | -119.3123 |  |  | -537.0905 |  |  | -1566.5732 |  |  | -3371.312 |  |  | -5908.2156 |  |  | -8989.0212 |  |  | -12126.358 |  |  | -16684.3575
[13 empty] | Press drop ratio this iteration |  |  | 0.13859 |  |  | 0.081009 |  |  | 2.0116 |  |  | 1.1258 |  |  | 1.0398 |  |  | 1.0181 |  |  | 1.0103 |  |  | 1.0067 |  |  | 1.005 |  |  | 1.0036
[13 empty] | Expansion factor | 12 |  | 0.92782 |  |  | 0.95782 |  |  | -0.05739 |  |  | 0.3999 |  |  | 0.42852 |  |  | 0.40688 |  |  | 0.36681 |  |  | 0.29452 |  |  | 0.43274 |  |  | 0.11191
[13 empty] | C Non choked w/ reducers | 5 |  | 241.3885 |  |  | 359.4555 |  |  | -3252.4425 |  |  | 151.9772 |  |  | 79.373 |  |  | 57.3632 |  |  | 49.5153 |  |  | 52.9071 |  |  | 35.2404 |  |  | 155.4506
[13 empty] | C Choked w/ reducers | 5 |  | 156.2492 |  |  | 183.6195 |  |  | 498.4193 |  |  | 122.2587 |  |  | 66.7699 |  |  | 46.677 |  |  | 37.5301 |  |  | 33.9863 |  |  | 29.8259 |  |  | 42.5704
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 241.3885 |  |  | 359.4555 |  |  | 498.4193 |  |  | 122.2587 |  |  | 66.7699 |  |  | 46.677 |  |  | 37.5301 |  |  | 33.9863 |  |  | 29.8259 |  |  | 42.5704
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 236.6585 | 25528.3763 |  | 347.8555 | 28105.3822 |  | 18000 | 68819.7571 |  | 18000 | 134043.3208 |  | 18000 | 224882.9944 |  | 18000 | 328222.8552 |  | 18000 | 433677.8938 |  | 18000 | 534461.141 |  | 18000 | 620492.7925 |  | 18000 | 727576.5978
[13 empty] | Next iteration flow rate |  |  | 26038.9439 | Abs Value of | Flow this | 28386.436 | Abs Value of | Flow this | 69507.9546 | Abs Value of | Flow this | 135383.7541 | Abs Value of | Flow this | 227131.8243 | Abs Value of | Flow this | 331505.0838 | Abs Value of | Flow this | 438014.6727 | Abs Value of | Flow this | 539805.7524 | Abs Value of | Flow this | 626697.7204 | Abs Value of | Flow this | 734852.3638 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 68.8217 |  |  | 64.7877 |  |  | -62.3181 |  |  | -488.4936 |  |  | -1538.669 |  |  | -3379.683 |  |  | -5967.5783 |  |  | -9110.3082 |  |  | -12310.7055 |  |  | -16960.3207
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.33198 |  |  | 0.31252 |  |  | -0.30061 |  |  | -2.3564 |  |  | -7.4222 |  |  | -16.3027 |  |  | -28.7861 |  |  | -43.9458 |  |  | -59.3838 |  |  | -81.8123
[13 empty] | Delta P at this iteration flow rate |  |  | 8.8217 |  |  | 4.7877 |  |  | -122.3181 |  |  | -548.4936 |  |  | -1598.669 |  |  | -3439.683 |  |  | -6027.5783 |  |  | -9170.3082 |  |  | -12370.7055 |  |  | -17020.3207
[13 empty] | Press drop ratio this iteration |  |  | 0.12818 |  |  | 0.073898 |  |  | 1.9628 |  |  | 1.1228 |  |  | 1.039 |  |  | 1.0178 |  |  | 1.0101 |  |  | 1.0066 |  |  | 1.0049 |  |  | 1.0035
[13 empty] | Expansion factor | 12 |  | 0.93324 |  |  | 0.96152 |  |  | -0.031742 |  |  | 0.40147 |  |  | 0.42898 |  |  | 0.40709 |  |  | 0.36693 |  |  | 0.29461 |  |  | 0.4328 |  |  | 0.11197
[13 empty] | C Non choked w/ reducers | 5 |  | 257.6025 |  |  | 381.5829 |  |  | -5722.6004 |  |  | 149.5246 |  |  | 78.4423 |  |  | 56.7452 |  |  | 48.998 |  |  | 52.3597 |  |  | 34.8836 |  |  | 153.8136
[13 empty] | C Choked w/ reducers | 5 |  | 161.2993 |  |  | 186.8907 |  |  | 479.1227 |  |  | 120.5988 |  |  | 66.0309 |  |  | 46.19 |  |  | 37.1472 |  |  | 33.6431 |  |  | 29.5263 |  |  | 42.1444
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 257.6025 |  |  | 381.5829 |  |  | 479.1227 |  |  | 120.5988 |  |  | 66.0309 |  |  | 46.19 |  |  | 37.1472 |  |  | 33.6431 |  |  | 29.5263 |  |  | 42.1444
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 252.8725 | 26038.9439 |  | 369.9829 | 28386.436 |  | 18000 | 69507.9546 |  | 18000 | 135383.7541 |  | 18000 | 227131.8243 |  | 18000 | 331505.0838 |  | 18000 | 438014.6727 |  | 18000 | 539805.7524 |  | 18000 | 626697.7204 |  | 18000 | 734852.3638
[13 empty] | Next iteration flow rate |  |  | 26559.7228 | Abs Value of | Flow this | 28670.3003 | Abs Value of | Flow this | 70203.0342 | Abs Value of | Flow this | 136737.5916 | Abs Value of | Flow this | 229403.1426 | Abs Value of | Flow this | 334820.1346 | Abs Value of | Flow this | 442394.8194 | Abs Value of | Flow this | 545203.8099 | Abs Value of | Flow this | 632964.6977 | Abs Value of | Flow this | 742200.8875 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 67.9568 |  |  | 64.2763 |  |  | -65.3843 |  |  | -500.1259 |  |  | -1571.4099 |  |  | -3449.4283 |  |  | -6089.3403 |  |  | -9295.239 |  |  | -12559.9643 |  |  | -17303.0368
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.32781 |  |  | 0.31005 |  |  | -0.3154 |  |  | -2.4125 |  |  | -7.5801 |  |  | -16.6392 |  |  | -29.3735 |  |  | -44.8379 |  |  | -60.5861 |  |  | -83.4655
[13 empty] | Delta P at this iteration flow rate |  |  | 7.9568 |  |  | 4.2763 |  |  | -125.3843 |  |  | -560.1259 |  |  | -1631.4099 |  |  | -3509.4283 |  |  | -6149.3403 |  |  | -9355.239 |  |  | -12619.9643 |  |  | -17363.0368
[13 empty] | Press drop ratio this iteration |  |  | 0.11709 |  |  | 0.06653 |  |  | 1.9177 |  |  | 1.12 |  |  | 1.0382 |  |  | 1.0174 |  |  | 1.0099 |  |  | 1.0065 |  |  | 1.0048 |  |  | 1.0035
[13 empty] | Expansion factor | 12 |  | 0.93902 |  |  | 0.96536 |  |  | -0.0080084 |  |  | 0.40299 |  |  | 0.42943 |  |  | 0.4073 |  |  | 0.36706 |  |  | 0.2947 |  |  | 0.43285 |  |  | 0.11203
[13 empty] | C Non choked w/ reducers | 5 |  | 276.7084 |  |  | 407.7847 |  |  | -22089.9693 |  |  | 147.1372 |  |  | 77.5256 |  |  | 56.1349 |  |  | 48.4866 |  |  | 51.8184 |  |  | 34.5305 |  |  | 152.1958
[13 empty] | C Choked w/ reducers | 5 |  | 166.6193 |  |  | 190.2615 |  |  | 461.2206 |  |  | 118.9718 |  |  | 65.3017 |  |  | 45.7087 |  |  | 36.7685 |  |  | 33.3035 |  |  | 29.2297 |  |  | 41.7227
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 276.7084 |  |  | 407.7847 |  |  | 461.2206 |  |  | 118.9718 |  |  | 65.3017 |  |  | 45.7087 |  |  | 36.7685 |  |  | 33.3035 |  |  | 29.2297 |  |  | 41.7227
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 271.9784 | 26559.7228 |  | 396.1847 | 28670.3003 |  | 18000 | 70203.0342 |  | 18000 | 136737.5916 |  | 18000 | 229403.1426 |  | 18000 | 334820.1346 |  | 18000 | 442394.8194 |  | 18000 | 545203.8099 |  | 18000 | 632964.6977 |  | 18000 | 742200.8875
[13 empty] | Next iteration flow rate |  |  | 27090.9172 | Abs Value of | Flow this | 28957.0033 | Abs Value of | Flow this | 70905.0645 | Abs Value of | Flow this | 138104.9675 | Abs Value of | Flow this | 231697.174 | Abs Value of | Flow this | 338168.336 | Abs Value of | Flow this | 446818.7676 | Abs Value of | Flow this | 550655.848 | Abs Value of | Flow this | 639294.3446 | Abs Value of | Flow this | 749622.8963 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 67.057 |  |  | 63.7546 |  |  | -68.5121 |  |  | -511.9921 |  |  | -1604.8088 |  |  | -3520.5754 |  |  | -6213.5497 |  |  | -9483.8869 |  |  | -12814.2332 |  |  | -17652.6414
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.32347 |  |  | 0.30754 |  |  | -0.33049 |  |  | -2.4697 |  |  | -7.7412 |  |  | -16.9824 |  |  | -29.9726 |  |  | -45.7479 |  |  | -61.8127 |  |  | -85.1519
[13 empty] | Delta P at this iteration flow rate |  |  | 7.057 |  |  | 3.7546 |  |  | -128.5121 |  |  | -571.9921 |  |  | -1664.8088 |  |  | -3580.5754 |  |  | -6273.5497 |  |  | -9543.8869 |  |  | -12874.2332 |  |  | -17712.6414
[13 empty] | Press drop ratio this iteration |  |  | 0.10524 |  |  | 0.058891 |  |  | 1.8758 |  |  | 1.1172 |  |  | 1.0374 |  |  | 1.017 |  |  | 1.0097 |  |  | 1.0063 |  |  | 1.0047 |  |  | 1.0034
[13 empty] | Expansion factor | 12 |  | 0.94519 |  |  | 0.96934 |  |  | 0.014013 |  |  | 0.40447 |  |  | 0.42986 |  |  | 0.4075 |  |  | 0.36718 |  |  | 0.29479 |  |  | 0.4329 |  |  | 0.11209
[13 empty] | C Non choked w/ reducers | 5 |  | 299.7319 |  |  | 439.5287 |  |  | 12303.4204 |  |  | 144.8122 |  |  | 76.6227 |  |  | 55.5321 |  |  | 47.981 |  |  | 51.2831 |  |  | 34.1812 |  |  | 150.5969
[13 empty] | C Choked w/ reducers | 5 |  | 172.2322 |  |  | 193.7365 |  |  | 444.5657 |  |  | 117.3766 |  |  | 64.5821 |  |  | 45.2328 |  |  | 36.3938 |  |  | 32.9674 |  |  | 28.9362 |  |  | 41.3054
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 299.7319 |  |  | 439.5287 |  |  | 444.5657 |  |  | 117.3766 |  |  | 64.5821 |  |  | 45.2328 |  |  | 36.3938 |  |  | 32.9674 |  |  | 28.9362 |  |  | 41.3054
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 295.0019 | 27090.9172 |  | 427.9287 | 28957.0033 |  | 18000 | 70905.0645 |  | 18000 | 138104.9675 |  | 18000 | 231697.174 |  | 18000 | 338168.336 |  | 18000 | 446818.7676 |  | 18000 | 550655.848 |  | 18000 | 639294.3446 |  | 18000 | 749622.8963
[13 empty] | Next iteration flow rate |  |  | 27632.7356 | Abs Value of | Flow this | 29246.5734 | Abs Value of | Flow this | 71614.1152 | Abs Value of | Flow this | 139486.0172 | Abs Value of | Flow this | 234014.1457 | Abs Value of | Flow this | 341550.0193 | Abs Value of | Flow this | 451286.9553 | Abs Value of | Flow this | 556162.4065 | Abs Value of | Flow this | 645687.2881 | Abs Value of | Flow this | 757119.1253 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 66.1208 |  |  | 63.2224 |  |  | -71.7029 |  |  | -524.0968 |  |  | -1638.8791 |  |  | -3593.1526 |  |  | -6340.2556 |  |  | -9676.3267 |  |  | -13073.6129 |  |  | -18009.2731
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.31895 |  |  | 0.30497 |  |  | -0.34588 |  |  | -2.5281 |  |  | -7.9055 |  |  | -17.3325 |  |  | -30.5838 |  |  | -46.6762 |  |  | -63.0638 |  |  | -86.8722
[13 empty] | Delta P at this iteration flow rate |  |  | 6.1208 |  |  | 3.2224 |  |  | -131.7029 |  |  | -584.0968 |  |  | -1698.8791 |  |  | -3653.1526 |  |  | -6400.2556 |  |  | -9736.3267 |  |  | -13133.6129 |  |  | -18069.2731
[13 empty] | Press drop ratio this iteration |  |  | 0.09257 |  |  | 0.05097 |  |  | 1.8368 |  |  | 1.1145 |  |  | 1.0366 |  |  | 1.0167 |  |  | 1.0095 |  |  | 1.0062 |  |  | 1.0046 |  |  | 1.0033
[13 empty] | Expansion factor | 12 |  | 0.95179 |  |  | 0.97346 |  |  | 0.034498 |  |  | 0.40592 |  |  | 0.43029 |  |  | 0.4077 |  |  | 0.36731 |  |  | 0.29488 |  |  | 0.43296 |  |  | 0.11215
[13 empty] | C Non choked w/ reducers | 5 |  | 328.3 |  |  | 479.1529 |  |  | 4873.97 |  |  | 142.5472 |  |  | 75.7333 |  |  | 54.9368 |  |  | 47.4813 |  |  | 50.7538 |  |  | 33.8355 |  |  | 149.0166
[13 empty] | C Choked w/ reducers | 5 |  | 178.1643 |  |  | 197.3209 |  |  | 429.0307 |  |  | 115.8123 |  |  | 63.8719 |  |  | 44.7623 |  |  | 36.0232 |  |  | 32.6349 |  |  | 28.6457 |  |  | 40.8923
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 328.3 |  |  | 479.1529 |  |  | 429.0307 |  |  | 115.8123 |  |  | 63.8719 |  |  | 44.7623 |  |  | 36.0232 |  |  | 32.6349 |  |  | 28.6457 |  |  | 40.8923
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 323.57 | 27632.7356 |  | 467.5529 | 29246.5734 |  | 18000 | 71614.1152 |  | 18000 | 139486.0172 |  | 18000 | 234014.1457 |  | 18000 | 341550.0193 |  | 18000 | 451286.9553 |  | 18000 | 556162.4065 |  | 18000 | 645687.2881 |  | 18000 | 757119.1253
[13 empty] | Next iteration flow rate |  |  | 28185.3903 | Abs Value of | Flow this | 29539.0391 | Abs Value of | Flow this | 72330.2563 | Abs Value of | Flow this | 140880.8774 | Abs Value of | Flow this | 236354.2872 | Abs Value of | Flow this | 344965.5195 | Abs Value of | Flow this | 455799.8248 | Abs Value of | Flow this | 561724.0305 | Abs Value of | Flow this | 652144.161 | Abs Value of | Flow this | 764690.3165 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 65.1468 |  |  | 62.6796 |  |  | -74.9577 |  |  | -536.4447 |  |  | -1673.6342 |  |  | -3667.1886 |  |  | -6469.5084 |  |  | -9872.6345 |  |  | -13338.2061 |  |  | -18373.0732
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.31425 |  |  | 0.30235 |  |  | -0.36158 |  |  | -2.5877 |  |  | -8.0732 |  |  | -17.6896 |  |  | -31.2073 |  |  | -47.6231 |  |  | -64.3402 |  |  | -88.6271
[13 empty] | Delta P at this iteration flow rate |  |  | 5.1468 |  |  | 2.6796 |  |  | -134.9577 |  |  | -596.4447 |  |  | -1733.6342 |  |  | -3727.1886 |  |  | -6529.5084 |  |  | -9932.6345 |  |  | -13398.2061 |  |  | -18433.0732
[13 empty] | Press drop ratio this iteration |  |  | 0.079003 |  |  | 0.042751 |  |  | 1.8005 |  |  | 1.1118 |  |  | 1.0359 |  |  | 1.0164 |  |  | 1.0093 |  |  | 1.0061 |  |  | 1.0045 |  |  | 1.0033
[13 empty] | Expansion factor | 12 |  | 0.95885 |  |  | 0.97774 |  |  | 0.053598 |  |  | 0.40732 |  |  | 0.43071 |  |  | 0.4079 |  |  | 0.36742 |  |  | 0.29497 |  |  | 0.43301 |  |  | 0.11221
[13 empty] | C Non choked w/ reducers | 5 |  | 365.1889 |  |  | 530.6663 |  |  | 3061.3406 |  |  | 140.3396 |  |  | 74.857 |  |  | 54.3488 |  |  | 46.9872 |  |  | 50.2305 |  |  | 33.4935 |  |  | 147.4547
[13 empty] | C Choked w/ reducers | 5 |  | 184.4446 |  |  | 201.0201 |  |  | 414.5051 |  |  | 114.278 |  |  | 63.171 |  |  | 44.2972 |  |  | 35.6565 |  |  | 32.3059 |  |  | 28.3582 |  |  | 40.4834
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 365.1889 |  |  | 530.6663 |  |  | 414.5051 |  |  | 114.278 |  |  | 63.171 |  |  | 44.2972 |  |  | 35.6565 |  |  | 32.3059 |  |  | 28.3582 |  |  | 40.4834
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 360.4589 | 28185.3903 |  | 519.0663 | 29539.0391 |  | 18000 | 72330.2563 |  | 18000 | 140880.8774 |  | 18000 | 236354.2872 |  | 18000 | 344965.5195 |  | 18000 | 455799.8248 |  | 18000 | 561724.0305 |  | 18000 | 652144.161 |  | 18000 | 764690.3165
[13 empty] | Next iteration flow rate |  |  | 28749.0981 | Abs Value of | Flow this | 29834.4295 | Abs Value of | Flow this | 73053.5589 | Abs Value of | Flow this | 142289.6861 | Abs Value of | Flow this | 238717.8301 | Abs Value of | Flow this | 348415.1747 | Abs Value of | Flow this | 460357.8231 | Abs Value of | Flow this | 567341.2709 | Abs Value of | Flow this | 658665.6026 | Abs Value of | Flow this | 772337.2197 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 64.1334 |  |  | 62.1258 |  |  | -78.278 |  |  | -549.0409 |  |  | -1709.0879 |  |  | -3742.7127 |  |  | -6601.3591 |  |  | -10072.8881 |  |  | -13608.1177 |  |  | -18744.1856
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.30936 |  |  | 0.29968 |  |  | -0.37759 |  |  | -2.6484 |  |  | -8.2442 |  |  | -18.0539 |  |  | -31.8433 |  |  | -48.5891 |  |  | -65.6422 |  |  | -90.4173
[13 empty] | Delta P at this iteration flow rate |  |  | 4.1334 |  |  | 2.1258 |  |  | -138.278 |  |  | -609.0409 |  |  | -1769.0879 |  |  | -3802.7127 |  |  | -6661.3591 |  |  | -10132.8881 |  |  | -13668.1177 |  |  | -18804.1856
[13 empty] | Press drop ratio this iteration |  |  | 0.06445 |  |  | 0.034218 |  |  | 1.7665 |  |  | 1.1093 |  |  | 1.0351 |  |  | 1.016 |  |  | 1.0091 |  |  | 1.006 |  |  | 1.0044 |  |  | 1.0032
[13 empty] | Expansion factor | 12 |  | 0.96643 |  |  | 0.98218 |  |  | 0.071445 |  |  | 0.40869 |  |  | 0.43112 |  |  | 0.40809 |  |  | 0.36754 |  |  | 0.29505 |  |  | 0.43306 |  |  | 0.11227
[13 empty] | C Non choked w/ reducers | 5 |  | 415.639 |  |  | 601.6884 |  |  | 2242.4357 |  |  | 138.1872 |  |  | 73.9936 |  |  | 53.768 |  |  | 46.4988 |  |  | 49.7129 |  |  | 33.1551 |  |  | 145.911
[13 empty] | C Choked w/ reducers | 5 |  | 191.1062 |  |  | 204.84 |  |  | 400.8925 |  |  | 112.7727 |  |  | 62.4791 |  |  | 43.8374 |  |  | 35.2938 |  |  | 31.9802 |  |  | 28.0737 |  |  | 40.0787
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 415.639 |  |  | 601.6884 |  |  | 400.8925 |  |  | 112.7727 |  |  | 62.4791 |  |  | 43.8374 |  |  | 35.2938 |  |  | 31.9802 |  |  | 28.0737 |  |  | 40.0787
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 410.909 | 28749.0981 |  | 590.0884 | 29834.4295 |  | 18000 | 73053.5589 |  | 18000 | 142289.6861 |  | 18000 | 238717.8301 |  | 18000 | 348415.1747 |  | 18000 | 460357.8231 |  | 18000 | 567341.2709 |  | 18000 | 658665.6026 |  | 18000 | 772337.2197
[13 empty] | Next iteration flow rate |  |  | 29324.08 | Abs Value of | Flow this | 30132.7738 | Abs Value of | Flow this | 73784.0945 | Abs Value of | Flow this | 143712.583 | Abs Value of | Flow this | 241105.0084 | Abs Value of | Flow this | 351899.3265 | Abs Value of | Flow this | 464961.4013 | Abs Value of | Flow this | 573014.6836 | Abs Value of | Flow this | 665252.2586 | Abs Value of | Flow this | 780060.5919 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 63.0791 |  |  | 61.5609 |  |  | -81.665 |  |  | -561.8903 |  |  | -1745.2542 |  |  | -3819.7549 |  |  | -6735.8601 |  |  | -10277.1667 |  |  | -13883.4545 |  |  | -19122.7573
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.30428 |  |  | 0.29695 |  |  | -0.39393 |  |  | -2.7104 |  |  | -8.4187 |  |  | -18.4255 |  |  | -32.4921 |  |  | -49.5745 |  |  | -66.9703 |  |  | -92.2434
[13 empty] | Delta P at this iteration flow rate |  |  | 3.0791 |  |  | 1.5609 |  |  | -141.665 |  |  | -621.8903 |  |  | -1805.2542 |  |  | -3879.7549 |  |  | -6795.8601 |  |  | -10337.1667 |  |  | -13943.4545 |  |  | -19182.7573
[13 empty] | Press drop ratio this iteration |  |  | 0.048813 |  |  | 0.025356 |  |  | 1.7347 |  |  | 1.1068 |  |  | 1.0344 |  |  | 1.0157 |  |  | 1.0089 |  |  | 1.0058 |  |  | 1.0043 |  |  | 1.0031
[13 empty] | Expansion factor | 12 |  | 0.97458 |  |  | 0.9868 |  |  | 0.088155 |  |  | 0.41002 |  |  | 0.43152 |  |  | 0.40828 |  |  | 0.36765 |  |  | 0.29514 |  |  | 0.43311 |  |  | 0.11232
[13 empty] | C Non choked w/ reducers | 5 |  | 491.1495 |  |  | 709.1099 |  |  | 1775.4598 |  |  | 136.0877 |  |  | 73.1427 |  |  | 53.1943 |  |  | 46.0159 |  |  | 49.2011 |  |  | 32.8202 |  |  | 144.385
[13 empty] | C Choked w/ reducers | 5 |  | 198.1863 |  |  | 208.7869 |  |  | 388.1083 |  |  | 111.2958 |  |  | 61.7963 |  |  | 43.3828 |  |  | 34.9349 |  |  | 31.658 |  |  | 27.7921 |  |  | 39.6781
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 491.1495 |  |  | 709.1099 |  |  | 388.1083 |  |  | 111.2958 |  |  | 61.7963 |  |  | 43.3828 |  |  | 34.9349 |  |  | 31.658 |  |  | 27.7921 |  |  | 39.6781
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 486.4195 | 29324.08 |  | 697.5099 | 30132.7738 |  | 18000 | 73784.0945 |  | 18000 | 143712.583 |  | 18000 | 241105.0084 |  | 18000 | 351899.3265 |  | 18000 | 464961.4013 |  | 18000 | 573014.6836 |  | 18000 | 665252.2586 |  | 18000 | 780060.5919
[13 empty] | Next iteration flow rate |  |  | 29910.5616 | Abs Value of | Flow this | 30434.1015 | Abs Value of | Flow this | 74521.9354 | Abs Value of | Flow this | 145149.7088 | Abs Value of | Flow this | 243516.0584 | Abs Value of | Flow this | 355418.3197 | Abs Value of | Flow this | 469611.0153 | Abs Value of | Flow this | 578744.8304 | Abs Value of | Flow this | 671904.7812 | Abs Value of | Flow this | 787861.1978 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 61.9822 |  |  | 60.9847 |  |  | -85.1201 |  |  | -574.9979 |  |  | -1782.1474 |  |  | -3898.3456 |  |  | -6873.0645 |  |  | -10485.5514 |  |  | -14164.3256 |  |  | -19508.9384
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.29899 |  |  | 0.29417 |  |  | -0.4106 |  |  | -2.7736 |  |  | -8.5966 |  |  | -18.8046 |  |  | -33.1539 |  |  | -50.5797 |  |  | -68.3252 |  |  | -94.1062
[13 empty] | Delta P at this iteration flow rate |  |  | 1.9822 |  |  | 0.98467 |  |  | -145.1201 |  |  | -634.9979 |  |  | -1842.1474 |  |  | -3958.3456 |  |  | -6933.0645 |  |  | -10545.5514 |  |  | -14224.3256 |  |  | -19568.9384
[13 empty] | Press drop ratio this iteration |  |  | 0.03198 |  |  | 0.016146 |  |  | 1.7049 |  |  | 1.1043 |  |  | 1.0337 |  |  | 1.0154 |  |  | 1.0087 |  |  | 1.0057 |  |  | 1.0042 |  |  | 1.0031
[13 empty] | Expansion factor | 12 |  | 0.98334 |  |  | 0.99159 |  |  | 0.10383 |  |  | 0.41132 |  |  | 0.43191 |  |  | 0.40847 |  |  | 0.36777 |  |  | 0.29522 |  |  | 0.43316 |  |  | 0.11238
[13 empty] | C Non choked w/ reducers | 5 |  | 624.2697 |  |  | 901.6067 |  |  | 1473.4019 |  |  | 134.0391 |  |  | 72.3042 |  |  | 52.6276 |  |  | 45.5385 |  |  | 48.6949 |  |  | 32.4889 |  |  | 142.8767
[13 empty] | C Choked w/ reducers | 5 |  | 205.7275 |  |  | 212.8674 |  |  | 376.0782 |  |  | 109.8463 |  |  | 61.1221 |  |  | 42.9332 |  |  | 34.5799 |  |  | 31.3391 |  |  | 27.5134 |  |  | 39.2816
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 624.2697 |  |  | 901.6067 |  |  | 376.0782 |  |  | 109.8463 |  |  | 61.1221 |  |  | 42.9332 |  |  | 34.5799 |  |  | 31.3391 |  |  | 27.5134 |  |  | 39.2816
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 619.5397 | 29910.5616 |  | 890.0067 | 30434.1015 |  | 18000 | 74521.9354 |  | 18000 | 145149.7088 |  | 18000 | 243516.0584 |  | 18000 | 355418.3197 |  | 18000 | 469611.0153 |  | 18000 | 578744.8304 |  | 18000 | 671904.7812 |  | 18000 | 787861.1978
[13 empty] | Next iteration flow rate |  |  | 30508.7729 | Abs Value of | Flow this | 30738.4425 | Abs Value of | Flow this | 75267.1548 | Abs Value of | Flow this | 146601.2059 | Abs Value of | Flow this | 245951.219 | Abs Value of | Flow this | 358972.5029 | Abs Value of | Flow this | 474307.1255 | Abs Value of | Flow this | 584532.2787 | Abs Value of | Flow this | 678623.829 | Abs Value of | Flow this | 795739.8098 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 60.841 |  |  | 60.3968 |  |  | -88.6446 |  |  | -588.369 |  |  | -1819.7822 |  |  | -3978.5159 |  |  | -7013.0267 |  |  | -10698.1246 |  |  | -14450.8421 |  |  | -19902.8817
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.29348 |  |  | 0.29134 |  |  | -0.4276 |  |  | -2.8381 |  |  | -8.7782 |  |  | -19.1914 |  |  | -33.8291 |  |  | -51.6051 |  |  | -69.7072 |  |  | -96.0065
[13 empty] | Delta P at this iteration flow rate |  |  | 0.84098 |  |  | 0.39683 |  |  | -148.6446 |  |  | -648.369 |  |  | -1879.7822 |  |  | -4038.5159 |  |  | -7073.0267 |  |  | -10758.1246 |  |  | -14510.8421 |  |  | -19962.8817
[13 empty] | Press drop ratio this iteration |  |  | 0.013823 |  |  | 0.0065705 |  |  | 1.6769 |  |  | 1.102 |  |  | 1.033 |  |  | 1.0151 |  |  | 1.0086 |  |  | 1.0056 |  |  | 1.0042 |  |  | 1.003
[13 empty] | Expansion factor | 12 |  | 0.9928 |  |  | 0.99658 |  |  | 0.11856 |  |  | 0.41258 |  |  | 0.43229 |  |  | 0.40865 |  |  | 0.36787 |  |  | 0.2953 |  |  | 0.4332 |  |  | 0.11243
[13 empty] | C Non choked w/ reducers | 5 |  | 977.3081 |  |  | 1434.1809 |  |  | 1261.8253 |  |  | 132.0393 |  |  | 71.4777 |  |  | 52.0677 |  |  | 45.0665 |  |  | 48.1943 |  |  | 32.161 |  |  | 141.3857
[13 empty] | C Choked w/ reducers | 5 |  | 213.7782 |  |  | 217.0886 |  |  | 364.7365 |  |  | 108.4234 |  |  | 60.4567 |  |  | 42.4888 |  |  | 34.2287 |  |  | 31.0236 |  |  | 27.2376 |  |  | 38.8892
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 977.3081 |  |  | 1434.1809 |  |  | 364.7365 |  |  | 108.4234 |  |  | 60.4567 |  |  | 42.4888 |  |  | 34.2287 |  |  | 31.0236 |  |  | 27.2376 |  |  | 38.8892
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 972.5781 | 30508.7729 |  | 1422.5809 | 30738.4425 |  | 18000 | 75267.1548 |  | 18000 | 146601.2059 |  | 18000 | 245951.219 |  | 18000 | 358972.5029 |  | 18000 | 474307.1255 |  | 18000 | 584532.2787 |  | 18000 | 678623.829 |  | 18000 | 795739.8098
[13 empty] | Next iteration flow rate |  |  | 31118.9483 | Abs Value of | Flow this | 31045.827 | Abs Value of | Flow this | 76019.8263 | Abs Value of | Flow this | 148067.218 | Abs Value of | Flow this | 248410.7312 | Abs Value of | Flow this | 362562.228 | Abs Value of | Flow this | 479050.1967 | Abs Value of | Flow this | 590377.6015 | Abs Value of | Flow this | 685410.0673 | Abs Value of | Flow this | 803697.2079 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 59.6537 |  |  | 59.7972 |  |  | -92.24 |  |  | -602.0088 |  |  | -1858.1735 |  |  | -4060.2977 |  |  | -7155.8022 |  |  | -10914.9706 |  |  | -14743.1177 |  |  | -20304.7432
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.28775 |  |  | 0.28845 |  |  | -0.44494 |  |  | -2.9039 |  |  | -8.9634 |  |  | -19.5859 |  |  | -34.5178 |  |  | -52.6511 |  |  | -71.1171 |  |  | -97.945
[13 empty] | Delta P at this iteration flow rate |  |  | -0.34634 |  |  | -0.20282 |  |  | -152.24 |  |  | -662.0088 |  |  | -1918.1735 |  |  | -4120.2977 |  |  | -7215.8022 |  |  | -10974.9706 |  |  | -14803.1177 |  |  | -20364.7432
[13 empty] | Press drop ratio this iteration |  |  | -0.0058059 |  |  | -0.0033917 |  |  | 1.6505 |  |  | 1.0997 |  |  | 1.0323 |  |  | 1.0148 |  |  | 1.0084 |  |  | 1.0055 |  |  | 1.0041 |  |  | 1.003
[13 empty] | Expansion factor | 12 |  | 1.003 |  |  | 1.0018 |  |  | 0.13243 |  |  | 0.41382 |  |  | 0.43266 |  |  | 0.40882 |  |  | 0.36798 |  |  | 0.29537 |  |  | 0.43325 |  |  | 0.11248
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 1105.2394 |  |  | 130.0867 |  |  | 70.6631 |  |  | 51.5145 |  |  | 44.5998 |  |  | 47.6992 |  |  | 31.8365 |  |  | 139.9118
[13 empty] | C Choked w/ reducers | 5 |  | 222.3938 |  |  | 221.4582 |  |  | 354.0248 |  |  | 107.0265 |  |  | 59.7997 |  |  | 42.0493 |  |  | 33.8812 |  |  | 30.7113 |  |  | 26.9646 |  |  | 38.5007
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 354.0248 |  |  | 107.0265 |  |  | 59.7997 |  |  | 42.0493 |  |  | 33.8812 |  |  | 30.7113 |  |  | 26.9646 |  |  | 38.5007
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 31118.9483 |  | 18000 | 31045.827 |  | 18000 | 76019.8263 |  | 18000 | 148067.218 |  | 18000 | 248410.7312 |  | 18000 | 362562.228 |  | 18000 | 479050.1967 |  | 18000 | 590377.6015 |  | 18000 | 685410.0673 |  | 18000 | 803697.2079
[13 empty] | Next iteration flow rate |  |  | 31741.3273 | Abs Value of | Flow this | 31356.2852 | Abs Value of | Flow this | 76780.0246 | Abs Value of | Flow this | 149547.8901 | Abs Value of | Flow this | 250894.8385 | Abs Value of | Flow this | 366187.8502 | Abs Value of | Flow this | 483840.6987 | Abs Value of | Flow this | 596281.3775 | Abs Value of | Flow this | 692264.1679 | Abs Value of | Flow this | 811734.18 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 58.4184 |  |  | 59.1855 |  |  | -95.9077 |  |  | -615.9228 |  |  | -1897.3364 |  |  | -4143.7233 |  |  | -7301.4474 |  |  | -11136.1751 |  |  | -15041.268 |  |  | -20714.6822
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.2818 |  |  | 0.2855 |  |  | -0.46263 |  |  | -2.9711 |  |  | -9.1523 |  |  | -19.9883 |  |  | -35.2204 |  |  | -53.7181 |  |  | -72.5553 |  |  | -99.9224
[13 empty] | Delta P at this iteration flow rate |  |  | -1.5816 |  |  | -0.81452 |  |  | -155.9077 |  |  | -675.9228 |  |  | -1957.3364 |  |  | -4203.7233 |  |  | -7361.4474 |  |  | -11196.1751 |  |  | -15101.268 |  |  | -20774.6822
[13 empty] | Press drop ratio this iteration |  |  | -0.027074 |  |  | -0.013762 |  |  | 1.6256 |  |  | 1.0974 |  |  | 1.0316 |  |  | 1.0145 |  |  | 1.0082 |  |  | 1.0054 |  |  | 1.004 |  |  | 1.0029
[13 empty] | Expansion factor | 12 |  | 1.0141 |  |  | 1.0072 |  |  | 0.14551 |  |  | 0.41502 |  |  | 0.43303 |  |  | 0.409 |  |  | 0.36809 |  |  | 0.29545 |  |  | 0.43329 |  |  | 0.11254
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 984.5744 |  |  | 128.1794 |  |  | 69.86 |  |  | 50.968 |  |  | 44.1383 |  |  | 47.2096 |  |  | 31.5155 |  |  | 138.4548
[13 empty] | C Choked w/ reducers | 5 |  | 231.6384 |  |  | 225.9845 |  |  | 343.8912 |  |  | 105.6548 |  |  | 59.151 |  |  | 41.6148 |  |  | 33.5374 |  |  | 30.4023 |  |  | 26.6944 |  |  | 38.1161
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 343.8912 |  |  | 105.6548 |  |  | 59.151 |  |  | 41.6148 |  |  | 33.5374 |  |  | 30.4023 |  |  | 26.6944 |  |  | 38.1161
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 31741.3273 |  | 18000 | 31356.2852 |  | 18000 | 76780.0246 |  | 18000 | 149547.8901 |  | 18000 | 250894.8385 |  | 18000 | 366187.8502 |  | 18000 | 483840.6987 |  | 18000 | 596281.3775 |  | 18000 | 692264.1679 |  | 18000 | 811734.18
[13 empty] | Next iteration flow rate |  |  | 32376.1538 | Abs Value of | Flow this | 31669.8481 | Abs Value of | Flow this | 77547.8248 | Abs Value of | Flow this | 151043.369 | Abs Value of | Flow this | 253403.7869 | Abs Value of | Flow this | 369849.7287 | Abs Value of | Flow this | 488679.1057 | Abs Value of | Flow this | 602244.1913 | Abs Value of | Flow this | 699186.8096 | Abs Value of | Flow this | 819851.5218 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 57.1332 |  |  | 58.5615 |  |  | -99.6491 |  |  | -630.1165 |  |  | -1937.2865 |  |  | -4228.8258 |  |  | -7450.0202 |  |  | -11361.8258 |  |  | -15345.4111 |  |  | -21132.8609
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.2756 |  |  | 0.28249 |  |  | -0.48068 |  |  | -3.0395 |  |  | -9.345 |  |  | -20.3988 |  |  | -35.937 |  |  | -54.8066 |  |  | -74.0224 |  |  | -101.9396
[13 empty] | Delta P at this iteration flow rate |  |  | -2.8668 |  |  | -1.4385 |  |  | -159.6491 |  |  | -690.1165 |  |  | -1997.2865 |  |  | -4288.8258 |  |  | -7510.0202 |  |  | -11421.8258 |  |  | -15405.4111 |  |  | -21192.8609
[13 empty] | Press drop ratio this iteration |  |  | -0.050178 |  |  | -0.024564 |  |  | 1.6021 |  |  | 1.0952 |  |  | 1.031 |  |  | 1.0142 |  |  | 1.0081 |  |  | 1.0053 |  |  | 1.0039 |  |  | 1.0028
[13 empty] | Expansion factor | 12 |  | 1.0261 |  |  | 1.0128 |  |  | 0.15785 |  |  | 0.41619 |  |  | 0.43339 |  |  | 0.40917 |  |  | 0.36819 |  |  | 0.29553 |  |  | 0.43334 |  |  | 0.11259
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 888.6685 |  |  | 126.3157 |  |  | 69.0683 |  |  | 50.4281 |  |  | 43.682 |  |  | 46.7254 |  |  | 31.1978 |  |  | 137.0143
[13 empty] | C Choked w/ reducers | 5 |  | 241.586 |  |  | 230.6764 |  |  | 334.2895 |  |  | 104.3077 |  |  | 58.5105 |  |  | 41.1851 |  |  | 33.1972 |  |  | 30.0965 |  |  | 26.427 |  |  | 37.7355
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 334.2895 |  |  | 104.3077 |  |  | 58.5105 |  |  | 41.1851 |  |  | 33.1972 |  |  | 30.0965 |  |  | 26.427 |  |  | 37.7355
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 32376.1538 |  | 18000 | 31669.8481 |  | 18000 | 77547.8248 |  | 18000 | 151043.369 |  | 18000 | 253403.7869 |  | 18000 | 369849.7287 |  | 18000 | 488679.1057 |  | 18000 | 602244.1913 |  | 18000 | 699186.8096 |  | 18000 | 819851.5218
[13 empty] | Next iteration flow rate |  |  | 33023.6769 | Abs Value of | Flow this | 31986.5466 | Abs Value of | Flow this | 78323.3031 | Abs Value of | Flow this | 152553.8027 | Abs Value of | Flow this | 255937.8248 | Abs Value of | Flow this | 373548.226 | Abs Value of | Flow this | 493565.8968 | Abs Value of | Flow this | 608266.6332 | Abs Value of | Flow this | 706178.6777 | Abs Value of | Flow this | 828050.037 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 55.7961 |  |  | 57.9249 |  |  | -103.4656 |  |  | -644.5955 |  |  | -1978.0395 |  |  | -4315.6388 |  |  | -7601.5792 |  |  | -11592.0122 |  |  | -15655.6675 |  |  | -21559.445
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.26915 |  |  | 0.27942 |  |  | -0.49909 |  |  | -3.1094 |  |  | -9.5416 |  |  | -20.8176 |  |  | -36.6681 |  |  | -55.917 |  |  | -75.519 |  |  | -103.9974
[13 empty] | Delta P at this iteration flow rate |  |  | -4.2039 |  |  | -2.0751 |  |  | -163.4656 |  |  | -704.5955 |  |  | -2038.0395 |  |  | -4375.6388 |  |  | -7661.5792 |  |  | -11652.0122 |  |  | -15715.6675 |  |  | -21619.445
[13 empty] | Press drop ratio this iteration |  |  | -0.075345 |  |  | -0.035823 |  |  | 1.5799 |  |  | 1.0931 |  |  | 1.0303 |  |  | 1.0139 |  |  | 1.0079 |  |  | 1.0052 |  |  | 1.0038 |  |  | 1.0028
[13 empty] | Expansion factor | 12 |  | 1.0392 |  |  | 1.0187 |  |  | 0.16953 |  |  | 0.41733 |  |  | 0.43374 |  |  | 0.40933 |  |  | 0.36829 |  |  | 0.2956 |  |  | 0.43338 |  |  | 0.11264
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 810.5534 |  |  | 124.4941 |  |  | 68.2876 |  |  | 49.8945 |  |  | 43.2309 |  |  | 46.2464 |  |  | 30.8834 |  |  | 135.5903
[13 empty] | C Choked w/ reducers | 5 |  | 252.323 |  |  | 235.5434 |  |  | 325.178 |  |  | 102.9843 |  |  | 57.8781 |  |  | 40.7601 |  |  | 32.8607 |  |  | 29.7938 |  |  | 26.1623 |  |  | 37.3588
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 325.178 |  |  | 102.9843 |  |  | 57.8781 |  |  | 40.7601 |  |  | 32.8607 |  |  | 29.7938 |  |  | 26.1623 |  |  | 37.3588
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 33023.6769 |  | 18000 | 31986.5466 |  | 18000 | 78323.3031 |  | 18000 | 152553.8027 |  | 18000 | 255937.8248 |  | 18000 | 373548.226 |  | 18000 | 493565.8968 |  | 18000 | 608266.6332 |  | 18000 | 706178.6777 |  | 18000 | 828050.037
[13 empty] | Next iteration flow rate |  |  | 33684.1504 | Abs Value of | Flow this | 32306.412 | Abs Value of | Flow this | 79106.5361 | Abs Value of | Flow this | 154079.3408 | Abs Value of | Flow this | 258497.203 | Abs Value of | Flow this | 377283.7083 | Abs Value of | Flow this | 498501.5557 | Abs Value of | Flow this | 614349.2995 | Abs Value of | Flow this | 713240.4645 | Abs Value of | Flow this | 836330.5374 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 54.4049 |  |  | 57.2756 |  |  | -107.3589 |  |  | -659.3655 |  |  | -2019.6118 |  |  | -4404.1968 |  |  | -7756.1846 |  |  | -11826.8252 |  |  | -15972.16 |  |  | -21994.6035
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.26244 |  |  | 0.27628 |  |  | -0.51787 |  |  | -3.1806 |  |  | -9.7421 |  |  | -21.2447 |  |  | -37.4139 |  |  | -57.0496 |  |  | -77.0457 |  |  | -106.0965
[13 empty] | Delta P at this iteration flow rate |  |  | -5.5951 |  |  | -2.7244 |  |  | -167.3589 |  |  | -719.3655 |  |  | -2079.6118 |  |  | -4464.1968 |  |  | -7816.1846 |  |  | -11886.8252 |  |  | -16032.16 |  |  | -22054.6035
[13 empty] | Press drop ratio this iteration |  |  | -0.10284 |  |  | -0.047566 |  |  | 1.5589 |  |  | 1.091 |  |  | 1.0297 |  |  | 1.0136 |  |  | 1.0077 |  |  | 1.0051 |  |  | 1.0038 |  |  | 1.0027
[13 empty] | Expansion factor | 12 |  | 1.0536 |  |  | 1.0248 |  |  | 0.18058 |  |  | 0.41844 |  |  | 0.43408 |  |  | 0.4095 |  |  | 0.36839 |  |  | 0.29567 |  |  | 0.43343 |  |  | 0.11269
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 745.6539 |  |  | 122.713 |  |  | 67.5178 |  |  | 49.3674 |  |  | 42.7847 |  |  | 45.7727 |  |  | 30.5723 |  |  | 134.1824
[13 empty] | C Choked w/ reducers | 5 |  | 263.9504 |  |  | 240.5959 |  |  | 316.5195 |  |  | 101.6842 |  |  | 57.2536 |  |  | 40.34 |  |  | 32.5278 |  |  | 29.4943 |  |  | 25.9003 |  |  | 36.9858
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 316.5195 |  |  | 101.6842 |  |  | 57.2536 |  |  | 40.34 |  |  | 32.5278 |  |  | 29.4943 |  |  | 25.9003 |  |  | 36.9858
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 33684.1504 |  | 18000 | 32306.412 |  | 18000 | 79106.5361 |  | 18000 | 154079.3408 |  | 18000 | 258497.203 |  | 18000 | 377283.7083 |  | 18000 | 498501.5557 |  | 18000 | 614349.2995 |  | 18000 | 713240.4645 |  | 18000 | 836330.5374
[13 empty] | Next iteration flow rate |  |  | 34357.8335 | Abs Value of | Flow this | 32629.4762 | Abs Value of | Flow this | 79897.6015 | Abs Value of | Flow this | 155620.1342 | Abs Value of | Flow this | 261082.1751 | Abs Value of | Flow this | 381056.5454 | Abs Value of | Flow this | 503486.5713 | Abs Value of | Flow this | 620492.7925 | Abs Value of | Flow this | 720372.8691 | Abs Value of | Flow this | 844693.8427 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 52.9576 |  |  | 56.6132 |  |  | -111.3305 |  |  | -674.4323 |  |  | -2062.0196 |  |  | -4494.5348 |  |  | -7913.8975 |  |  | -12066.358 |  |  | -16295.0141 |  |  | -22438.5087
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.25545 |  |  | 0.27309 |  |  | -0.53703 |  |  | -3.2533 |  |  | -9.9467 |  |  | -21.6805 |  |  | -38.1747 |  |  | -58.2051 |  |  | -78.6031 |  |  | -108.2378
[13 empty] | Delta P at this iteration flow rate |  |  | -7.0424 |  |  | -3.3868 |  |  | -171.3305 |  |  | -734.4323 |  |  | -2122.0196 |  |  | -4554.5348 |  |  | -7973.8975 |  |  | -12126.358 |  |  | -16355.0141 |  |  | -22498.5087
[13 empty] | Press drop ratio this iteration |  |  | -0.13298 |  |  | -0.059823 |  |  | 1.5389 |  |  | 1.089 |  |  | 1.0291 |  |  | 1.0133 |  |  | 1.0076 |  |  | 1.005 |  |  | 1.0037 |  |  | 1.0027
[13 empty] | Expansion factor | 12 |  | 1.0693 |  |  | 1.0311 |  |  | 0.19106 |  |  | 0.41952 |  |  | 0.43442 |  |  | 0.40966 |  |  | 0.36848 |  |  | 0.29574 |  |  | 0.43347 |  |  | 0.11273
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 690.8418 |  |  | 120.9711 |  |  | 66.7587 |  |  | 48.8464 |  |  | 42.3435 |  |  | 45.3041 |  |  | 30.2644 |  |  | 132.7904
[13 empty] | C Choked w/ reducers | 5 |  | 276.5875 |  |  | 245.8451 |  |  | 308.2805 |  |  | 100.4067 |  |  | 56.6368 |  |  | 39.9244 |  |  | 32.1983 |  |  | 29.1979 |  |  | 25.641 |  |  | 36.6167
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 308.2805 |  |  | 100.4067 |  |  | 56.6368 |  |  | 39.9244 |  |  | 32.1983 |  |  | 29.1979 |  |  | 25.641 |  |  | 36.6167
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 34357.8335 |  | 18000 | 32629.4762 |  | 18000 | 79897.6015 |  | 18000 | 155620.1342 |  | 18000 | 261082.1751 |  | 18000 | 381056.5454 |  | 18000 | 503486.5713 |  | 18000 | 620492.7925 |  | 18000 | 720372.8691 |  | 18000 | 844693.8427
[13 empty] | Next iteration flow rate |  |  | 35044.9901 | Abs Value of | Flow this | 32955.7709 | Abs Value of | Flow this | 80696.5775 | Abs Value of | Flow this | 157176.3355 | Abs Value of | Flow this | 263692.9968 | Abs Value of | Flow this | 384867.1108 | Abs Value of | Flow this | 508521.437 | Abs Value of | Flow this | 626697.7204 | Abs Value of | Flow this | 727576.5978 | Abs Value of | Flow this | 853140.7812 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 51.4518 |  |  | 55.9375 |  |  | -115.3818 |  |  | -689.802 |  |  | -2105.2798 |  |  | -4586.6885 |  |  | -8074.7805 |  |  | -12310.7055 |  |  | -16624.3575 |  |  | -22891.3363
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.24819 |  |  | 0.26983 |  |  | -0.55657 |  |  | -3.3274 |  |  | -10.1553 |  |  | -22.125 |  |  | -38.9507 |  |  | -59.3838 |  |  | -80.1917 |  |  | -110.4221
[13 empty] | Delta P at this iteration flow rate |  |  | -8.5482 |  |  | -4.0625 |  |  | -175.3818 |  |  | -749.802 |  |  | -2165.2798 |  |  | -4646.6885 |  |  | -8134.7805 |  |  | -12370.7055 |  |  | -16684.3575 |  |  | -22951.3363
[13 empty] | Press drop ratio this iteration |  |  | -0.16614 |  |  | -0.072625 |  |  | 1.52 |  |  | 1.087 |  |  | 1.0285 |  |  | 1.0131 |  |  | 1.0074 |  |  | 1.0049 |  |  | 1.0036 |  |  | 1.0026
[13 empty] | Expansion factor | 12 |  | 1.0865 |  |  | 1.0378 |  |  | 0.20101 |  |  | 0.42058 |  |  | 0.43475 |  |  | 0.40981 |  |  | 0.36858 |  |  | 0.29581 |  |  | 0.43351 |  |  | 0.11278
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 643.9052 |  |  | 119.2669 |  |  | 66.0101 |  |  | 48.3316 |  |  | 41.9072 |  |  | 44.8407 |  |  | 29.9597 |  |  | 131.4141
[13 empty] | C Choked w/ reducers | 5 |  | 290.3759 |  |  | 251.3029 |  |  | 300.4305 |  |  | 99.1512 |  |  | 56.0278 |  |  | 39.5135 |  |  | 31.8724 |  |  | 28.9046 |  |  | 25.3844 |  |  | 36.2512
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 300.4305 |  |  | 99.1512 |  |  | 56.0278 |  |  | 39.5135 |  |  | 31.8724 |  |  | 28.9046 |  |  | 25.3844 |  |  | 36.2512
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 35044.9901 |  | 18000 | 32955.7709 |  | 18000 | 80696.5775 |  | 18000 | 157176.3355 |  | 18000 | 263692.9968 |  | 18000 | 384867.1108 |  | 18000 | 508521.437 |  | 18000 | 626697.7204 |  | 18000 | 727576.5978 |  | 18000 | 853140.7812
[13 empty] | Next iteration flow rate |  |  | 35745.8899 | Abs Value of | Flow this | 33285.3286 | Abs Value of | Flow this | 81503.5433 | Abs Value of | Flow this | 158748.0989 | Abs Value of | Flow this | 266329.9268 | Abs Value of | Flow this | 388715.7819 | Abs Value of | Flow this | 513606.6514 | Abs Value of | Flow this | 632964.6977 | Abs Value of | Flow this | 734852.3638 | Abs Value of | Flow this | 861672.189 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 49.8851 |  |  | 55.2482 |  |  | -119.5146 |  |  | -705.4807 |  |  | -2149.4096 |  |  | -4680.6946 |  |  | -8238.8972 |  |  | -12559.9643 |  |  | -16960.3207 |  |  | -23353.2658
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.24063 |  |  | 0.2665 |  |  | -0.57651 |  |  | -3.4031 |  |  | -10.3682 |  |  | -22.5785 |  |  | -39.7424 |  |  | -60.5861 |  |  | -81.8123 |  |  | -112.6503
[13 empty] | Delta P at this iteration flow rate |  |  | -10.1149 |  |  | -4.7518 |  |  | -179.5146 |  |  | -765.4807 |  |  | -2209.4096 |  |  | -4740.6946 |  |  | -8298.8972 |  |  | -12619.9643 |  |  | -17020.3207 |  |  | -23413.2658
[13 empty] | Press drop ratio this iteration |  |  | -0.20276 |  |  | -0.086008 |  |  | 1.502 |  |  | 1.085 |  |  | 1.0279 |  |  | 1.0128 |  |  | 1.0073 |  |  | 1.0048 |  |  | 1.0035 |  |  | 1.0026
[13 empty] | Expansion factor | 12 |  | 1.1056 |  |  | 1.0448 |  |  | 0.21046 |  |  | 0.42161 |  |  | 0.43507 |  |  | 0.40996 |  |  | 0.36867 |  |  | 0.29588 |  |  | 0.43355 |  |  | 0.11283
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 603.2362 |  |  | 117.5992 |  |  | 65.2717 |  |  | 47.8229 |  |  | 41.4758 |  |  | 44.3823 |  |  | 29.6582 |  |  | 130.0533
[13 empty] | C Choked w/ reducers | 5 |  | 305.4851 |  |  | 256.9826 |  |  | 292.942 |  |  | 97.9172 |  |  | 55.4262 |  |  | 39.1071 |  |  | 31.5498 |  |  | 28.6143 |  |  | 25.1304 |  |  | 35.8895
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 292.942 |  |  | 97.9172 |  |  | 55.4262 |  |  | 39.1071 |  |  | 31.5498 |  |  | 28.6143 |  |  | 25.1304 |  |  | 35.8895
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 35745.8899 |  | 18000 | 33285.3286 |  | 18000 | 81503.5433 |  | 18000 | 158748.0989 |  | 18000 | 266329.9268 |  | 18000 | 388715.7819 |  | 18000 | 513606.6514 |  | 18000 | 632964.6977 |  | 18000 | 734852.3638 |  | 18000 | 861672.189
[13 empty] | Next iteration flow rate |  |  | 36460.8077 | Abs Value of | Flow this | 33618.1819 | Abs Value of | Flow this | 82318.5787 | Abs Value of | Flow this | 160335.5799 | Abs Value of | Flow this | 268993.226 | Abs Value of | Flow this | 392602.9398 | Abs Value of | Flow this | 518742.7179 | Abs Value of | Flow this | 639294.3446 | Abs Value of | Flow this | 742200.8875 | Abs Value of | Flow this | 870288.9109 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 48.2552 |  |  | 54.5451 |  |  | -123.7305 |  |  | -721.4745 |  |  | -2194.4263 |  |  | -4776.5902 |  |  | -8406.3126 |  |  | -12814.2332 |  |  | -17303.0368 |  |  | -23824.4801
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.23277 |  |  | 0.26311 |  |  | -0.59684 |  |  | -3.4802 |  |  | -10.5854 |  |  | -23.0411 |  |  | -40.55 |  |  | -61.8127 |  |  | -83.4655 |  |  | -114.9233
[13 empty] | Delta P at this iteration flow rate |  |  | -11.7448 |  |  | -5.4549 |  |  | -183.7305 |  |  | -781.4745 |  |  | -2254.4263 |  |  | -4836.5902 |  |  | -8466.3126 |  |  | -12874.2332 |  |  | -17363.0368 |  |  | -23884.4801
[13 empty] | Press drop ratio this iteration |  |  | -0.24339 |  |  | -0.10001 |  |  | 1.4849 |  |  | 1.0832 |  |  | 1.0273 |  |  | 1.0126 |  |  | 1.0071 |  |  | 1.0047 |  |  | 1.0035 |  |  | 1.0025
[13 empty] | Expansion factor | 12 |  | 1.1268 |  |  | 1.0521 |  |  | 0.21945 |  |  | 0.42261 |  |  | 0.43538 |  |  | 0.41011 |  |  | 0.36876 |  |  | 0.29595 |  |  | 0.43359 |  |  | 0.11287
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 567.6377 |  |  | 115.9668 |  |  | 64.5433 |  |  | 47.3201 |  |  | 41.0491 |  |  | 43.9288 |  |  | 29.3598 |  |  | 128.7078
[13 empty] | C Choked w/ reducers | 5 |  | 322.1197 |  |  | 262.8983 |  |  | 285.7902 |  |  | 96.704 |  |  | 54.8321 |  |  | 38.7052 |  |  | 31.2307 |  |  | 28.3269 |  |  | 24.879 |  |  | 35.5315
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 285.7902 |  |  | 96.704 |  |  | 54.8321 |  |  | 38.7052 |  |  | 31.2307 |  |  | 28.3269 |  |  | 24.879 |  |  | 35.5315
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 36460.8077 |  | 18000 | 33618.1819 |  | 18000 | 82318.5787 |  | 18000 | 160335.5799 |  | 18000 | 268993.226 |  | 18000 | 392602.9398 |  | 18000 | 518742.7179 |  | 18000 | 639294.3446 |  | 18000 | 742200.8875 |  | 18000 | 870288.9109
[13 empty] | Next iteration flow rate |  |  | 37190.0239 | Abs Value of | Flow this | 33954.3637 | Abs Value of | Flow this | 83141.7645 | Abs Value of | Flow this | 161938.9357 | Abs Value of | Flow this | 271683.1583 | Abs Value of | Flow this | 396528.9692 | Abs Value of | Flow this | 523930.1451 | Abs Value of | Flow this | 645687.2881 | Abs Value of | Flow this | 749622.8963 | Abs Value of | Flow this | 878991.8 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 46.5594 |  |  | 53.8278 |  |  | -128.0311 |  |  | -737.7897 |  |  | -2240.3479 |  |  | -4874.4133 |  |  | -8577.0931 |  |  | -13073.6129 |  |  | -17652.6414 |  |  | -24305.1657
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.22459 |  |  | 0.25965 |  |  | -0.61759 |  |  | -3.5589 |  |  | -10.8069 |  |  | -23.513 |  |  | -41.3738 |  |  | -63.0638 |  |  | -85.1519 |  |  | -117.242
[13 empty] | Delta P at this iteration flow rate |  |  | -13.4406 |  |  | -6.1722 |  |  | -188.0311 |  |  | -797.7897 |  |  | -2300.3479 |  |  | -4934.4133 |  |  | -8637.0931 |  |  | -13133.6129 |  |  | -17712.6414 |  |  | -24365.1657
[13 empty] | Press drop ratio this iteration |  |  | -0.28868 |  |  | -0.11467 |  |  | 1.4686 |  |  | 1.0813 |  |  | 1.0268 |  |  | 1.0123 |  |  | 1.007 |  |  | 1.0046 |  |  | 1.0034 |  |  | 1.0025
[13 empty] | Expansion factor | 12 |  | 1.1503 |  |  | 1.0597 |  |  | 0.22802 |  |  | 0.42359 |  |  | 0.43569 |  |  | 0.41026 |  |  | 0.36885 |  |  | 0.29601 |  |  | 0.43363 |  |  | 0.11291
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 536.2 |  |  | 114.3684 |  |  | 63.8248 |  |  | 46.8233 |  |  | 40.6271 |  |  | 43.4803 |  |  | 29.0645 |  |  | 127.3774
[13 empty] | C Choked w/ reducers | 5 |  | 340.529 |  |  | 269.0655 |  |  | 278.9523 |  |  | 95.5112 |  |  | 54.2453 |  |  | 38.3078 |  |  | 30.915 |  |  | 28.0426 |  |  | 24.6301 |  |  | 35.1771
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 278.9523 |  |  | 95.5112 |  |  | 54.2453 |  |  | 38.3078 |  |  | 30.915 |  |  | 28.0426 |  |  | 24.6301 |  |  | 35.1771
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 37190.0239 |  | 18000 | 33954.3637 |  | 18000 | 83141.7645 |  | 18000 | 161938.9357 |  | 18000 | 271683.1583 |  | 18000 | 396528.9692 |  | 18000 | 523930.1451 |  | 18000 | 645687.2881 |  | 18000 | 749622.8963 |  | 18000 | 878991.8
[13 empty] | Next iteration flow rate |  |  | 37933.8244 | Abs Value of | Flow this | 34293.9074 | Abs Value of | Flow this | 83973.1821 | Abs Value of | Flow this | 163558.325 | Abs Value of | Flow this | 274399.9899 | Abs Value of | Flow this | 400494.2588 | Abs Value of | Flow this | 529169.4465 | Abs Value of | Flow this | 652144.161 | Abs Value of | Flow this | 757119.1253 | Abs Value of | Flow this | 887781.718 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 44.7951 |  |  | 53.0961 |  |  | -132.4182 |  |  | -754.4329 |  |  | -2287.1925 |  |  | -4974.2026 |  |  | -8751.3063 |  |  | -13338.2061 |  |  | -18009.2731 |  |  | -24795.5132
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.21608 |  |  | 0.25612 |  |  | -0.63875 |  |  | -3.6392 |  |  | -11.0328 |  |  | -23.9943 |  |  | -42.2141 |  |  | -64.3402 |  |  | -86.8722 |  |  | -119.6074
[13 empty] | Delta P at this iteration flow rate |  |  | -15.2049 |  |  | -6.9039 |  |  | -192.4182 |  |  | -814.4329 |  |  | -2347.1925 |  |  | -5034.2026 |  |  | -8811.3063 |  |  | -13398.2061 |  |  | -18069.2731 |  |  | -24855.5132
[13 empty] | Press drop ratio this iteration |  |  | -0.33943 |  |  | -0.13003 |  |  | 1.4531 |  |  | 1.0795 |  |  | 1.0262 |  |  | 1.0121 |  |  | 1.0069 |  |  | 1.0045 |  |  | 1.0033 |  |  | 1.0024
[13 empty] | Expansion factor | 12 |  | 1.1768 |  |  | 1.0677 |  |  | 0.23618 |  |  | 0.42455 |  |  | 0.43599 |  |  | 0.4104 |  |  | 0.36894 |  |  | 0.29607 |  |  | 0.43367 |  |  | 0.11296
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 508.2194 |  |  | 112.803 |  |  | 63.116 |  |  | 46.3322 |  |  | 40.2098 |  |  | 43.0366 |  |  | 28.7723 |  |  | 126.0619
[13 empty] | C Choked w/ reducers | 5 |  | 361.0199 |  |  | 275.5011 |  |  | 272.4077 |  |  | 94.3382 |  |  | 53.6656 |  |  | 37.9146 |  |  | 30.6025 |  |  | 27.7612 |  |  | 24.3838 |  |  | 34.8262
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 272.4077 |  |  | 94.3382 |  |  | 53.6656 |  |  | 37.9146 |  |  | 30.6025 |  |  | 27.7612 |  |  | 24.3838 |  |  | 34.8262
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 37933.8244 |  | 18000 | 34293.9074 |  | 18000 | 83973.1821 |  | 18000 | 163558.325 |  | 18000 | 274399.9899 |  | 18000 | 400494.2588 |  | 18000 | 529169.4465 |  | 18000 | 652144.161 |  | 18000 | 757119.1253 |  | 18000 | 887781.718
[13 empty] | Next iteration flow rate |  |  | 38692.5008 | Abs Value of | Flow this | 34636.8464 | Abs Value of | Flow this | 84812.9139 | Abs Value of | Flow this | 165193.9083 | Abs Value of | Flow this | 277143.9898 | Abs Value of | Flow this | 404499.2014 | Abs Value of | Flow this | 534461.141 | Abs Value of | Flow this | 658665.6026 | Abs Value of | Flow this | 764690.3165 | Abs Value of | Flow this | 896659.5352 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 42.9595 |  |  | 52.3497 |  |  | -136.8934 |  |  | -771.4107 |  |  | -2334.9787 |  |  | -5075.9977 |  |  | -8929.0212 |  |  | -13608.1177 |  |  | -18373.0732 |  |  | -25295.7166
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.20723 |  |  | 0.25252 |  |  | -0.66034 |  |  | -3.7211 |  |  | -11.2634 |  |  | -24.4853 |  |  | -43.0714 |  |  | -65.6422 |  |  | -88.6271 |  |  | -122.0202
[13 empty] | Delta P at this iteration flow rate |  |  | -17.0405 |  |  | -7.6503 |  |  | -196.8934 |  |  | -831.4107 |  |  | -2394.9787 |  |  | -5135.9977 |  |  | -8989.0212 |  |  | -13668.1177 |  |  | -18433.0732 |  |  | -25355.7166
[13 empty] | Press drop ratio this iteration |  |  | -0.39666 |  |  | -0.14614 |  |  | 1.4383 |  |  | 1.0778 |  |  | 1.0257 |  |  | 1.0118 |  |  | 1.0067 |  |  | 1.0044 |  |  | 1.0033 |  |  | 1.0024
[13 empty] | Expansion factor | 12 |  | 1.2066 |  |  | 1.0761 |  |  | 0.24396 |  |  | 0.42548 |  |  | 0.43629 |  |  | 0.41055 |  |  | 0.36902 |  |  | 0.29614 |  |  | 0.4337 |  |  | 0.113
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 483.143 |  |  | 111.2694 |  |  | 62.4166 |  |  | 45.8468 |  |  | 39.7971 |  |  | 42.5977 |  |  | 28.4831 |  |  | 124.761
[13 empty] | C Choked w/ reducers | 5 |  | 383.9745 |  |  | 282.2234 |  |  | 266.1373 |  |  | 93.1845 |  |  | 53.093 |  |  | 37.5258 |  |  | 30.2934 |  |  | 27.4826 |  |  | 24.14 |  |  | 34.4789
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 266.1373 |  |  | 93.1845 |  |  | 53.093 |  |  | 37.5258 |  |  | 30.2934 |  |  | 27.4826 |  |  | 24.14 |  |  | 34.4789
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 38692.5008 |  | 18000 | 34636.8464 |  | 18000 | 84812.9139 |  | 18000 | 165193.9083 |  | 18000 | 277143.9898 |  | 18000 | 404499.2014 |  | 18000 | 534461.141 |  | 18000 | 658665.6026 |  | 18000 | 764690.3165 |  | 18000 | 896659.5352
[13 empty] | Next iteration flow rate |  |  | 39466.3509 | Abs Value of | Flow this | 34983.2149 | Abs Value of | Flow this | 85661.0431 | Abs Value of | Flow this | 166845.8473 | Abs Value of | Flow this | 279915.4297 | Abs Value of | Flow this | 408544.1934 | Abs Value of | Flow this | 539805.7524 | Abs Value of | Flow this | 665252.2586 | Abs Value of | Flow this | 772337.2197 | Abs Value of | Flow this | 905626.1305 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 41.0498 |  |  | 51.5884 |  |  | -141.4586 |  |  | -788.7297 |  |  | -2383.7254 |  |  | -5179.8389 |  |  | -9110.3082 |  |  | -13883.4545 |  |  | -18744.1856 |  |  | -25805.9742
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.19801 |  |  | 0.24885 |  |  | -0.68236 |  |  | -3.8046 |  |  | -11.4985 |  |  | -24.9862 |  |  | -43.9458 |  |  | -66.9703 |  |  | -90.4173 |  |  | -124.4816
[13 empty] | Delta P at this iteration flow rate |  |  | -18.9502 |  |  | -8.4116 |  |  | -201.4586 |  |  | -848.7297 |  |  | -2443.7254 |  |  | -5239.8389 |  |  | -9170.3082 |  |  | -13943.4545 |  |  | -18804.1856 |  |  | -25865.9742
[13 empty] | Press drop ratio this iteration |  |  | -0.46164 |  |  | -0.16305 |  |  | 1.4242 |  |  | 1.0761 |  |  | 1.0252 |  |  | 1.0116 |  |  | 1.0066 |  |  | 1.0043 |  |  | 1.0032 |  |  | 1.0023
[13 empty] | Expansion factor | 12 |  | 1.2404 |  |  | 1.0849 |  |  | 0.2514 |  |  | 0.42639 |  |  | 0.43658 |  |  | 0.41068 |  |  | 0.36911 |  |  | 0.2962 |  |  | 0.43374 |  |  | 0.11304
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 460.5302 |  |  | 109.7668 |  |  | 61.7266 |  |  | 45.367 |  |  | 39.3889 |  |  | 42.1636 |  |  | 28.1969 |  |  | 123.4746
[13 empty] | C Choked w/ reducers | 5 |  | 409.8747 |  |  | 289.2526 |  |  | 260.1239 |  |  | 92.0498 |  |  | 52.5273 |  |  | 37.1413 |  |  | 29.9875 |  |  | 27.207 |  |  | 23.8987 |  |  | 34.1352
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 260.1239 |  |  | 92.0498 |  |  | 52.5273 |  |  | 37.1413 |  |  | 29.9875 |  |  | 27.207 |  |  | 23.8987 |  |  | 34.1352
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 39466.3509 |  | 18000 | 34983.2149 |  | 18000 | 85661.0431 |  | 18000 | 166845.8473 |  | 18000 | 279915.4297 |  | 18000 | 408544.1934 |  | 18000 | 539805.7524 |  | 18000 | 665252.2586 |  | 18000 | 772337.2197 |  | 18000 | 905626.1305
[13 empty] | Next iteration flow rate |  |  | 40255.6779 | Abs Value of | Flow this | 35333.0471 | Abs Value of | Flow this | 86517.6535 | Abs Value of | Flow this | 168514.3058 | Abs Value of | Flow this | 282714.584 | Abs Value of | Flow this | 412629.6354 | Abs Value of | Flow this | 545203.8099 | Abs Value of | Flow this | 671904.7812 | Abs Value of | Flow this | 780060.5919 | Abs Value of | Flow this | 914682.3918 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 39.0629 |  |  | 50.8117 |  |  | -146.1155 |  |  | -806.3967 |  |  | -2433.4519 |  |  | -5285.7673 |  |  | -9295.239 |  |  | -14164.3256 |  |  | -19122.7573 |  |  | -26326.4879
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.18843 |  |  | 0.2451 |  |  | -0.70482 |  |  | -3.8899 |  |  | -11.7384 |  |  | -25.4972 |  |  | -44.8379 |  |  | -68.3252 |  |  | -92.2434 |  |  | -126.9924
[13 empty] | Delta P at this iteration flow rate |  |  | -20.9371 |  |  | -9.1883 |  |  | -206.1155 |  |  | -866.3967 |  |  | -2493.4519 |  |  | -5345.7673 |  |  | -9355.239 |  |  | -14224.3256 |  |  | -19182.7573 |  |  | -26386.4879
[13 empty] | Press drop ratio this iteration |  |  | -0.53599 |  |  | -0.18083 |  |  | 1.4106 |  |  | 1.0744 |  |  | 1.0247 |  |  | 1.0114 |  |  | 1.0065 |  |  | 1.0042 |  |  | 1.0031 |  |  | 1.0023
[13 empty] | Expansion factor | 12 |  | 1.2791 |  |  | 1.0942 |  |  | 0.2585 |  |  | 0.42728 |  |  | 0.43686 |  |  | 0.41082 |  |  | 0.36919 |  |  | 0.29626 |  |  | 0.43378 |  |  | 0.11308
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 440.0258 |  |  | 108.294 |  |  | 61.0457 |  |  | 44.8928 |  |  | 38.9852 |  |  | 41.7341 |  |  | 27.9137 |  |  | 122.2025
[13 empty] | C Choked w/ reducers | 5 |  | 439.337 |  |  | 296.6109 |  |  | 254.3517 |  |  | 90.9334 |  |  | 51.9685 |  |  | 36.7609 |  |  | 29.6848 |  |  | 26.9341 |  |  | 23.6598 |  |  | 33.7949
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 254.3517 |  |  | 90.9334 |  |  | 51.9685 |  |  | 36.7609 |  |  | 29.6848 |  |  | 26.9341 |  |  | 23.6598 |  |  | 33.7949
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 40255.6779 |  | 18000 | 35333.0471 |  | 18000 | 86517.6535 |  | 18000 | 168514.3058 |  | 18000 | 282714.584 |  | 18000 | 412629.6354 |  | 18000 | 545203.8099 |  | 18000 | 671904.7812 |  | 18000 | 780060.5919 |  | 18000 | 914682.3918
[13 empty] | Next iteration flow rate |  |  | 41060.7914 | Abs Value of | Flow this | 35686.3775 | Abs Value of | Flow this | 87382.8301 | Abs Value of | Flow this | 170199.4489 | Abs Value of | Flow this | 285541.7298 | Abs Value of | Flow this | 416755.9317 | Abs Value of | Flow this | 550655.848 | Abs Value of | Flow this | 678623.829 | Abs Value of | Flow this | 787861.1978 | Abs Value of | Flow this | 923829.2157 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 36.9957 |  |  | 50.0193 |  |  | -150.8661 |  |  | -824.4189 |  |  | -2484.1779 |  |  | -5393.8248 |  |  | -9483.8869 |  |  | -14450.8421 |  |  | -19508.9384 |  |  | -26857.4639
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.17846 |  |  | 0.24128 |  |  | -0.72774 |  |  | -3.9768 |  |  | -11.9831 |  |  | -26.0185 |  |  | -45.7479 |  |  | -69.7072 |  |  | -94.1062 |  |  | -129.5537
[13 empty] | Delta P at this iteration flow rate |  |  | -23.0043 |  |  | -9.9807 |  |  | -210.8661 |  |  | -884.4189 |  |  | -2544.1779 |  |  | -5453.8248 |  |  | -9543.8869 |  |  | -14510.8421 |  |  | -19568.9384 |  |  | -26917.4639
[13 empty] | Press drop ratio this iteration |  |  | -0.62181 |  |  | -0.19954 |  |  | 1.3977 |  |  | 1.0728 |  |  | 1.0242 |  |  | 1.0111 |  |  | 1.0063 |  |  | 1.0042 |  |  | 1.0031 |  |  | 1.0022
[13 empty] | Expansion factor | 12 |  | 1.3238 |  |  | 1.1039 |  |  | 0.2653 |  |  | 0.42815 |  |  | 0.43714 |  |  | 0.41095 |  |  | 0.36927 |  |  | 0.29632 |  |  | 0.43381 |  |  | 0.11312
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 421.34 |  |  | 106.8501 |  |  | 60.3737 |  |  | 44.424 |  |  | 38.5858 |  |  | 41.3092 |  |  | 27.6334 |  |  | 120.9445
[13 empty] | C Choked w/ reducers | 5 |  | 473.1629 |  |  | 304.3223 |  |  | 248.806 |  |  | 89.835 |  |  | 51.4164 |  |  | 36.3847 |  |  | 29.3853 |  |  | 26.6641 |  |  | 23.4234 |  |  | 33.458
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 248.806 |  |  | 89.835 |  |  | 51.4164 |  |  | 36.3847 |  |  | 29.3853 |  |  | 26.6641 |  |  | 23.4234 |  |  | 33.458
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 41060.7914 |  | 18000 | 35686.3775 |  | 18000 | 87382.8301 |  | 18000 | 170199.4489 |  | 18000 | 285541.7298 |  | 18000 | 416755.9317 |  | 18000 | 550655.848 |  | 18000 | 678623.829 |  | 18000 | 787861.1978 |  | 18000 | 923829.2157
[13 empty] | Next iteration flow rate |  |  | 41882.0073 | Abs Value of | Flow this | 36043.2413 | Abs Value of | Flow this | 88256.6584 | Abs Value of | Flow this | 171901.4434 | Abs Value of | Flow this | 288397.1471 | Abs Value of | Flow this | 420923.4911 | Abs Value of | Flow this | 556162.4065 | Abs Value of | Flow this | 685410.0673 | Abs Value of | Flow this | 795739.8098 | Abs Value of | Flow this | 933067.5079 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 34.845 |  |  | 49.2111 |  |  | -155.7121 |  |  | -842.8034 |  |  | -2535.9235 |  |  | -5504.0544 |  |  | -9676.3267 |  |  | -14743.1177 |  |  | -19902.8817 |  |  | -27399.1126
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.16808 |  |  | 0.23738 |  |  | -0.75112 |  |  | -4.0655 |  |  | -12.2327 |  |  | -26.5502 |  |  | -46.6762 |  |  | -71.1171 |  |  | -96.0065 |  |  | -132.1665
[13 empty] | Delta P at this iteration flow rate |  |  | -25.155 |  |  | -10.7889 |  |  | -215.7121 |  |  | -902.8034 |  |  | -2595.9235 |  |  | -5564.0544 |  |  | -9736.3267 |  |  | -14803.1177 |  |  | -19962.8817 |  |  | -27459.1126
[13 empty] | Press drop ratio this iteration |  |  | -0.72191 |  |  | -0.21924 |  |  | 1.3853 |  |  | 1.0712 |  |  | 1.0237 |  |  | 1.0109 |  |  | 1.0062 |  |  | 1.0041 |  |  | 1.003 |  |  | 1.0022
[13 empty] | Expansion factor | 12 |  | 1.376 |  |  | 1.1142 |  |  | 0.27181 |  |  | 0.42899 |  |  | 0.43741 |  |  | 0.41108 |  |  | 0.36935 |  |  | 0.29637 |  |  | 0.43384 |  |  | 0.11316
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 404.2341 |  |  | 105.4344 |  |  | 59.7106 |  |  | 43.9607 |  |  | 38.1909 |  |  | 40.8889 |  |  | 27.3559 |  |  | 119.7004
[13 empty] | C Choked w/ reducers | 5 |  | 512.4144 |  |  | 312.4137 |  |  | 243.4733 |  |  | 88.7541 |  |  | 50.8709 |  |  | 36.0126 |  |  | 29.0889 |  |  | 26.3969 |  |  | 23.1893 |  |  | 33.1245
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 243.4733 |  |  | 88.7541 |  |  | 50.8709 |  |  | 36.0126 |  |  | 29.0889 |  |  | 26.3969 |  |  | 23.1893 |  |  | 33.1245
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 41882.0073 |  | 18000 | 36043.2413 |  | 18000 | 88256.6584 |  | 18000 | 171901.4434 |  | 18000 | 288397.1471 |  | 18000 | 420923.4911 |  | 18000 | 556162.4065 |  | 18000 | 685410.0673 |  | 18000 | 795739.8098 |  | 18000 | 933067.5079
[13 empty] | Next iteration flow rate |  |  | 42719.6474 | Abs Value of | Flow this | 36403.6737 | Abs Value of | Flow this | 89139.2249 | Abs Value of | Flow this | 173620.4578 | Abs Value of | Flow this | 291281.1186 | Abs Value of | Flow this | 425132.726 | Abs Value of | Flow this | 561724.0305 | Abs Value of | Flow this | 692264.1679 | Abs Value of | Flow this | 803697.2079 | Abs Value of | Flow this | 942398.183 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 32.6075 |  |  | 48.3866 |  |  | -160.6555 |  |  | -861.5574 |  |  | -2588.7092 |  |  | -5616.4995 |  |  | -9872.6345 |  |  | -15041.268 |  |  | -20304.7432 |  |  | -27951.6484
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.15729 |  |  | 0.2334 |  |  | -0.77496 |  |  | -4.1559 |  |  | -12.4873 |  |  | -27.0926 |  |  | -47.6231 |  |  | -72.5553 |  |  | -97.945 |  |  | -134.8318
[13 empty] | Delta P at this iteration flow rate |  |  | -27.3925 |  |  | -11.6134 |  |  | -220.6555 |  |  | -921.5574 |  |  | -2648.7092 |  |  | -5676.4995 |  |  | -9932.6345 |  |  | -15101.268 |  |  | -20364.7432 |  |  | -28011.6484
[13 empty] | Press drop ratio this iteration |  |  | -0.84007 |  |  | -0.24001 |  |  | 1.3735 |  |  | 1.0696 |  |  | 1.0232 |  |  | 1.0107 |  |  | 1.0061 |  |  | 1.004 |  |  | 1.003 |  |  | 1.0021
[13 empty] | Expansion factor | 12 |  | 1.4375 |  |  | 1.125 |  |  | 0.27804 |  |  | 0.42982 |  |  | 0.43767 |  |  | 0.41121 |  |  | 0.36943 |  |  | 0.29643 |  |  | 0.43388 |  |  | 0.1132
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 388.5096 |  |  | 104.0458 |  |  | 59.0561 |  |  | 43.5026 |  |  | 37.8002 |  |  | 40.4731 |  |  | 27.0814 |  |  | 118.47
[13 empty] | C Choked w/ reducers | 5 |  | 558.5283 |  |  | 320.9144 |  |  | 238.3414 |  |  | 87.6904 |  |  | 50.3319 |  |  | 35.6445 |  |  | 28.7956 |  |  | 26.1324 |  |  | 22.9577 |  |  | 32.7945
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 238.3414 |  |  | 87.6904 |  |  | 50.3319 |  |  | 35.6445 |  |  | 28.7956 |  |  | 26.1324 |  |  | 22.9577 |  |  | 32.7945
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 42719.6474 |  | 18000 | 36403.6737 |  | 18000 | 89139.2249 |  | 18000 | 173620.4578 |  | 18000 | 291281.1186 |  | 18000 | 425132.726 |  | 18000 | 561724.0305 |  | 18000 | 692264.1679 |  | 18000 | 803697.2079 |  | 18000 | 942398.183
[13 empty] | Next iteration flow rate |  |  | 43574.0404 | Abs Value of | Flow this | 36767.7105 | Abs Value of | Flow this | 90030.6172 | Abs Value of | Flow this | 175356.6624 | Abs Value of | Flow this | 294193.9298 | Abs Value of | Flow this | 429384.0532 | Abs Value of | Flow this | 567341.2709 | Abs Value of | Flow this | 699186.8096 | Abs Value of | Flow this | 811734.18 | Abs Value of | Flow this | 951822.1648 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 30.2795 |  |  | 47.5456 |  |  | -165.6983 |  |  | -880.6883 |  |  | -2642.5559 |  |  | -5731.2047 |  |  | -10072.8881 |  |  | -15345.4111 |  |  | -20714.6822 |  |  | -28515.2901
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.14606 |  |  | 0.22935 |  |  | -0.79929 |  |  | -4.2482 |  |  | -12.747 |  |  | -27.6459 |  |  | -48.5891 |  |  | -74.0224 |  |  | -99.9224 |  |  | -137.5506
[13 empty] | Delta P at this iteration flow rate |  |  | -29.7205 |  |  | -12.4544 |  |  | -225.6983 |  |  | -940.6883 |  |  | -2702.5559 |  |  | -5791.2047 |  |  | -10132.8881 |  |  | -15405.4111 |  |  | -20774.6822 |  |  | -28575.2901
[13 empty] | Press drop ratio this iteration |  |  | -0.98154 |  |  | -0.26195 |  |  | 1.3621 |  |  | 1.0681 |  |  | 1.0227 |  |  | 1.0105 |  |  | 1.006 |  |  | 1.0039 |  |  | 1.0029 |  |  | 1.0021
[13 empty] | Expansion factor | 12 |  | 1.5112 |  |  | 1.1364 |  |  | 0.28401 |  |  | 0.43063 |  |  | 0.43793 |  |  | 0.41133 |  |  | 0.3695 |  |  | 0.29649 |  |  | 0.43391 |  |  | 0.11324
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 374.0002 |  |  | 102.6836 |  |  | 58.4101 |  |  | 43.0498 |  |  | 37.4138 |  |  | 40.0617 |  |  | 26.8096 |  |  | 117.2531
[13 empty] | C Choked w/ reducers | 5 |  | 613.4986 |  |  | 329.8571 |  |  | 233.3986 |  |  | 86.6434 |  |  | 49.7994 |  |  | 35.2805 |  |  | 28.5053 |  |  | 25.8706 |  |  | 22.7284 |  |  | 32.4677
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 233.3986 |  |  | 86.6434 |  |  | 49.7994 |  |  | 35.2805 |  |  | 28.5053 |  |  | 25.8706 |  |  | 22.7284 |  |  | 32.4677
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 43574.0404 |  | 18000 | 36767.7105 |  | 18000 | 90030.6172 |  | 18000 | 175356.6624 |  | 18000 | 294193.9298 |  | 18000 | 429384.0532 |  | 18000 | 567341.2709 |  | 18000 | 699186.8096 |  | 18000 | 811734.18 |  | 18000 | 951822.1648
[13 empty] | Next iteration flow rate |  |  | 44445.5212 | Abs Value of | Flow this | 37135.3876 | Abs Value of | Flow this | 90930.9234 | Abs Value of | Flow this | 177110.229 | Abs Value of | Flow this | 297135.8691 | Abs Value of | Flow this | 433677.8938 | Abs Value of | Flow this | 573014.6836 | Abs Value of | Flow this | 706178.6777 | Abs Value of | Flow this | 819851.5218 | Abs Value of | Flow this | 961340.3865 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 27.8575 |  |  | 46.6876 |  |  | -170.8425 |  |  | -900.2038 |  |  | -2697.4849 |  |  | -5848.2156 |  |  | -10277.1667 |  |  | -15655.6675 |  |  | -21132.8609 |  |  | -29090.2611
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.13438 |  |  | 0.22521 |  |  | -0.8241 |  |  | -4.3424 |  |  | -13.012 |  |  | -28.2103 |  |  | -49.5745 |  |  | -75.519 |  |  | -101.9396 |  |  | -140.3241
[13 empty] | Delta P at this iteration flow rate |  |  | -32.1425 |  |  | -13.3124 |  |  | -230.8425 |  |  | -960.2038 |  |  | -2757.4849 |  |  | -5908.2156 |  |  | -10337.1667 |  |  | -15715.6675 |  |  | -21192.8609 |  |  | -29150.2611
[13 empty] | Press drop ratio this iteration |  |  | -1.1538 |  |  | -0.28514 |  |  | 1.3512 |  |  | 1.0667 |  |  | 1.0222 |  |  | 1.0103 |  |  | 1.0058 |  |  | 1.0038 |  |  | 1.0028 |  |  | 1.0021
[13 empty] | Expansion factor | 12 |  | 1.6009 |  |  | 1.1485 |  |  | 0.28974 |  |  | 0.43141 |  |  | 0.43819 |  |  | 0.41146 |  |  | 0.36958 |  |  | 0.29654 |  |  | 0.43394 |  |  | 0.11327
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 360.5654 |  |  | 101.347 |  |  | 57.7725 |  |  | 42.6021 |  |  | 37.0316 |  |  | 39.6547 |  |  | 26.5407 |  |  | 116.0497
[13 empty] | C Choked w/ reducers | 5 |  | 680.1745 |  |  | 339.278 |  |  | 228.6346 |  |  | 85.6127 |  |  | 49.2732 |  |  | 34.9203 |  |  | 28.2181 |  |  | 25.6115 |  |  | 22.5014 |  |  | 32.1442
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 228.6346 |  |  | 85.6127 |  |  | 49.2732 |  |  | 34.9203 |  |  | 28.2181 |  |  | 25.6115 |  |  | 22.5014 |  |  | 32.1442
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 44445.5212 |  | 18000 | 37135.3876 |  | 18000 | 90930.9234 |  | 18000 | 177110.229 |  | 18000 | 297135.8691 |  | 18000 | 433677.8938 |  | 18000 | 573014.6836 |  | 18000 | 706178.6777 |  | 18000 | 819851.5218 |  | 18000 | 961340.3865
[13 empty] | Next iteration flow rate |  |  | 45334.4316 | Abs Value of | Flow this | 37506.7414 | Abs Value of | Flow this | 91840.2326 | Abs Value of | Flow this | 178881.3313 | Abs Value of | Flow this | 300107.2278 | Abs Value of | Flow this | 438014.6727 | Abs Value of | Flow this | 578744.8304 | Abs Value of | Flow this | 713240.4645 | Abs Value of | Flow this | 828050.037 | Abs Value of | Flow this | 970953.7903 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 25.3377 |  |  | 45.8124 |  |  | -176.0901 |  |  | -920.1115 |  |  | -2753.518 |  |  | -5967.5783 |  |  | -10485.5514 |  |  | -15972.16 |  |  | -21559.445 |  |  | -29676.789
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.12222 |  |  | 0.22099 |  |  | -0.84941 |  |  | -4.4384 |  |  | -13.2823 |  |  | -28.7861 |  |  | -50.5797 |  |  | -77.0457 |  |  | -103.9974 |  |  | -143.1534
[13 empty] | Delta P at this iteration flow rate |  |  | -34.6623 |  |  | -14.1876 |  |  | -236.0901 |  |  | -980.1115 |  |  | -2813.518 |  |  | -6027.5783 |  |  | -10545.5514 |  |  | -16032.16 |  |  | -21619.445 |  |  | -29736.789
[13 empty] | Press drop ratio this iteration |  |  | -1.368 |  |  | -0.30969 |  |  | 1.3407 |  |  | 1.0652 |  |  | 1.0218 |  |  | 1.0101 |  |  | 1.0057 |  |  | 1.0038 |  |  | 1.0028 |  |  | 1.002
[13 empty] | Expansion factor | 12 |  | 1.7125 |  |  | 1.1613 |  |  | 0.29525 |  |  | 0.43218 |  |  | 0.43844 |  |  | 0.41157 |  |  | 0.36965 |  |  | 0.29659 |  |  | 0.43398 |  |  | 0.11331
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 348.0858 |  |  | 100.0353 |  |  | 57.143 |  |  | 42.1595 |  |  | 36.6535 |  |  | 39.2521 |  |  | 26.2745 |  |  | 114.8594
[13 empty] | C Choked w/ reducers | 5 |  | 762.7749 |  |  | 349.2172 |  |  | 224.0394 |  |  | 84.598 |  |  | 48.7532 |  |  | 34.5641 |  |  | 27.9339 |  |  | 25.355 |  |  | 22.2768 |  |  | 31.824
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 224.0394 |  |  | 84.598 |  |  | 48.7532 |  |  | 34.5641 |  |  | 27.9339 |  |  | 25.355 |  |  | 22.2768 |  |  | 31.824
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 45334.4316 |  | 18000 | 37506.7414 |  | 18000 | 91840.2326 |  | 18000 | 178881.3313 |  | 18000 | 300107.2278 |  | 18000 | 438014.6727 |  | 18000 | 578744.8304 |  | 18000 | 713240.4645 |  | 18000 | 828050.037 |  | 18000 | 970953.7903
[13 empty] | Next iteration flow rate |  |  | 46241.1202 | Abs Value of | Flow this | 37881.8088 | Abs Value of | Flow this | 92758.6349 | Abs Value of | Flow this | 180670.1446 | Abs Value of | Flow this | 303108.3 | Abs Value of | Flow this | 442394.8194 | Abs Value of | Flow this | 584532.2787 | Abs Value of | Flow this | 720372.8691 | Abs Value of | Flow this | 836330.5374 | Abs Value of | Flow this | 980663.3282 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 22.716 |  |  | 44.9196 |  |  | -181.4431 |  |  | -940.4193 |  |  | -2810.6773 |  |  | -6089.3403 |  |  | -10698.1246 |  |  | -16295.0141 |  |  | -21994.6035 |  |  | -30275.106
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.10958 |  |  | 0.21668 |  |  | -0.87524 |  |  | -4.5363 |  |  | -13.558 |  |  | -29.3735 |  |  | -51.6051 |  |  | -78.6031 |  |  | -106.0965 |  |  | -146.0395
[13 empty] | Delta P at this iteration flow rate |  |  | -37.284 |  |  | -15.0804 |  |  | -241.4431 |  |  | -1000.4193 |  |  | -2870.6773 |  |  | -6149.3403 |  |  | -10758.1246 |  |  | -16355.0141 |  |  | -22054.6035 |  |  | -30335.106
[13 empty] | Press drop ratio this iteration |  |  | -1.6413 |  |  | -0.33572 |  |  | 1.3307 |  |  | 1.0638 |  |  | 1.0213 |  |  | 1.0099 |  |  | 1.0056 |  |  | 1.0037 |  |  | 1.0027 |  |  | 1.002
[13 empty] | Expansion factor | 12 |  | 1.8548 |  |  | 1.1748 |  |  | 0.30053 |  |  | 0.43293 |  |  | 0.43868 |  |  | 0.41169 |  |  | 0.36972 |  |  | 0.29665 |  |  | 0.43401 |  |  | 0.11335
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 336.4592 |  |  | 98.7478 |  |  | 56.5216 |  |  | 41.7219 |  |  | 36.2795 |  |  | 38.8538 |  |  | 26.0111 |  |  | 113.6822
[13 empty] | C Choked w/ reducers | 5 |  | 867.8229 |  |  | 359.7196 |  |  | 219.6039 |  |  | 83.5988 |  |  | 48.2394 |  |  | 34.2116 |  |  | 27.6526 |  |  | 25.1012 |  |  | 22.0544 |  |  | 31.507
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 219.6039 |  |  | 83.5988 |  |  | 48.2394 |  |  | 34.2116 |  |  | 27.6526 |  |  | 25.1012 |  |  | 22.0544 |  |  | 31.507
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 46241.1202 |  | 18000 | 37881.8088 |  | 18000 | 92758.6349 |  | 18000 | 180670.1446 |  | 18000 | 303108.3 |  | 18000 | 442394.8194 |  | 18000 | 584532.2787 |  | 18000 | 720372.8691 |  | 18000 | 836330.5374 |  | 18000 | 980663.3282
[13 empty] | Next iteration flow rate |  |  | 47165.9426 | Abs Value of | Flow this | 38260.6269 | Abs Value of | Flow this | 93686.2213 | Abs Value of | Flow this | 182476.8461 | Abs Value of | Flow this | 306139.383 | Abs Value of | Flow this | 446818.7676 | Abs Value of | Flow this | 590377.6015 | Abs Value of | Flow this | 727576.5978 | Abs Value of | Flow this | 844693.8427 | Abs Value of | Flow this | 990469.9615 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 19.9884 |  |  | 44.0089 |  |  | -186.9037 |  |  | -961.1354 |  |  | -2868.9856 |  |  | -6213.5497 |  |  | -10914.9706 |  |  | -16624.3575 |  |  | -22438.5087 |  |  | -30885.4493
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.096419 |  |  | 0.21229 |  |  | -0.90158 |  |  | -4.6363 |  |  | -13.8393 |  |  | -29.9726 |  |  | -52.6511 |  |  | -80.1917 |  |  | -108.2378 |  |  | -148.9837
[13 empty] | Delta P at this iteration flow rate |  |  | -40.0116 |  |  | -15.9911 |  |  | -246.9037 |  |  | -1021.1354 |  |  | -2928.9856 |  |  | -6273.5497 |  |  | -10974.9706 |  |  | -16684.3575 |  |  | -22498.5087 |  |  | -30945.4493
[13 empty] | Press drop ratio this iteration |  |  | -2.0017 |  |  | -0.36336 |  |  | 1.321 |  |  | 1.0624 |  |  | 1.0209 |  |  | 1.0097 |  |  | 1.0055 |  |  | 1.0036 |  |  | 1.0027 |  |  | 1.0019
[13 empty] | Expansion factor | 12 |  | 2.0425 |  |  | 1.1892 |  |  | 0.30561 |  |  | 0.43367 |  |  | 0.43892 |  |  | 0.41181 |  |  | 0.36979 |  |  | 0.2967 |  |  | 0.43404 |  |  | 0.11338
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 325.5975 |  |  | 97.4837 |  |  | 55.9081 |  |  | 41.2893 |  |  | 35.9095 |  |  | 38.4596 |  |  | 25.7503 |  |  | 112.5178
[13 empty] | C Choked w/ reducers | 5 |  | 1005.9687 |  |  | 370.8355 |  |  | 215.3198 |  |  | 82.6149 |  |  | 47.7315 |  |  | 33.863 |  |  | 27.3743 |  |  | 24.8499 |  |  | 21.8343 |  |  | 31.1933
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 215.3198 |  |  | 82.6149 |  |  | 47.7315 |  |  | 33.863 |  |  | 27.3743 |  |  | 24.8499 |  |  | 21.8343 |  |  | 31.1933
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 47165.9426 |  | 18000 | 38260.6269 |  | 18000 | 93686.2213 |  | 18000 | 182476.8461 |  | 18000 | 306139.383 |  | 18000 | 446818.7676 |  | 18000 | 590377.6015 |  | 18000 | 727576.5978 |  | 18000 | 844693.8427 |  | 18000 | 990469.9615
[13 empty] | Next iteration flow rate |  |  | 48109.2615 | Abs Value of | Flow this | 38643.2332 | Abs Value of | Flow this | 94623.0835 | Abs Value of | Flow this | 184301.6145 | Abs Value of | Flow this | 309200.7769 | Abs Value of | Flow this | 451286.9553 | Abs Value of | Flow this | 596281.3775 | Abs Value of | Flow this | 734852.3638 | Abs Value of | Flow this | 853140.7812 | Abs Value of | Flow this | 1000374.6611 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 17.1507 |  |  | 43.0798 |  |  | -192.4741 |  |  | -982.2679 |  |  | -2928.4658 |  |  | -6340.2556 |  |  | -11136.1751 |  |  | -16960.3207 |  |  | -22891.3363 |  |  | -31508.0605
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.082731 |  |  | 0.20781 |  |  | -0.92845 |  |  | -4.7382 |  |  | -14.1262 |  |  | -30.5838 |  |  | -53.7181 |  |  | -81.8123 |  |  | -110.4221 |  |  | -151.987
[13 empty] | Delta P at this iteration flow rate |  |  | -42.8493 |  |  | -16.9202 |  |  | -252.4741 |  |  | -1042.2679 |  |  | -2988.4658 |  |  | -6400.2556 |  |  | -11196.1751 |  |  | -17020.3207 |  |  | -22951.3363 |  |  | -31568.0605
[13 empty] | Press drop ratio this iteration |  |  | -2.4984 |  |  | -0.39276 |  |  | 1.3117 |  |  | 1.0611 |  |  | 1.0205 |  |  | 1.0095 |  |  | 1.0054 |  |  | 1.0035 |  |  | 1.0026 |  |  | 1.0019
[13 empty] | Expansion factor | 12 |  | 2.3012 |  |  | 1.2045 |  |  | 0.31049 |  |  | 0.43438 |  |  | 0.43915 |  |  | 0.41192 |  |  | 0.36986 |  |  | 0.29675 |  |  | 0.43407 |  |  | 0.11341
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 315.4246 |  |  | 96.2423 |  |  | 55.3024 |  |  | 40.8616 |  |  | 35.5435 |  |  | 38.0697 |  |  | 25.4923 |  |  | 111.3661
[13 empty] | C Choked w/ reducers | 5 |  | 1195.8656 |  |  | 382.6212 |  |  | 211.1791 |  |  | 81.6459 |  |  | 47.2297 |  |  | 33.5182 |  |  | 27.0989 |  |  | 24.6013 |  |  | 21.6164 |  |  | 30.8826
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 211.1791 |  |  | 81.6459 |  |  | 47.2297 |  |  | 33.5182 |  |  | 27.0989 |  |  | 24.6013 |  |  | 21.6164 |  |  | 30.8826
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 48109.2615 |  | 18000 | 38643.2332 |  | 18000 | 94623.0835 |  | 18000 | 184301.6145 |  | 18000 | 309200.7769 |  | 18000 | 451286.9553 |  | 18000 | 596281.3775 |  | 18000 | 734852.3638 |  | 18000 | 853140.7812 |  | 18000 | 1000374.6611
[13 empty] | Next iteration flow rate |  |  | 49071.4467 | Abs Value of | Flow this | 39029.6655 | Abs Value of | Flow this | 95569.3143 | Abs Value of | Flow this | 186144.6307 | Abs Value of | Flow this | 312292.7846 | Abs Value of | Flow this | 455799.8248 | Abs Value of | Flow this | 602244.1913 | Abs Value of | Flow this | 742200.8875 | Abs Value of | Flow this | 861672.189 | Abs Value of | Flow this | 1010378.4077 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 14.1983 |  |  | 42.1321 |  |  | -198.1565 |  |  | -1003.8251 |  |  | -2989.1416 |  |  | -6469.5084 |  |  | -11361.8258 |  |  | -17303.0368 |  |  | -23353.2658 |  |  | -32143.1861
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.068489 |  |  | 0.20323 |  |  | -0.95586 |  |  | -4.8422 |  |  | -14.4189 |  |  | -31.2073 |  |  | -54.8066 |  |  | -83.4655 |  |  | -112.6503 |  |  | -155.0507
[13 empty] | Delta P at this iteration flow rate |  |  | -45.8017 |  |  | -17.8679 |  |  | -258.1565 |  |  | -1063.8251 |  |  | -3049.1416 |  |  | -6529.5084 |  |  | -11421.8258 |  |  | -17363.0368 |  |  | -23413.2658 |  |  | -32203.1861
[13 empty] | Press drop ratio this iteration |  |  | -3.2259 |  |  | -0.42409 |  |  | 1.3028 |  |  | 1.0598 |  |  | 1.0201 |  |  | 1.0093 |  |  | 1.0053 |  |  | 1.0035 |  |  | 1.0026 |  |  | 1.0019
[13 empty] | Expansion factor | 12 |  | 2.6801 |  |  | 1.2208 |  |  | 0.31519 |  |  | 0.43508 |  |  | 0.43938 |  |  | 0.41203 |  |  | 0.36993 |  |  | 0.2968 |  |  | 0.4341 |  |  | 0.11345
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 305.8741 |  |  | 95.0232 |  |  | 54.7043 |  |  | 40.4386 |  |  | 35.1815 |  |  | 37.6839 |  |  | 25.2369 |  |  | 110.227
[13 empty] | C Choked w/ reducers | 5 |  | 1473.4268 |  |  | 395.1401 |  |  | 207.1746 |  |  | 80.6915 |  |  | 46.7337 |  |  | 33.177 |  |  | 26.8263 |  |  | 24.3551 |  |  | 21.4007 |  |  | 30.5751
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 207.1746 |  |  | 80.6915 |  |  | 46.7337 |  |  | 33.177 |  |  | 26.8263 |  |  | 24.3551 |  |  | 21.4007 |  |  | 30.5751
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 49071.4467 |  | 18000 | 39029.6655 |  | 18000 | 95569.3143 |  | 18000 | 186144.6307 |  | 18000 | 312292.7846 |  | 18000 | 455799.8248 |  | 18000 | 602244.1913 |  | 18000 | 742200.8875 |  | 18000 | 861672.189 |  | 18000 | 1010378.4077
[13 empty] | Next iteration flow rate |  |  | 50052.8756 | Abs Value of | Flow this | 39419.9622 | Abs Value of | Flow this | 96525.0075 | Abs Value of | Flow this | 188006.077 | Abs Value of | Flow this | 315415.7125 | Abs Value of | Flow this | 460357.8231 | Abs Value of | Flow this | 608266.6332 | Abs Value of | Flow this | 749622.8963 | Abs Value of | Flow this | 870288.9109 | Abs Value of | Flow this | 1020482.1918 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 11.1266 |  |  | 41.1653 |  |  | -203.9531 |  |  | -1025.8156 |  |  | -3051.037 |  |  | -6601.3591 |  |  | -11592.0122 |  |  | -17652.6414 |  |  | -23824.4801 |  |  | -32791.0778
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.053672 |  |  | 0.19857 |  |  | -0.98382 |  |  | -4.9483 |  |  | -14.7174 |  |  | -31.8433 |  |  | -55.917 |  |  | -85.1519 |  |  | -114.9233 |  |  | -158.176
[13 empty] | Delta P at this iteration flow rate |  |  | -48.8734 |  |  | -18.8347 |  |  | -263.9531 |  |  | -1085.8156 |  |  | -3111.037 |  |  | -6661.3591 |  |  | -11652.0122 |  |  | -17712.6414 |  |  | -23884.4801 |  |  | -32851.0778
[13 empty] | Press drop ratio this iteration |  |  | -4.3925 |  |  | -0.45754 |  |  | 1.2942 |  |  | 1.0585 |  |  | 1.0197 |  |  | 1.0091 |  |  | 1.0052 |  |  | 1.0034 |  |  | 1.0025 |  |  | 1.0018
[13 empty] | Expansion factor | 12 |  | 3.2877 |  |  | 1.2382 |  |  | 0.31971 |  |  | 0.43576 |  |  | 0.4396 |  |  | 0.41214 |  |  | 0.36999 |  |  | 0.29685 |  |  | 0.43412 |  |  | 0.11348
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 296.888 |  |  | 93.8255 |  |  | 54.1137 |  |  | 40.0204 |  |  | 34.8233 |  |  | 37.3022 |  |  | 24.9841 |  |  | 109.1002
[13 empty] | C Choked w/ reducers | 5 |  | 1917.7965 |  |  | 408.4643 |  |  | 203.2993 |  |  | 79.7513 |  |  | 46.2435 |  |  | 32.8395 |  |  | 26.5565 |  |  | 24.1115 |  |  | 21.1872 |  |  | 30.2707
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 203.2993 |  |  | 79.7513 |  |  | 46.2435 |  |  | 32.8395 |  |  | 26.5565 |  |  | 24.1115 |  |  | 21.1872 |  |  | 30.2707
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 50052.8756 |  | 18000 | 39419.9622 |  | 18000 | 96525.0075 |  | 18000 | 188006.077 |  | 18000 | 315415.7125 |  | 18000 | 460357.8231 |  | 18000 | 608266.6332 |  | 18000 | 749622.8963 |  | 18000 | 870288.9109 |  | 18000 | 1020482.1918
[13 empty] | Next iteration flow rate |  |  | 51053.9332 | Abs Value of | Flow this | 39814.1618 | Abs Value of | Flow this | 97490.2575 | Abs Value of | Flow this | 189886.1377 | Abs Value of | Flow this | 318569.8696 | Abs Value of | Flow this | 464961.4013 | Abs Value of | Flow this | 614349.2995 | Abs Value of | Flow this | 757119.1253 | Abs Value of | Flow this | 878991.8 | Abs Value of | Flow this | 1030687.0137 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 7.9308 |  |  | 40.1791 |  |  | -209.8661 |  |  | -1048.2481 |  |  | -3114.1764 |  |  | -6735.8601 |  |  | -11826.8252 |  |  | -18009.2731 |  |  | -24305.1657 |  |  | -33451.9921
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.038256 |  |  | 0.19381 |  |  | -1.0123 |  |  | -5.0565 |  |  | -15.022 |  |  | -32.4921 |  |  | -57.0496 |  |  | -86.8722 |  |  | -117.242 |  |  | -161.364
[13 empty] | Delta P at this iteration flow rate |  |  | -52.0692 |  |  | -19.8209 |  |  | -269.8661 |  |  | -1108.2481 |  |  | -3174.1764 |  |  | -6795.8601 |  |  | -11886.8252 |  |  | -18069.2731 |  |  | -24365.1657 |  |  | -33511.9921
[13 empty] | Press drop ratio this iteration |  |  | -6.5655 |  |  | -0.49331 |  |  | 1.2859 |  |  | 1.0572 |  |  | 1.0193 |  |  | 1.0089 |  |  | 1.0051 |  |  | 1.0033 |  |  | 1.0025 |  |  | 1.0018
[13 empty] | Expansion factor | 12 |  | 4.4193 |  |  | 1.2569 |  |  | 0.32407 |  |  | 0.43643 |  |  | 0.43982 |  |  | 0.41224 |  |  | 0.37006 |  |  | 0.29689 |  |  | 0.43415 |  |  | 0.11351
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 288.4155 |  |  | 92.6489 |  |  | 53.5305 |  |  | 39.6069 |  |  | 34.469 |  |  | 36.9245 |  |  | 24.7339 |  |  | 107.9856
[13 empty] | C Choked w/ reducers | 5 |  | 2744.4028 |  |  | 422.675 |  |  | 199.5469 |  |  | 78.8251 |  |  | 45.759 |  |  | 32.5056 |  |  | 26.2895 |  |  | 23.8704 |  |  | 20.9758 |  |  | 29.9694
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 199.5469 |  |  | 78.8251 |  |  | 45.759 |  |  | 32.5056 |  |  | 26.2895 |  |  | 23.8704 |  |  | 20.9758 |  |  | 29.9694
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 51053.9332 |  | 18000 | 39814.1618 |  | 18000 | 97490.2575 |  | 18000 | 189886.1377 |  | 18000 | 318569.8696 |  | 18000 | 464961.4013 |  | 18000 | 614349.2995 |  | 18000 | 757119.1253 |  | 18000 | 878991.8 |  | 18000 | 1030687.0137
[13 empty] | Next iteration flow rate |  |  | 52075.0118 | Abs Value of | Flow this | 40212.3034 | Abs Value of | Flow this | 98465.1601 | Abs Value of | Flow this | 191784.9991 | Abs Value of | Flow this | 321755.5683 | Abs Value of | Flow this | 469611.0153 | Abs Value of | Flow this | 620492.7925 | Abs Value of | Flow this | 764690.3165 | Abs Value of | Flow this | 887781.718 | Abs Value of | Flow this | 1040993.8839 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 4.6059 |  |  | 39.1731 |  |  | -215.8981 |  |  | -1071.1315 |  |  | -3178.585 |  |  | -6873.0645 |  |  | -12066.358 |  |  | -18373.0732 |  |  | -24795.5132 |  |  | -34126.1907
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.022218 |  |  | 0.18896 |  |  | -1.0414 |  |  | -5.1669 |  |  | -15.3327 |  |  | -33.1539 |  |  | -58.2051 |  |  | -88.6271 |  |  | -119.6074 |  |  | -164.6162
[13 empty] | Delta P at this iteration flow rate |  |  | -55.3941 |  |  | -20.8269 |  |  | -275.8981 |  |  | -1131.1315 |  |  | -3238.585 |  |  | -6933.0645 |  |  | -12126.358 |  |  | -18433.0732 |  |  | -24855.5132 |  |  | -34186.1907
[13 empty] | Press drop ratio this iteration |  |  | -12.0268 |  |  | -0.53166 |  |  | 1.2779 |  |  | 1.056 |  |  | 1.0189 |  |  | 1.0087 |  |  | 1.005 |  |  | 1.0033 |  |  | 1.0024 |  |  | 1.0018
[13 empty] | Expansion factor | 12 |  | 7.2637 |  |  | 1.2768 |  |  | 0.32827 |  |  | 0.43708 |  |  | 0.44004 |  |  | 0.41235 |  |  | 0.37012 |  |  | 0.29694 |  |  | 0.43418 |  |  | 0.11354
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 280.4117 |  |  | 91.4926 |  |  | 52.9546 |  |  | 39.198 |  |  | 34.1185 |  |  | 36.5508 |  |  | 24.4862 |  |  | 106.8832
[13 empty] | C Choked w/ reducers | 5 |  | 4820.0402 |  |  | 437.8653 |  |  | 195.9116 |  |  | 77.9125 |  |  | 45.28 |  |  | 32.1753 |  |  | 26.0253 |  |  | 23.6317 |  |  | 20.7666 |  |  | 29.6711
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 195.9116 |  |  | 77.9125 |  |  | 45.28 |  |  | 32.1753 |  |  | 26.0253 |  |  | 23.6317 |  |  | 20.7666 |  |  | 29.6711
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 52075.0118 |  | 18000 | 40212.3034 |  | 18000 | 98465.1601 |  | 18000 | 191784.9991 |  | 18000 | 321755.5683 |  | 18000 | 469611.0153 |  | 18000 | 620492.7925 |  | 18000 | 764690.3165 |  | 18000 | 887781.718 |  | 18000 | 1040993.8839
[13 empty] | Next iteration flow rate |  |  | 53116.5121 | Abs Value of | Flow this | 40614.4265 | Abs Value of | Flow this | 99449.8117 | Abs Value of | Flow this | 193702.8491 | Abs Value of | Flow this | 324973.124 | Abs Value of | Flow this | 474307.1255 | Abs Value of | Flow this | 626697.7204 | Abs Value of | Flow this | 772337.2197 | Abs Value of | Flow this | 896659.5352 | Abs Value of | Flow this | 1051403.8227 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | 1.1467 |  |  | 38.1468 |  |  | -222.0512 |  |  | -1094.4749 |  |  | -3244.2882 |  |  | -7013.0267 |  |  | -12310.7055 |  |  | -18744.1856 |  |  | -25295.7166 |  |  | -34813.9408
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | 0.0055312 |  |  | 0.18401 |  |  | -1.0711 |  |  | -5.2795 |  |  | -15.6496 |  |  | -33.8291 |  |  | -59.3838 |  |  | -90.4173 |  |  | -122.0202 |  |  | -167.9337
[13 empty] | Delta P at this iteration flow rate |  |  | -58.8533 |  |  | -21.8532 |  |  | -282.0512 |  |  | -1154.4749 |  |  | -3304.2882 |  |  | -7073.0267 |  |  | -12370.7055 |  |  | -18804.1856 |  |  | -25355.7166 |  |  | -34873.9408
[13 empty] | Press drop ratio this iteration |  |  | -51.3255 |  |  | -0.57287 |  |  | 1.2702 |  |  | 1.0548 |  |  | 1.0185 |  |  | 1.0086 |  |  | 1.0049 |  |  | 1.0032 |  |  | 1.0024 |  |  | 1.0017
[13 empty] | Expansion factor | 12 |  | 27.7308 |  |  | 1.2983 |  |  | 0.33232 |  |  | 0.43772 |  |  | 0.44025 |  |  | 0.41245 |  |  | 0.37018 |  |  | 0.29698 |  |  | 0.43421 |  |  | 0.11357
[13 empty] | C Non choked w/ reducers | 5 |  | #NUM! |  |  | #NUM! |  |  | 272.8368 |  |  | 90.3562 |  |  | 52.3858 |  |  | 38.7937 |  |  | 33.7717 |  |  | 36.1811 |  |  | 24.2411 |  |  | 105.7926
[13 empty] | C Choked w/ reducers | 5 |  | 19748.1498 |  |  | 454.1414 |  |  | 192.3876 |  |  | 77.0133 |  |  | 44.8067 |  |  | 31.8485 |  |  | 25.7639 |  |  | 23.3955 |  |  | 20.5596 |  |  | 29.3758
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | #NUM! |  |  | #NUM! |  |  | 192.3876 |  |  | 77.0133 |  |  | 44.8067 |  |  | 31.8485 |  |  | 25.7639 |  |  | 23.3955 |  |  | 20.5596 |  |  | 29.3758
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 53116.5121 |  | 18000 | 40614.4265 |  | 18000 | 99449.8117 |  | 18000 | 193702.8491 |  | 18000 | 324973.124 |  | 18000 | 474307.1255 |  | 18000 | 626697.7204 |  | 18000 | 772337.2197 |  | 18000 | 896659.5352 |  | 18000 | 1051403.8227
[13 empty] | Next iteration flow rate |  |  | 54178.8423 | Abs Value of | Flow this | 41020.5707 | Abs Value of | Flow this | 100444.3098 | Abs Value of | Flow this | 195639.8776 | Abs Value of | Flow this | 328222.8552 | Abs Value of | Flow this | 479050.1967 | Abs Value of | Flow this | 632964.6977 | Abs Value of | Flow this | 780060.5919 | Abs Value of | Flow this | 905626.1305 | Abs Value of | Flow this | 1061917.8609 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -2.4523 |  |  | 37.1 |  |  | -228.3281 |  |  | -1118.2874 |  |  | -3311.312 |  |  | -7155.8022 |  |  | -12559.9643 |  |  | -19122.7573 |  |  | -25805.9742 |  |  | -35515.5146
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.011829 |  |  | 0.17896 |  |  | -1.1014 |  |  | -5.3943 |  |  | -15.9729 |  |  | -34.5178 |  |  | -60.5861 |  |  | -92.2434 |  |  | -124.4816 |  |  | -171.318
[13 empty] | Delta P at this iteration flow rate |  |  | -62.4523 |  |  | -22.9 |  |  | -288.3281 |  |  | -1178.2874 |  |  | -3371.312 |  |  | -7215.8022 |  |  | -12619.9643 |  |  | -19182.7573 |  |  | -25865.9742 |  |  | -35575.5146
[13 empty] | Press drop ratio this iteration |  |  | 25.4668 |  |  | -0.61725 |  |  | 1.2628 |  |  | 1.0537 |  |  | 1.0181 |  |  | 1.0084 |  |  | 1.0048 |  |  | 1.0031 |  |  | 1.0023 |  |  | 1.0017
[13 empty] | Expansion factor | 12 |  | -12.2633 |  |  | 1.3214 |  |  | 0.33622 |  |  | 0.43834 |  |  | 0.44045 |  |  | 0.41255 |  |  | 0.37024 |  |  | 0.29703 |  |  | 0.43423 |  |  | 0.1136
[13 empty] | C Non choked w/ reducers | 5 |  | -81.2121 |  |  | #NUM! |  |  | 265.6554 |  |  | 89.2391 |  |  | 51.824 |  |  | 38.3939 |  |  | 33.4287 |  |  | 35.8152 |  |  | 23.9985 |  |  | 104.7138
[13 empty] | C Choked w/ reducers | 5 |  | 9418.6808 |  |  | 471.6258 |  |  | 188.9697 |  |  | 76.1271 |  |  | 44.3387 |  |  | 31.5251 |  |  | 25.5051 |  |  | 23.1616 |  |  | 20.3546 |  |  | 29.0835
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 9418.6808 |  |  | #NUM! |  |  | 188.9697 |  |  | 76.1271 |  |  | 44.3387 |  |  | 31.5251 |  |  | 25.5051 |  |  | 23.1616 |  |  | 20.3546 |  |  | 29.0835
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 54178.8423 |  | 18000 | 41020.5707 |  | 18000 | 100444.3098 |  | 18000 | 195639.8776 |  | 18000 | 328222.8552 |  | 18000 | 479050.1967 |  | 18000 | 632964.6977 |  | 18000 | 780060.5919 |  | 18000 | 905626.1305 |  | 18000 | 1061917.8609
[13 empty] | Next iteration flow rate |  |  | 55262.4191 | Abs Value of | Flow this | 41430.7764 | Abs Value of | Flow this | 101448.7529 | Abs Value of | Flow this | 197596.2764 | Abs Value of | Flow this | 331505.0838 | Abs Value of | Flow this | 483840.6987 | Abs Value of | Flow this | 639294.3446 | Abs Value of | Flow this | 787861.1978 | Abs Value of | Flow this | 914682.3918 | Abs Value of | Flow this | 1072537.0395 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -6.1967 |  |  | 36.032 |  |  | -234.7311 |  |  | -1142.5787 |  |  | -3379.683 |  |  | -7301.4474 |  |  | -12814.2332 |  |  | -19508.9384 |  |  | -26326.4879 |  |  | -36231.1901
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.029891 |  |  | 0.17381 |  |  | -1.1323 |  |  | -5.5115 |  |  | -16.3027 |  |  | -35.2204 |  |  | -61.8127 |  |  | -94.1062 |  |  | -126.9924 |  |  | -174.7702
[13 empty] | Delta P at this iteration flow rate |  |  | -66.1967 |  |  | -23.968 |  |  | -294.7311 |  |  | -1202.5787 |  |  | -3439.683 |  |  | -7361.4474 |  |  | -12874.2332 |  |  | -19568.9384 |  |  | -26386.4879 |  |  | -36291.1901
[13 empty] | Press drop ratio this iteration |  |  | 10.6826 |  |  | -0.66518 |  |  | 1.2556 |  |  | 1.0525 |  |  | 1.0178 |  |  | 1.0082 |  |  | 1.0047 |  |  | 1.0031 |  |  | 1.0023 |  |  | 1.0017
[13 empty] | Expansion factor | 12 |  | -4.5636 |  |  | 1.3464 |  |  | 0.33999 |  |  | 0.43895 |  |  | 0.44065 |  |  | 0.41264 |  |  | 0.3703 |  |  | 0.29707 |  |  | 0.43426 |  |  | 0.11363
[13 empty] | C Non choked w/ reducers | 5 |  | -136.0146 |  |  | #NUM! |  |  | 258.8362 |  |  | 88.1408 |  |  | 51.2692 |  |  | 37.9985 |  |  | 33.0893 |  |  | 35.4532 |  |  | 23.7584 |  |  | 103.6466
[13 empty] | C Choked w/ reducers | 5 |  | 3801.9452 |  |  | 490.4599 |  |  | 185.6531 |  |  | 75.2537 |  |  | 43.8762 |  |  | 31.2052 |  |  | 25.249 |  |  | 22.9302 |  |  | 20.1516 |  |  | 28.7941
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 3801.9452 |  |  | #NUM! |  |  | 185.6531 |  |  | 75.2537 |  |  | 43.8762 |  |  | 31.2052 |  |  | 25.249 |  |  | 22.9302 |  |  | 20.1516 |  |  | 28.7941
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 55262.4191 |  | 18000 | 41430.7764 |  | 18000 | 101448.7529 |  | 18000 | 197596.2764 |  | 18000 | 331505.0838 |  | 18000 | 483840.6987 |  | 18000 | 639294.3446 |  | 18000 | 787861.1978 |  | 18000 | 914682.3918 |  | 18000 | 1072537.0395
[13 empty] | Next iteration flow rate |  |  | 56367.6675 | Abs Value of | Flow this | 41845.0842 | Abs Value of | Flow this | 102463.2405 | Abs Value of | Flow this | 199572.2391 | Abs Value of | Flow this | 334820.1346 | Abs Value of | Flow this | 488679.1057 | Abs Value of | Flow this | 645687.2881 | Abs Value of | Flow this | 795739.8098 | Abs Value of | Flow this | 923829.2157 | Abs Value of | Flow this | 1083262.4099 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -10.0923 |  |  | 34.9427 |  |  | -241.2628 |  |  | -1167.3581 |  |  | -3449.4283 |  |  | -7450.0202 |  |  | -13073.6129 |  |  | -19902.8817 |  |  | -26857.4639 |  |  | -36961.2506
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.048683 |  |  | 0.16855 |  |  | -1.1638 |  |  | -5.631 |  |  | -16.6392 |  |  | -35.937 |  |  | -63.0638 |  |  | -96.0065 |  |  | -129.5537 |  |  | -178.2918
[13 empty] | Delta P at this iteration flow rate |  |  | -70.0923 |  |  | -25.0573 |  |  | -301.2628 |  |  | -1227.3581 |  |  | -3509.4283 |  |  | -7510.0202 |  |  | -13133.6129 |  |  | -19962.8817 |  |  | -26917.4639 |  |  | -37021.2506
[13 empty] | Press drop ratio this iteration |  |  | 6.9451 |  |  | -0.7171 |  |  | 1.2487 |  |  | 1.0514 |  |  | 1.0174 |  |  | 1.0081 |  |  | 1.0046 |  |  | 1.003 |  |  | 1.0022 |  |  | 1.0016
[13 empty] | Expansion factor | 12 |  | -2.6171 |  |  | 1.3734 |  |  | 0.34363 |  |  | 0.43954 |  |  | 0.44085 |  |  | 0.41274 |  |  | 0.37036 |  |  | 0.29711 |  |  | 0.43429 |  |  | 0.11366
[13 empty] | C Non choked w/ reducers | 5 |  | -184.2227 |  |  | #NUM! |  |  | 252.3509 |  |  | 87.0609 |  |  | 50.7211 |  |  | 37.6074 |  |  | 32.7535 |  |  | 35.095 |  |  | 23.5207 |  |  | 102.5909
[13 empty] | C Choked w/ reducers | 5 |  | 2381.079 |  |  | 510.8081 |  |  | 182.4332 |  |  | 74.3929 |  |  | 43.4189 |  |  | 30.8888 |  |  | 24.9955 |  |  | 22.7011 |  |  | 19.9508 |  |  | 28.5076
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 2381.079 |  |  | #NUM! |  |  | 182.4332 |  |  | 74.3929 |  |  | 43.4189 |  |  | 30.8888 |  |  | 24.9955 |  |  | 22.7011 |  |  | 19.9508 |  |  | 28.5076
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 56367.6675 |  | 18000 | 41845.0842 |  | 18000 | 102463.2405 |  | 18000 | 199572.2391 |  | 18000 | 334820.1346 |  | 18000 | 488679.1057 |  | 18000 | 645687.2881 |  | 18000 | 795739.8098 |  | 18000 | 923829.2157 |  | 18000 | 1083262.4099
[13 empty] | Next iteration flow rate |  |  | 57495.0209 | Abs Value of | Flow this | 42263.535 | Abs Value of | Flow this | 103487.8729 | Abs Value of | Flow this | 201567.9615 | Abs Value of | Flow this | 338168.336 | Abs Value of | Flow this | 493565.8968 | Abs Value of | Flow this | 652144.161 | Abs Value of | Flow this | 803697.2079 | Abs Value of | Flow this | 933067.5079 | Abs Value of | Flow this | 1094095.034 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -14.1454 |  |  | 33.8314 |  |  | -247.9259 |  |  | -1192.6356 |  |  | -3520.5754 |  |  | -7601.5792 |  |  | -13338.2061 |  |  | -20304.7432 |  |  | -27399.1126 |  |  | -37705.9854
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.068234 |  |  | 0.16319 |  |  | -1.1959 |  |  | -5.753 |  |  | -16.9824 |  |  | -36.6681 |  |  | -64.3402 |  |  | -97.945 |  |  | -132.1665 |  |  | -181.8842
[13 empty] | Delta P at this iteration flow rate |  |  | -74.1454 |  |  | -26.1686 |  |  | -307.9259 |  |  | -1252.6356 |  |  | -3580.5754 |  |  | -7661.5792 |  |  | -13398.2061 |  |  | -20364.7432 |  |  | -27459.1126 |  |  | -37765.9854
[13 empty] | Press drop ratio this iteration |  |  | 5.2417 |  |  | -0.7735 |  |  | 1.242 |  |  | 1.0503 |  |  | 1.017 |  |  | 1.0079 |  |  | 1.0045 |  |  | 1.003 |  |  | 1.0022 |  |  | 1.0016
[13 empty] | Expansion factor | 12 |  | -1.7299 |  |  | 1.4028 |  |  | 0.34714 |  |  | 0.44013 |  |  | 0.44104 |  |  | 0.41283 |  |  | 0.37042 |  |  | 0.29716 |  |  | 0.43431 |  |  | 0.11369
[13 empty] | C Non choked w/ reducers | 5 |  | -233.4629 |  |  | #NUM! |  |  | 246.1743 |  |  | 85.9988 |  |  | 50.1797 |  |  | 37.2207 |  |  | 32.4212 |  |  | 34.7406 |  |  | 23.2855 |  |  | 101.5466
[13 empty] | C Choked w/ reducers | 5 |  | 1732.8116 |  |  | 532.8628 |  |  | 179.3056 |  |  | 73.5443 |  |  | 42.9669 |  |  | 30.5756 |  |  | 24.7447 |  |  | 22.4743 |  |  | 19.7519 |  |  | 28.224
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1732.8116 |  |  | #NUM! |  |  | 179.3056 |  |  | 73.5443 |  |  | 42.9669 |  |  | 30.5756 |  |  | 24.7447 |  |  | 22.4743 |  |  | 19.7519 |  |  | 28.224
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 57495.0209 |  | 18000 | 42263.535 |  | 18000 | 103487.8729 |  | 18000 | 201567.9615 |  | 18000 | 338168.336 |  | 18000 | 493565.8968 |  | 18000 | 652144.161 |  | 18000 | 803697.2079 |  | 18000 | 933067.5079 |  | 18000 | 1094095.034
[13 empty] | Next iteration flow rate |  |  | 58644.9213 | Abs Value of | Flow this | 42686.1704 | Abs Value of | Flow this | 104522.7516 | Abs Value of | Flow this | 203583.6411 | Abs Value of | Flow this | 341550.0193 | Abs Value of | Flow this | 498501.5557 | Abs Value of | Flow this | 658665.6026 | Abs Value of | Flow this | 811734.18 | Abs Value of | Flow this | 942398.183 | Abs Value of | Flow this | 1105035.9844 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -18.3621 |  |  | 32.6978 |  |  | -254.7228 |  |  | -1218.4212 |  |  | -3593.1526 |  |  | -7756.1846 |  |  | -13608.1177 |  |  | -20714.6822 |  |  | -27951.6484 |  |  | -38465.6893
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.088574 |  |  | 0.15773 |  |  | -1.2287 |  |  | -5.8774 |  |  | -17.3325 |  |  | -37.4139 |  |  | -65.6422 |  |  | -99.9224 |  |  | -134.8318 |  |  | -185.5489
[13 empty] | Delta P at this iteration flow rate |  |  | -78.3621 |  |  | -27.3022 |  |  | -314.7228 |  |  | -1278.4212 |  |  | -3653.1526 |  |  | -7816.1846 |  |  | -13668.1177 |  |  | -20774.6822 |  |  | -28011.6484 |  |  | -38525.6893
[13 empty] | Press drop ratio this iteration |  |  | 4.2676 |  |  | -0.83499 |  |  | 1.2356 |  |  | 1.0492 |  |  | 1.0167 |  |  | 1.0077 |  |  | 1.0044 |  |  | 1.0029 |  |  | 1.0021 |  |  | 1.0016
[13 empty] | Expansion factor | 12 |  | -1.2226 |  |  | 1.4348 |  |  | 0.35054 |  |  | 0.44069 |  |  | 0.44123 |  |  | 0.41293 |  |  | 0.37047 |  |  | 0.2972 |  |  | 0.43433 |  |  | 0.11372
[13 empty] | C Non choked w/ reducers | 5 |  | -287.6677 |  |  | #NUM! |  |  | 240.2835 |  |  | 84.9542 |  |  | 49.6449 |  |  | 36.8383 |  |  | 32.0925 |  |  | 34.3899 |  |  | 23.0527 |  |  | 100.5134
[13 empty] | C Choked w/ reducers | 5 |  | 1361.5775 |  |  | 556.8502 |  |  | 176.2663 |  |  | 72.7078 |  |  | 42.52 |  |  | 30.2658 |  |  | 24.4964 |  |  | 22.2498 |  |  | 19.5551 |  |  | 27.9432
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1361.5775 |  |  | #NUM! |  |  | 176.2663 |  |  | 72.7078 |  |  | 42.52 |  |  | 30.2658 |  |  | 24.4964 |  |  | 22.2498 |  |  | 19.5551 |  |  | 27.9432
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 58644.9213 |  | 18000 | 42686.1704 |  | 18000 | 104522.7516 |  | 18000 | 203583.6411 |  | 18000 | 341550.0193 |  | 18000 | 498501.5557 |  | 18000 | 658665.6026 |  | 18000 | 811734.18 |  | 18000 | 942398.183 |  | 18000 | 1105035.9844
[13 empty] | Next iteration flow rate |  |  | 59817.8197 | Abs Value of | Flow this | 43113.0321 | Abs Value of | Flow this | 105567.9791 | Abs Value of | Flow this | 205619.4776 | Abs Value of | Flow this | 344965.5195 | Abs Value of | Flow this | 503486.5713 | Abs Value of | Flow this | 665252.2586 | Abs Value of | Flow this | 819851.5218 | Abs Value of | Flow this | 951822.1648 | Abs Value of | Flow this | 1116086.3442 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -22.7493 |  |  | 31.5414 |  |  | -261.6563 |  |  | -1244.7251 |  |  | -3667.1886 |  |  | -7913.8975 |  |  | -13883.4545 |  |  | -21132.8609 |  |  | -28515.2901 |  |  | -39240.6633
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.10974 |  |  | 0.15215 |  |  | -1.2622 |  |  | -6.0042 |  |  | -17.6896 |  |  | -38.1747 |  |  | -66.9703 |  |  | -101.9396 |  |  | -137.5506 |  |  | -189.2871
[13 empty] | Delta P at this iteration flow rate |  |  | -82.7493 |  |  | -28.4586 |  |  | -321.6563 |  |  | -1304.7251 |  |  | -3727.1886 |  |  | -7973.8975 |  |  | -13943.4545 |  |  | -21192.8609 |  |  | -28575.2901 |  |  | -39300.6633
[13 empty] | Press drop ratio this iteration |  |  | 3.6374 |  |  | -0.90226 |  |  | 1.2293 |  |  | 1.0482 |  |  | 1.0164 |  |  | 1.0076 |  |  | 1.0043 |  |  | 1.0028 |  |  | 1.0021 |  |  | 1.0015
[13 empty] | Expansion factor | 12 |  | -0.89442 |  |  | 1.4698 |  |  | 0.35382 |  |  | 0.44125 |  |  | 0.44142 |  |  | 0.41302 |  |  | 0.37053 |  |  | 0.29724 |  |  | 0.43436 |  |  | 0.11375
[13 empty] | C Non choked w/ reducers | 5 |  | -350.6596 |  |  | #NUM! |  |  | 234.6581 |  |  | 83.9265 |  |  | 49.1166 |  |  | 36.4601 |  |  | 31.7673 |  |  | 34.0428 |  |  | 22.8222 |  |  | 99.4913
[13 empty] | C Choked w/ reducers | 5 |  | 1120.9812 |  |  | 583.0387 |  |  | 173.3114 |  |  | 71.883 |  |  | 42.0782 |  |  | 29.9593 |  |  | 24.2507 |  |  | 22.0277 |  |  | 19.3603 |  |  | 27.6653
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 1120.9812 |  |  | #NUM! |  |  | 173.3114 |  |  | 71.883 |  |  | 42.0782 |  |  | 29.9593 |  |  | 24.2507 |  |  | 22.0277 |  |  | 19.3603 |  |  | 27.6653
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 59817.8197 |  | 18000 | 43113.0321 |  | 18000 | 105567.9791 |  | 18000 | 205619.4776 |  | 18000 | 344965.5195 |  | 18000 | 503486.5713 |  | 18000 | 665252.2586 |  | 18000 | 819851.5218 |  | 18000 | 951822.1648 |  | 18000 | 1116086.3442
[13 empty] | Next iteration flow rate |  |  | 61014.1761 | Abs Value of | Flow this | 43544.1624 | Abs Value of | Flow this | 106623.6589 | Abs Value of | Flow this | 207675.6723 | Abs Value of | Flow this | 348415.1747 | Abs Value of | Flow this | 508521.437 | Abs Value of | Flow this | 671904.7812 | Abs Value of | Flow this | 828050.037 | Abs Value of | Flow this | 961340.3865 | Abs Value of | Flow this | 1127247.2077 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -27.3136 |  |  | 30.3617 |  |  | -268.7293 |  |  | -1271.5577 |  |  | -3742.7127 |  |  | -8074.7805 |  |  | -14164.3256 |  |  | -21559.445 |  |  | -29090.2611 |  |  | -40031.2143
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.13175 |  |  | 0.14646 |  |  | -1.2963 |  |  | -6.1337 |  |  | -18.0539 |  |  | -38.9507 |  |  | -68.3252 |  |  | -103.9974 |  |  | -140.3241 |  |  | -193.1006
[13 empty] | Delta P at this iteration flow rate |  |  | -87.3136 |  |  | -29.6383 |  |  | -328.7293 |  |  | -1331.5577 |  |  | -3802.7127 |  |  | -8134.7805 |  |  | -14224.3256 |  |  | -21619.445 |  |  | -29150.2611 |  |  | -40091.2143
[13 empty] | Press drop ratio this iteration |  |  | 3.1967 |  |  | -0.97617 |  |  | 1.2233 |  |  | 1.0472 |  |  | 1.016 |  |  | 1.0074 |  |  | 1.0042 |  |  | 1.0028 |  |  | 1.0021 |  |  | 1.0015
[13 empty] | Expansion factor | 12 |  | -0.66487 |  |  | 1.5083 |  |  | 0.35699 |  |  | 0.44179 |  |  | 0.4416 |  |  | 0.4131 |  |  | 0.37058 |  |  | 0.29728 |  |  | 0.43438 |  |  | 0.11377
[13 empty] | C Non choked w/ reducers | 5 |  | -427.4857 |  |  | #NUM! |  |  | 229.2796 |  |  | 82.9154 |  |  | 48.5947 |  |  | 36.086 |  |  | 31.4455 |  |  | 33.6994 |  |  | 22.5941 |  |  | 98.4801
[13 empty] | C Choked w/ reducers | 5 |  | 952.3275 |  |  | 611.7485 |  |  | 170.4374 |  |  | 71.0698 |  |  | 41.6414 |  |  | 29.656 |  |  | 24.0075 |  |  | 21.8077 |  |  | 19.1674 |  |  | 27.3901
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 952.3275 |  |  | #NUM! |  |  | 170.4374 |  |  | 71.0698 |  |  | 41.6414 |  |  | 29.656 |  |  | 24.0075 |  |  | 21.8077 |  |  | 19.1674 |  |  | 27.3901
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 61014.1761 |  | 18000 | 43544.1624 |  | 18000 | 106623.6589 |  | 18000 | 207675.6723 |  | 18000 | 348415.1747 |  | 18000 | 508521.437 |  | 18000 | 671904.7812 |  | 18000 | 828050.037 |  | 18000 | 961340.3865 |  | 18000 | 1127247.2077
[13 empty] | Next iteration flow rate |  |  | 62234.4596 | Abs Value of | Flow this | 43979.604 | Abs Value of | Flow this | 107689.8955 | Abs Value of | Flow this | 209752.4291 | Abs Value of | Flow this | 351899.3265 | Abs Value of | Flow this | 513606.6514 | Abs Value of | Flow this | 678623.829 | Abs Value of | Flow this | 836330.5374 | Abs Value of | Flow this | 970953.7903 | Abs Value of | Flow this | 1138519.6797 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -32.0624 |  |  | 29.1584 |  |  | -275.9444 |  |  | -1298.9297 |  |  | -3819.7549 |  |  | -8238.8972 |  |  | -14450.8421 |  |  | -21994.6035 |  |  | -29676.789 |  |  | -40837.6553
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.15466 |  |  | 0.14065 |  |  | -1.3311 |  |  | -6.2657 |  |  | -18.4255 |  |  | -39.7424 |  |  | -69.7072 |  |  | -106.0965 |  |  | -143.1534 |  |  | -196.9906
[13 empty] | Delta P at this iteration flow rate |  |  | -92.0624 |  |  | -30.8416 |  |  | -335.9444 |  |  | -1358.9297 |  |  | -3879.7549 |  |  | -8298.8972 |  |  | -14510.8421 |  |  | -22054.6035 |  |  | -29736.789 |  |  | -40897.6553
[13 empty] | Press drop ratio this iteration |  |  | 2.8714 |  |  | -1.0577 |  |  | 1.2174 |  |  | 1.0462 |  |  | 1.0157 |  |  | 1.0073 |  |  | 1.0042 |  |  | 1.0027 |  |  | 1.002 |  |  | 1.0015
[13 empty] | Expansion factor | 12 |  | -0.49543 |  |  | 1.5507 |  |  | 0.36006 |  |  | 0.44232 |  |  | 0.44178 |  |  | 0.41319 |  |  | 0.37063 |  |  | 0.29732 |  |  | 0.43441 |  |  | 0.1138
[13 empty] | C Non choked w/ reducers | 5 |  | -525.9854 |  |  | #NUM! |  |  | 224.1309 |  |  | 81.9205 |  |  | 48.079 |  |  | 35.716 |  |  | 31.1272 |  |  | 33.3596 |  |  | 22.3683 |  |  | 97.4797
[13 empty] | C Choked w/ reducers | 5 |  | 827.5036 |  |  | 643.3651 |  |  | 167.6408 |  |  | 70.2679 |  |  | 41.2095 |  |  | 29.3559 |  |  | 23.7669 |  |  | 21.59 |  |  | 18.9764 |  |  | 27.1177
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 827.5036 |  |  | #NUM! |  |  | 167.6408 |  |  | 70.2679 |  |  | 41.2095 |  |  | 29.3559 |  |  | 23.7669 |  |  | 21.59 |  |  | 18.9764 |  |  | 27.1177
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 62234.4596 |  | 18000 | 43979.604 |  | 18000 | 107689.8955 |  | 18000 | 209752.4291 |  | 18000 | 351899.3265 |  | 18000 | 513606.6514 |  | 18000 | 678623.829 |  | 18000 | 836330.5374 |  | 18000 | 970953.7903 |  | 18000 | 1138519.6797
[13 empty] | Next iteration flow rate |  |  | 63479.1488 | Abs Value of | Flow this | 44419.4001 | Abs Value of | Flow this | 108766.7944 | Abs Value of | Flow this | 211849.9533 | Abs Value of | Flow this | 355418.3197 | Abs Value of | Flow this | 518742.7179 | Abs Value of | Flow this | 685410.0673 | Abs Value of | Flow this | 844693.8427 | Abs Value of | Flow this | 980663.3282 | Abs Value of | Flow this | 1149904.8765 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -37.003 |  |  | 27.9308 |  |  | -283.3045 |  |  | -1326.8518 |  |  | -3898.3456 |  |  | -8406.3126 |  |  | -14743.1177 |  |  | -22438.5087 |  |  | -30275.106 |  |  | -41660.3058
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.17849 |  |  | 0.13473 |  |  | -1.3666 |  |  | -6.4004 |  |  | -18.8046 |  |  | -40.55 |  |  | -71.1171 |  |  | -108.2378 |  |  | -146.0395 |  |  | -200.9589
[13 empty] | Delta P at this iteration flow rate |  |  | -97.003 |  |  | -32.0692 |  |  | -343.3045 |  |  | -1386.8518 |  |  | -3958.3456 |  |  | -8466.3126 |  |  | -14803.1177 |  |  | -22498.5087 |  |  | -30335.106 |  |  | -41720.3058
[13 empty] | Press drop ratio this iteration |  |  | 2.6215 |  |  | -1.1482 |  |  | 1.2118 |  |  | 1.0452 |  |  | 1.0154 |  |  | 1.0071 |  |  | 1.0041 |  |  | 1.0027 |  |  | 1.002 |  |  | 1.0014
[13 empty] | Expansion factor | 12 |  | -0.3653 |  |  | 1.5978 |  |  | 0.36303 |  |  | 0.44284 |  |  | 0.44195 |  |  | 0.41327 |  |  | 0.37069 |  |  | 0.29735 |  |  | 0.43443 |  |  | 0.11382
[13 empty] | C Non choked w/ reducers | 5 |  | -659.8359 |  |  | #NUM! |  |  | 219.1968 |  |  | 80.9414 |  |  | 47.5695 |  |  | 35.3501 |  |  | 30.8122 |  |  | 33.0233 |  |  | 22.1448 |  |  | 96.49
[13 empty] | C Choked w/ reducers | 5 |  | 731.3561 |  |  | 678.357 |  |  | 164.9184 |  |  | 69.477 |  |  | 40.7825 |  |  | 29.059 |  |  | 23.5286 |  |  | 21.3745 |  |  | 18.7874 |  |  | 26.8481
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 731.3561 |  |  | #NUM! |  |  | 164.9184 |  |  | 69.477 |  |  | 40.7825 |  |  | 29.059 |  |  | 23.5286 |  |  | 21.3745 |  |  | 18.7874 |  |  | 26.8481
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 63479.1488 |  | 18000 | 44419.4001 |  | 18000 | 108766.7944 |  | 18000 | 211849.9533 |  | 18000 | 355418.3197 |  | 18000 | 518742.7179 |  | 18000 | 685410.0673 |  | 18000 | 844693.8427 |  | 18000 | 980663.3282 |  | 18000 | 1149904.8765
[13 empty] | Next iteration flow rate |  |  | 64748.7318 | Abs Value of | Flow this | 44863.5941 | Abs Value of | Flow this | 109854.4624 | Abs Value of | Flow this | 213968.4529 | Abs Value of | Flow this | 358972.5029 | Abs Value of | Flow this | 523930.1451 | Abs Value of | Flow this | 692264.1679 | Abs Value of | Flow this | 853140.7812 | Abs Value of | Flow this | 990469.9615 | Abs Value of | Flow this | 1161403.9253 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -42.1432 |  |  | 26.6786 |  |  | -290.8125 |  |  | -1355.3351 |  |  | -3978.5159 |  |  | -8577.0931 |  |  | -15041.268 |  |  | -22891.3363 |  |  | -30885.4493 |  |  | -42499.4916
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.20329 |  |  | 0.12869 |  |  | -1.4028 |  |  | -6.5378 |  |  | -19.1914 |  |  | -41.3738 |  |  | -72.5553 |  |  | -110.4221 |  |  | -148.9837 |  |  | -205.0069
[13 empty] | Delta P at this iteration flow rate |  |  | -102.1432 |  |  | -33.3214 |  |  | -350.8125 |  |  | -1415.3351 |  |  | -4038.5159 |  |  | -8637.0931 |  |  | -15101.268 |  |  | -22951.3363 |  |  | -30945.4493 |  |  | -42559.4916
[13 empty] | Press drop ratio this iteration |  |  | 2.4237 |  |  | -1.249 |  |  | 1.2063 |  |  | 1.0443 |  |  | 1.0151 |  |  | 1.007 |  |  | 1.004 |  |  | 1.0026 |  |  | 1.0019 |  |  | 1.0014
[13 empty] | Expansion factor | 12 |  | -0.26229 |  |  | 1.6503 |  |  | 0.3659 |  |  | 0.44334 |  |  | 0.44212 |  |  | 0.41336 |  |  | 0.37074 |  |  | 0.29739 |  |  | 0.43445 |  |  | 0.11385
[13 empty] | C Non choked w/ reducers | 5 |  | -855.9248 |  |  | #NUM! |  |  | 214.4634 |  |  | 79.9777 |  |  | 47.0661 |  |  | 34.9881 |  |  | 30.5005 |  |  | 32.6906 |  |  | 21.9235 |  |  | 95.5108
[13 empty] | C Choked w/ reducers | 5 |  | 654.9955 |  |  | 717.2991 |  |  | 162.2672 |  |  | 68.6971 |  |  | 40.3603 |  |  | 28.7652 |  |  | 23.2929 |  |  | 21.1612 |  |  | 18.6003 |  |  | 26.5811
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 654.9955 |  |  | #NUM! |  |  | 162.2672 |  |  | 68.6971 |  |  | 40.3603 |  |  | 28.7652 |  |  | 23.2929 |  |  | 21.1612 |  |  | 18.6003 |  |  | 26.5811
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 64748.7318 |  | 18000 | 44863.5941 |  | 18000 | 109854.4624 |  | 18000 | 213968.4529 |  | 18000 | 358972.5029 |  | 18000 | 523930.1451 |  | 18000 | 692264.1679 |  | 18000 | 853140.7812 |  | 18000 | 990469.9615 |  | 18000 | 1161403.9253
[13 empty] | Next iteration flow rate |  |  | 66043.7064 | Abs Value of | Flow this | 45312.23 | Abs Value of | Flow this | 110953.007 | Abs Value of | Flow this | 216108.1374 | Abs Value of | Flow this | 362562.228 | Abs Value of | Flow this | 529169.4465 | Abs Value of | Flow this | 699186.8096 | Abs Value of | Flow this | 861672.189 | Abs Value of | Flow this | 1000374.6611 | Abs Value of | Flow this | 1173017.9645 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -47.4911 |  |  | 25.4012 |  |  | -298.4715 |  |  | -1384.391 |  |  | -4060.2977 |  |  | -8751.3063 |  |  | -15345.4111 |  |  | -23353.2658 |  |  | -31508.0605 |  |  | -43355.545
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.22909 |  |  | 0.12253 |  |  | -1.4398 |  |  | -6.678 |  |  | -19.5859 |  |  | -42.2141 |  |  | -74.0224 |  |  | -112.6503 |  |  | -151.987 |  |  | -209.1363
[13 empty] | Delta P at this iteration flow rate |  |  | -107.4911 |  |  | -34.5988 |  |  | -358.4715 |  |  | -1444.391 |  |  | -4120.2977 |  |  | -8811.3063 |  |  | -15405.4111 |  |  | -23413.2658 |  |  | -31568.0605 |  |  | -43415.545
[13 empty] | Press drop ratio this iteration |  |  | 2.2634 |  |  | -1.3621 |  |  | 1.201 |  |  | 1.0433 |  |  | 1.0148 |  |  | 1.0069 |  |  | 1.0039 |  |  | 1.0026 |  |  | 1.0019 |  |  | 1.0014
[13 empty] | Expansion factor | 12 |  | -0.1788 |  |  | 1.7092 |  |  | 0.36868 |  |  | 0.44384 |  |  | 0.44229 |  |  | 0.41344 |  |  | 0.37079 |  |  | 0.29743 |  |  | 0.43447 |  |  | 0.11387
[13 empty] | C Non choked w/ reducers | 5 |  | -1176.0908 |  |  | #NUM! |  |  | 209.9178 |  |  | 79.029 |  |  | 46.5686 |  |  | 34.6301 |  |  | 30.1921 |  |  | 32.3613 |  |  | 21.7046 |  |  | 94.5421
[13 empty] | C Choked w/ reducers | 5 |  | 592.8624 |  |  | 760.9047 |  |  | 159.6844 |  |  | 67.9278 |  |  | 39.9429 |  |  | 28.4745 |  |  | 23.0595 |  |  | 20.9501 |  |  | 18.4151 |  |  | 26.3168
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 592.8624 |  |  | #NUM! |  |  | 159.6844 |  |  | 67.9278 |  |  | 39.9429 |  |  | 28.4745 |  |  | 23.0595 |  |  | 20.9501 |  |  | 18.4151 |  |  | 26.3168
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 66043.7064 |  | 18000 | 45312.23 |  | 18000 | 110953.007 |  | 18000 | 216108.1374 |  | 18000 | 362562.228 |  | 18000 | 529169.4465 |  | 18000 | 699186.8096 |  | 18000 | 861672.189 |  | 18000 | 1000374.6611 |  | 18000 | 1173017.9645
[13 empty] | Next iteration flow rate |  |  | 67364.5806 | Abs Value of | Flow this | 45765.3523 | Abs Value of | Flow this | 112062.5371 | Abs Value of | Flow this | 218269.2188 | Abs Value of | Flow this | 366187.8502 | Abs Value of | Flow this | 534461.141 | Abs Value of | Flow this | 706178.6777 | Abs Value of | Flow this | 870288.9109 | Abs Value of | Flow this | 1010378.4077 | Abs Value of | Flow this | 1184748.1442 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -53.0551 |  |  | 24.0982 |  |  | -306.2844 |  |  | -1414.0309 |  |  | -4143.7233 |  |  | -8929.0212 |  |  | -15655.6675 |  |  | -23824.4801 |  |  | -32143.1861 |  |  | -44228.8051
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.25592 |  |  | 0.11624 |  |  | -1.4774 |  |  | -6.8209 |  |  | -19.9883 |  |  | -43.0714 |  |  | -75.519 |  |  | -114.9233 |  |  | -155.0507 |  |  | -213.3487
[13 empty] | Delta P at this iteration flow rate |  |  | -113.0551 |  |  | -35.9018 |  |  | -366.2844 |  |  | -1474.0309 |  |  | -4203.7233 |  |  | -8989.0212 |  |  | -15715.6675 |  |  | -23884.4801 |  |  | -32203.1861 |  |  | -44288.8051
[13 empty] | Press drop ratio this iteration |  |  | 2.1309 |  |  | -1.4898 |  |  | 1.1959 |  |  | 1.0424 |  |  | 1.0145 |  |  | 1.0067 |  |  | 1.0038 |  |  | 1.0025 |  |  | 1.0019 |  |  | 1.0014
[13 empty] | Expansion factor | 12 |  | -0.10979 |  |  | 1.7757 |  |  | 0.37138 |  |  | 0.44432 |  |  | 0.44245 |  |  | 0.41352 |  |  | 0.37083 |  |  | 0.29746 |  |  | 0.43449 |  |  | 0.1139
[13 empty] | C Non choked w/ reducers | 5 |  | -1802.2328 |  |  | #NUM! |  |  | 205.5485 |  |  | 78.095 |  |  | 46.0771 |  |  | 34.276 |  |  | 29.8869 |  |  | 32.0354 |  |  | 21.4878 |  |  | 93.5836
[13 empty] | C Choked w/ reducers | 5 |  | 541.3021 |  |  | 810.0696 |  |  | 157.1672 |  |  | 67.169 |  |  | 39.5301 |  |  | 28.1868 |  |  | 22.8286 |  |  | 20.7411 |  |  | 18.2317 |  |  | 26.0552
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 541.3021 |  |  | #NUM! |  |  | 157.1672 |  |  | 67.169 |  |  | 39.5301 |  |  | 28.1868 |  |  | 22.8286 |  |  | 20.7411 |  |  | 18.2317 |  |  | 26.0552
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 67364.5806 |  | 18000 | 45765.3523 |  | 18000 | 112062.5371 |  | 18000 | 218269.2188 |  | 18000 | 366187.8502 |  | 18000 | 534461.141 |  | 18000 | 706178.6777 |  | 18000 | 870288.9109 |  | 18000 | 1010378.4077 |  | 18000 | 1184748.1442
[13 empty] | Next iteration flow rate |  |  | 68711.8722 | Abs Value of | Flow this | 46223.0059 | Abs Value of | Flow this | 113183.1624 | Abs Value of | Flow this | 220451.911 | Abs Value of | Flow this | 369849.7287 | Abs Value of | Flow this | 539805.7524 | Abs Value of | Flow this | 713240.4645 | Abs Value of | Flow this | 878991.8 | Abs Value of | Flow this | 1020482.1918 | Abs Value of | Flow this | 1196595.6256 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -58.8438 |  |  | 22.7689 |  |  | -314.2543 |  |  | -1444.2665 |  |  | -4228.8258 |  |  | -9110.3082 |  |  | -15972.16 |  |  | -24305.1657 |  |  | -32791.0778 |  |  | -45119.6177
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.28385 |  |  | 0.10983 |  |  | -1.5159 |  |  | -6.9668 |  |  | -20.3988 |  |  | -43.9458 |  |  | -77.0457 |  |  | -117.242 |  |  | -158.176 |  |  | -217.6458
[13 empty] | Delta P at this iteration flow rate |  |  | -118.8438 |  |  | -37.2311 |  |  | -374.2543 |  |  | -1504.2665 |  |  | -4288.8258 |  |  | -9170.3082 |  |  | -16032.16 |  |  | -24365.1657 |  |  | -32851.0778 |  |  | -45179.6177
[13 empty] | Press drop ratio this iteration |  |  | 2.0196 |  |  | -1.6352 |  |  | 1.1909 |  |  | 1.0415 |  |  | 1.0142 |  |  | 1.0066 |  |  | 1.0038 |  |  | 1.0025 |  |  | 1.0018 |  |  | 1.0013
[13 empty] | Expansion factor | 12 |  | -0.051852 |  |  | 1.8514 |  |  | 0.37399 |  |  | 0.4448 |  |  | 0.44261 |  |  | 0.4136 |  |  | 0.37088 |  |  | 0.2975 |  |  | 0.43451 |  |  | 0.11392
[13 empty] | C Non choked w/ reducers | 5 |  | -3604.8822 |  |  | #NUM! |  |  | 201.3446 |  |  | 77.1754 |  |  | 45.5914 |  |  | 33.9258 |  |  | 29.585 |  |  | 31.7129 |  |  | 21.2732 |  |  | 92.6352
[13 empty] | C Choked w/ reducers | 5 |  | 497.8128 |  |  | 865.9353 |  |  | 154.713 |  |  | 66.4205 |  |  | 39.1219 |  |  | 27.9022 |  |  | 22.6 |  |  | 20.5342 |  |  | 18.0502 |  |  | 25.7962
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 497.8128 |  |  | #NUM! |  |  | 154.713 |  |  | 66.4205 |  |  | 39.1219 |  |  | 27.9022 |  |  | 22.6 |  |  | 20.5342 |  |  | 18.0502 |  |  | 25.7962
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 68711.8722 |  | 18000 | 46223.0059 |  | 18000 | 113183.1624 |  | 18000 | 220451.911 |  | 18000 | 369849.7287 |  | 18000 | 539805.7524 |  | 18000 | 713240.4645 |  | 18000 | 878991.8 |  | 18000 | 1020482.1918 |  | 18000 | 1196595.6256
[13 empty] | Next iteration flow rate |  |  | 70086.1096 | Abs Value of | Flow this | 46685.2359 | Abs Value of | Flow this | 114314.9941 | Abs Value of | Flow this | 222656.4301 | Abs Value of | Flow this | 373548.226 | Abs Value of | Flow this | 545203.8099 | Abs Value of | Flow this | 720372.8691 | Abs Value of | Flow this | 887781.718 | Abs Value of | Flow this | 1030687.0137 | Abs Value of | Flow this | 1208561.5819 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -64.8664 |  |  | 21.4129 |  |  | -322.3844 |  |  | -1475.1099 |  |  | -4315.6388 |  |  | -9295.239 |  |  | -16295.0141 |  |  | -24795.5132 |  |  | -33451.9921 |  |  | -46028.3356
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.3129 |  |  | 0.10329 |  |  | -1.5551 |  |  | -7.1156 |  |  | -20.8176 |  |  | -44.8379 |  |  | -78.6031 |  |  | -119.6074 |  |  | -161.364 |  |  | -222.0292
[13 empty] | Delta P at this iteration flow rate |  |  | -124.8664 |  |  | -38.5871 |  |  | -382.3844 |  |  | -1535.1099 |  |  | -4375.6388 |  |  | -9355.239 |  |  | -16355.0141 |  |  | -24855.5132 |  |  | -33511.9921 |  |  | -46088.3356
[13 empty] | Press drop ratio this iteration |  |  | 1.925 |  |  | -1.802 |  |  | 1.1861 |  |  | 1.0407 |  |  | 1.0139 |  |  | 1.0065 |  |  | 1.0037 |  |  | 1.0024 |  |  | 1.0018 |  |  | 1.0013
[13 empty] | Expansion factor | 12 |  | -0.0025465 |  |  | 1.9383 |  |  | 0.37652 |  |  | 0.44526 |  |  | 0.44277 |  |  | 0.41367 |  |  | 0.37093 |  |  | 0.29753 |  |  | 0.43453 |  |  | 0.11395
[13 empty] | C Non choked w/ reducers | 5 |  | -69569.7445 |  |  | #NUM! |  |  | 197.2963 |  |  | 76.2698 |  |  | 45.1114 |  |  | 33.5793 |  |  | 29.2862 |  |  | 31.3938 |  |  | 21.0609 |  |  | 91.697
[13 empty] | C Choked w/ reducers | 5 |  | 460.6247 |  |  | 929.9783 |  |  | 152.3194 |  |  | 65.682 |  |  | 38.7183 |  |  | 27.6206 |  |  | 22.3737 |  |  | 20.3294 |  |  | 17.8706 |  |  | 25.5398
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 460.6247 |  |  | #NUM! |  |  | 152.3194 |  |  | 65.682 |  |  | 38.7183 |  |  | 27.6206 |  |  | 22.3737 |  |  | 20.3294 |  |  | 17.8706 |  |  | 25.5398
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 70086.1096 |  | 18000 | 46685.2359 |  | 18000 | 114314.9941 |  | 18000 | 222656.4301 |  | 18000 | 373548.226 |  | 18000 | 545203.8099 |  | 18000 | 720372.8691 |  | 18000 | 887781.718 |  | 18000 | 1030687.0137 |  | 18000 | 1208561.5819
[13 empty] | Next iteration flow rate |  |  | 71487.8318 | Abs Value of | Flow this | 47152.0883 | Abs Value of | Flow this | 115458.144 | Abs Value of | Flow this | 224882.9944 | Abs Value of | Flow this | 377283.7083 | Abs Value of | Flow this | 550655.848 | Abs Value of | Flow this | 727576.5978 | Abs Value of | Flow this | 896659.5352 | Abs Value of | Flow this | 1040993.8839 | Abs Value of | Flow this | 1220647.1977 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -71.1323 |  |  | 20.0297 |  |  | -330.678 |  |  | -1506.5732 |  |  | -4404.1968 |  |  | -9483.8869 |  |  | -16624.3575 |  |  | -25295.7166 |  |  | -34126.1907 |  |  | -46955.3188
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.34312 |  |  | 0.096618 |  |  | -1.5951 |  |  | -7.2673 |  |  | -21.2447 |  |  | -45.7479 |  |  | -80.1917 |  |  | -122.0202 |  |  | -164.6162 |  |  | -226.5007
[13 empty] | Delta P at this iteration flow rate |  |  | -131.1323 |  |  | -39.9703 |  |  | -390.678 |  |  | -1566.5732 |  |  | -4464.1968 |  |  | -9543.8869 |  |  | -16684.3575 |  |  | -25355.7166 |  |  | -34186.1907 |  |  | -47015.3188
[13 empty] | Press drop ratio this iteration |  |  | 1.8435 |  |  | -1.9956 |  |  | 1.1814 |  |  | 1.0398 |  |  | 1.0136 |  |  | 1.0063 |  |  | 1.0036 |  |  | 1.0024 |  |  | 1.0018 |  |  | 1.0013
[13 empty] | Expansion factor | 12 |  | 0.039889 |  |  | 2.0391 |  |  | 0.37898 |  |  | 0.44571 |  |  | 0.44292 |  |  | 0.41375 |  |  | 0.37097 |  |  | 0.29756 |  |  | 0.43455 |  |  | 0.11397
[13 empty] | C Non choked w/ reducers | 5 |  | 4221.3727 |  |  | #NUM! |  |  | 193.3947 |  |  | 75.3779 |  |  | 44.637 |  |  | 33.2366 |  |  | 28.9906 |  |  | 31.078 |  |  | 20.8506 |  |  | 90.7686
[13 empty] | C Choked w/ reducers | 5 |  | 428.4502 |  |  | 1004.1435 |  |  | 149.9842 |  |  | 64.9534 |  |  | 38.3192 |  |  | 27.3419 |  |  | 22.1498 |  |  | 20.1267 |  |  | 17.6927 |  |  | 25.2859
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 428.4502 |  |  | #NUM! |  |  | 149.9842 |  |  | 64.9534 |  |  | 38.3192 |  |  | 27.3419 |  |  | 22.1498 |  |  | 20.1267 |  |  | 17.6927 |  |  | 25.2859
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 71487.8318 |  | 18000 | 47152.0883 |  | 18000 | 115458.144 |  | 18000 | 224882.9944 |  | 18000 | 377283.7083 |  | 18000 | 550655.848 |  | 18000 | 727576.5978 |  | 18000 | 896659.5352 |  | 18000 | 1040993.8839 |  | 18000 | 1220647.1977
[13 empty] | Next iteration flow rate |  |  | 72917.5885 | Abs Value of | Flow this | 47623.6092 | Abs Value of | Flow this | 116612.7255 | Abs Value of | Flow this | 227131.8243 | Abs Value of | Flow this | 381056.5454 | Abs Value of | Flow this | 556162.4065 | Abs Value of | Flow this | 734852.3638 | Abs Value of | Flow this | 905626.1305 | Abs Value of | Flow this | 1051403.8227 | Abs Value of | Flow this | 1232853.6697 | Abs Value of | Flow this
[17 empty] | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration |  | C_h - C this iteration | iteration
[13 empty] | P1 at this iteration flow rate |  |  | -77.6513 |  |  | 18.6187 |  |  | -339.1383 |  |  | -1538.669 |  |  | -4494.5348 |  |  | -9676.3267 |  |  | -16960.3207 |  |  | -25805.9742 |  |  | -34813.9408 |  |  | -47900.9343
[13 empty] | P2 at this iteration flow rate |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60 |  |  | 60
[13 empty] | Density at this iteration |  |  | -0.37457 |  |  | 0.089812 |  |  | -1.6359 |  |  | -7.4222 |  |  | -21.6805 |  |  | -46.6762 |  |  | -81.8123 |  |  | -124.4816 |  |  | -167.9337 |  |  | -231.0621
[13 empty] | Delta P at this iteration flow rate |  |  | -137.6513 |  |  | -41.3813 |  |  | -399.1383 |  |  | -1598.669 |  |  | -4554.5348 |  |  | -9736.3267 |  |  | -17020.3207 |  |  | -25865.9742 |  |  | -34873.9408 |  |  | -47960.9343
[13 empty] | Press drop ratio this iteration |  |  | 1.7727 |  |  | -2.2226 |  |  | 1.1769 |  |  | 1.039 |  |  | 1.0133 |  |  | 1.0062 |  |  | 1.0035 |  |  | 1.0023 |  |  | 1.0017 |  |  | 1.0013
[13 empty] | Expansion factor | 12 |  | 0.076769 |  |  | 2.1573 |  |  | 0.38136 |  |  | 0.44616 |  |  | 0.44307 |  |  | 0.41382 |  |  | 0.37102 |  |  | 0.2976 |  |  | 0.43457 |  |  | 0.11399
[13 empty] | C Non choked w/ reducers | 5 |  | 2089.9705 |  |  | #NUM! |  |  | 189.6312 |  |  | 74.4994 |  |  | 44.1682 |  |  | 32.8976 |  |  | 28.698 |  |  | 30.7654 |  |  | 20.6426 |  |  | 89.85
[13 empty] | C Choked w/ reducers | 5 |  | 400.3302 |  |  | 1091.0457 |  |  | 147.7051 |  |  | 64.2345 |  |  | 37.9245 |  |  | 27.0661 |  |  | 21.9281 |  |  | 19.926 |  |  | 17.5166 |  |  | 25.0346
[13 empty] | Choked pressure drop ratio w/ reducers (xchoked) | 10 |  | 0.64003 |  |  | 0.64018 |  |  | 0.63414 |  |  | 0.62532 |  |  | 0.60651 |  |  | 0.57218 |  |  | 0.53183 |  |  | 0.47567 |  |  | 0.59054 |  |  | 0.37669
[13 empty] | Selected C this iteration |  |  | 400.3302 |  |  | #NUM! |  |  | 147.7051 |  |  | 64.2345 |  |  | 37.9245 |  |  | 27.0661 |  |  | 21.9281 |  |  | 19.926 |  |  | 17.5166 |  |  | 25.0346
[13 empty] | Absolute value C_100 - Selected C |  |  |  | 18000 | 72917.5885 |  | 18000 | 47623.6092 |  | 18000 | 116612.7255 |  | 18000 | 227131.8243 |  | 18000 | 381056.5454 |  | 18000 | 556162.4065 |  | 18000 | 734852.3638 |  | 18000 | 905626.1305 |  | 18000 | 1051403.8227 |  | 18000 | 1232853.6697

## Installed Gain
BALL_SEG
3
PV123
Wmax = maximum
[8 empty] | design flow = | 18000
Wmin = minimum
[8 empty] | design flow = | 2700
[8 empty] | Flow units are | lbm/h
Graph Data
Valve relative travel, h | 0 | 0.05 | 0.1 | 0.15 | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.55 | 0.6 | 0.65 | 0.7 | 0.75 | 0.8 | 0.85 | 0.9 | 0.95 | 1
Relative flow Q/Qmax | 0 | 0.024963 | 0.049925 | 0.086087 | 0.12225 | 0.18018 | 0.23811 | 0.31879 | 0.39947 | 0.49126 | 0.58304 | 0.67671 | 0.77037 | 0.85988 | 0.9494 | 1.0258 | 1.1022 | 1.1973 | 1.2924 | 1.3391 | 1.3857 | 0.15 | 0.15 | 1 | 1
Gain = Delta Q / Delta h |  | 0.49925 | 0.61124 | 0.72324 | 0.94092 | 1.1586 | 1.3861 | 1.6136 | 1.7247 | 1.8357 | 1.8545 | 1.8733 | 1.8318 | 1.7903 | 1.6593 | 1.5282 | 1.7152 | 1.9022 | 1.4173 | 0.93231
Qmin vertical line | [21 empty] | 0 | 4
Qmax vertical line | [23 empty] | 0 | 4
Delta Q |  | 0.049925 | 0.061124 | 0.072324 | 0.094092 | 0.11586 | 0.13861 | 0.16136 | 0.17247 | 0.18357 | 0.18545 | 0.18733 | 0.18318 | 0.17903 | 0.16593 | 0.15282 | 0.17152 | 0.19022 | 0.14173 | 0.093231
Delta h |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1

## xT, FL, Fd, AEta, Stp
Intermediate calculations
THE ONLY USER ACTION ON THIS TAB IS TO COPY xT VALLUES
[8 empty] | DESCRIPTION OF VARIABLE | NAME OF VARIABLE | FORMULA
Typical xT values based on the Reqired C and Valve size shown on the |  |  |  |  | For initial calculations (before |  |  | CALCULATED IN COLUMN "O" | CALCULATED IN COLUMN "O"
Valve Sizing tab. They can be copied to the the Valve Sizing tab. |  |  |  |  | the Cv is known), consider using
[5 empty] | the xT values listed below. |  |  | Capacity in units of Cv | C_v | 14.3307 | 39.6575 | 92.5767 | 136.2431
Flow | 31863 | 27000 | 65000 | 94000 | Minimum | Maximum |  | Valve size in units of inch | d_in | 3
Valve type | Choked press drop ratio factor, xT |  |  |  | Flow | Flow |  | Valve Cv/Valve size squared | Cv_over_d_Sq | 1.5923 | 4.4064 | 10.2863 | 15.1381
INSTRUCTIONS FOR xT CALCULATIONS
Globe, 4 port cage | 0.73105 | 0.72078 | 0.7 | 0.7 | 0.74 | 0.72 | Perform initial valve sizing useing the suggested xT values in Columns H & I.
Fine tune xT values on Valve sizing tab as follows:
Globe, Parabolic plug | 0.60716 | 0.6 | 0.6 | 0.6 | 0.62 | 0.6
1. Copy xT values: Highlight all 4 columns in the row for the valve type
Rotary eccentric plug | 0.62 | 0.62 | 0.54509 | 0.399 | 0.62 | 0.52 | you are sizing.
2. Press Ctrl + C
Segment ball | 0.63729 | 0.6229 | 0.55108 | 0.45043 | 0.64 | 0.4 | 3. Go to the Valve Sizing tab
4. Right Click on D9.
Butterfly | 0.693 | 0.66174 | 0.56878 | 0.49208 | 0.68 | 0.37 | 5. From "Paste Options" Select "Values"
Full ball (Full and reduced port) | 0.82 | 0.75841 | 0.6162 | 0.52001 | 0.82 | 0.3 | You may need to repeat Steps 1 through 5 one or two more times until
the xT values on this tab agree closely with what are on the Valve Sizing tab.
Typical FL values based on the Reqired C and Valve size shown
on the Valve Sizing tab. FL is only used in the IEC noise calculation.
This data is automaically copied to the Valve Sizing tab.
Flow | 31863 | 27000 | 65000 | 94000
Valve type | Liquid pressure recovery factor. FL
Globe, 4 port cage | 0.84002 | 0.8495 | 0.83006 | 0.81832
Globe, Parabolic plug | 0.90977 | 0.87846 | 0.84628 | 0.82386
Rotary eccentric plug | 0.90098 | 0.85262 | 0.79121 | 0.76
Segment ball | 0.92296 | 0.89285 | 0.82994 | 0.77802
Butterfly | 0.85631 | 0.82693 | 0.76605 | 0.71634
Full ball (Full and reduced port) | 0.89853 | 0.87606 | 0.8309 | 0.7954
Cv Table in current use | BALL_SEG
Values automatically copied to the | 0.92296 | 0.89285 | 0.82994 | 0.77802
Vlalve Sizing tab
Typical Fd values based on the Relative Travel on the Valve Sizing tab.
on the Valve Sizing tab. Fd is only used in the IEC noise calculation. | [8 empty] | Fd calculations
This data is automaically copied to the Valve Sizing tab. | [8 empty] | Valve travel from Valve Travel tab | 22.3954 | 40.1192 | 61.3343 | 73.4643
Valve type | Valve style modifier, Fd | [7 empty] | Relative travel | 0.22395 | 0.40119 | 0.61334 | 0.73464
Globe, 4 port cage =% | 0.42768 | 0.32936 | 0.3142 | 0.33215
[10 empty] | Case 1 | Case 2 | Case 3 | Case 4
Globe, 4 port cage Linear | 0.38221 | 0.34584 | 0.34776 | 0.37449
Globe, 4 port cage =%
Globe, Parabolic plug =% | 0.068161 | 0.13047 | 0.25008 | 0.32888
[9 empty] | Relatve travel | 0.22395 | 0.40119 | 0.61334 | 0.73464
Globe, Parabolic plug Linear | 0.18012 | 0.25792 | 0.35106 | 0.40431 |  |  |  |  | Fd_GCE | 0.42768 | 0.32936 | 0.3142 | 0.33215
Rotary eccentric plug | 0.12267 | 0.12982 | 0.16619 | 0.18975 |  |  |  |  | Globe, 4 port cage Linear
Segment ball | 0.78001 | 0.8486 | 0.9233 | 0.95562 |  |  |  |  | Relatve travel | 0.22395 | 0.40119 | 0.61334 | 0.73464
[9 empty] | Fd_GCL | 0.38221 | 0.34584 | 0.34776 | 0.37449
Butterfly | 0.15453 | 0.20127 | 0.26766 | 0.29937
Globe Parabolic plug =%
Full ball (Standard port) | 0.70167 | 0.86099 | 0.95475 | 0.98315
[9 empty] | Relatve travel | 0.22395 | 0.40119 | 0.61334 | 0.73464
Full ball (Full port) | 0.70167 | 0.86099 | 0.95475 | 0.98315 |  |  |  |  | Fd_GPE | 0.068161 | 0.13047 | 0.25008 | 0.32888
Globe Parabolic plug LIN
Values automatically copied to the | 0.78001 | 0.8486 | 0.9233 | 0.95562
Vlalve Sizing tab | [8 empty] | Relatve travel | 0.22395 | 0.40119 | 0.61334 | 0.73464
[9 empty] | Fd_GPL | 0.18012 | 0.25792 | 0.35106 | 0.40431
Typical values of Valve correction factor for acoustic efficiency, Aη | [8 empty] | Rotary eccentric plug
and Strouhal number for peak frequency calculation, Stp
Relatve travel
| Aη | Stp | [6 empty] | Relatve travel | 0.22395 | 0.40119 | 0.61334 | 0.73464
Globe parabolic Plug | -4.2 | 0.19 | [6 empty] | Fd_RP | 0.12267 | 0.12982 | 0.16619 | 0.18975
Globe Cage | -3.8 | 0.2
Eccendtric rotary plug | -3.6 | 0.3 | [6 empty] | Segment ball
Ball, Segment ball | -3.6 | 0.3
Butterfly | -4.2 | 0.3 | [6 empty] | Relatve travel | 0.22395 | 0.40119 | 0.61334 | 0.73464
[9 empty] | Fd_SEG | 0.78001 | 0.8486 | 0.9233 | 0.95562
Values automatically copied to the | -3.6 | 0.3
Vlalve Sizing tab | [8 empty] | Butterfly
[9 empty] | Relatve travel | 0.22395 | 0.40119 | 0.61334 | 0.73464
[9 empty] | Fd_BF | 0.15453 | 0.20127 | 0.26766 | 0.29937
Full ball reduced Port
[9 empty] | Relatve travel | 0.22395 | 0.40119 | 0.61334 | 0.73464
[9 empty] | Fd_FB | 0.70167 | 0.86099 | 0.95475 | 0.98315
Full ball full Port
[9 empty] | Relatve travel | 0.22395 | 0.40119 | 0.61334 | 0.73464
[9 empty] | Fd_FB_FP | 0.70167 | 0.86099 | 0.95475 | 0.98315

## Density, Mol Mass
This tab calculates Molecular mass from Specific gravity or from Valve Sizing tab process data. It also calculates Density from Valve Sizing tab data and Compressibility factor.
Conversion from specific gravity to Molecular Mass: |  |  |  | Case 1 | Case 2 | Case 3 | Case 4 |  | Intermediate Calculations
Inlet pressure converted to Pa (Pascal)
|  | Specific gravity | G_ | 1 | ======> | ======> | ======> | Inlet temperature coverted to Kelvin
|  | Molecular Mass |  | 28.97 | ======> | ======> | ======> | Pa | P_1..L | 620528.157 | 610875.4968 | 577091.186 | 551580.584
[8 empty] | K | T_1..L | 310.9278 | 310.9278 | 310.9278 | 310.9278
Conversion from Molecular Mass, Inlet Pressure and Temperature given on the Valve Sizing tab to Density
|  | Compressibility factor (Z)* | Z_ | 1 | 1 | 1 | 1
|  | Density (kg/m3) |  | 6.9541 | 6.8459 | 6.4673 | 6.1814
|  | Density (lbm/ft3) |  | 0.43414 | 0.42739 | 0.40375 | 0.38591
Conversion from Density, Inlet Pressure and Temperature given in Column D on the Valve Sizing tab to Molecular Mass
|  | Compressibility factor (Z)* |  | 1
|  | Molecular mass |  | 28.9709
Data input
Final results
*Use 1.00 if compressibility factor is unknown. Using a compressibility factor of 1.0
will result in calculated density or molecular mass above to be an approximation.

## SPL Conv
Aerodynamic Noise - IEC 60534-8-3 Ed: 3.0 | Data imported from Valve Sizing tab | [5 empty] | Scroll to the right to view the conversion from user interface units to units required by the IEC Standard and the pipe reducer calculations. | Conversion from user interface units to
Mass Flow | NO USER INPUT IS REQUIRED FOR THIS TAB. | [6 empty] | Units required by the IEC Standard. |  |  | Case 1 | Case 2 | Case 3 | Case 4 | DESCRIPTION OF VARIABLE | Eq | NAME OF VARIABLE
Process Parameters |  |  | Case 1 | Case 2 | Case 3 | Case 4 |  | (kg/s, Pa, K, kg/m3, m/s, m) | Units | [5 empty] | CALCULATED IN COLUMN "AA" |  | CALCULATED IN COLUMN "AA" | Case 1 | Case 2 | Case 3 | Case 4
Mass flow | lbm/h | m_dot | 2700 | 7200 | 14400 | 18000 |  | Flow | kg/s | m_dot | 0.3402 | 0.9072 | 1.8144 | 2.268
Inlet pressure | psiA | P_1 | 90 | 88.6 | 83.7 | 80 |  | Inlet pressure | Pa | P_1 | 620528.157 | 610875.4968 | 577091.186 | 551580.584
Inlet temperature | F | T_1 | 100 | 100 | 100 | 100 |  | Inlet temperature | K | T_1 | 310.9278 | 310.9278 | 310.9278 | 310.9278 | Calculation of FP and FLP
Pressure drop | psi | DELTA_P | 30 | 28.6 | 23.7 | 20 |  | Pressure drop | Pa | DELTA_P | 206842.719 | 197190.0588 | 163405.748 | 137895.146 | Reducer velocity head coefficients | S7501 18 | ZETA_1 | 0.28125 | 0.28125 | 0.28125 | 0.28125
Inlet density | lbm/ft3 | RHO_1 | 0.43414 | 0.42739 | 0.40375 | 0.3859 |  | Inlet density | kg/m3 | RHO_1 | 6.9543 | 6.8462 | 6.4675 | 6.1815 |  | S7501 17 | ZETA_B1 | 0.9375 | 0.9375 | 0.9375 | 0.9375
Molecular mass |  | M_ | 28.97 | =========> | =========> | =========> |  | Molecular mass |  | M_ | 28.97 | 28.97 | 28.97 | 28.97 |  | S7501 19 | ZETA_2 | 0.5625 | 0.5625 | 0.5625 | 0.5625
Specific heat ratio (g) |  | GAMMA | 1.4 | =========> | =========> | =========> |  | Specific heat ratio (g) |  | GAMMA | 1.4 | 1.4 | 1.4 | 1.4 |  | S7501 17 | ZETA_B2 | 0.9375 | 0.9375 | 0.9375 | 0.9375
Pipe/Valve Parameters | [14 empty] | Sum of velocity head coefficients | S7501 16 | SIGMA_ZETA | 0.84375 | 0.84375 | 0.84375 | 0.84375
Flow coefficient (Kv or Cv) | Cv | C_ | 14.3307 | 39.6575 | 92.5767 | 136.2431 |  | Flow coefficient (Kv or Cv) | Cv | C_ | 14.3307 | 39.6575 | 92.5767 | 136.2431 | Sum of upstream velocity head coef | S7501 | SIGMA_ZETA_1 | 1.2188 | 1.2188 | 1.2188 | 1.2188
Liquid pressure recovery factor |  | F_L | 0.92296 | 0.89285 | 0.82994 | 0.77802 |  | Liquid pressure recovery factor |  | F_L | 0.92296 | 0.89285 | 0.82994 | 0.77802 | Piping geometry factor | S7501 15 | F_P | 0.9988 | 0.99093 | 0.95336 | 0.90644
Valve style modifier |  | F_D | 0.78001 | 0.8486 | 0.9233 | 0.95562 |  | Valve style modifier |  | F_D | 0.78001 | 0.8486 | 0.9233 | 0.95562 | Combined liquid pressure recovery
Valve correction - accoustic efficiency, Ah |  | A_ETA | -3.6 | =========> | =========> | =========> |  | Valve correction - accoustic efficiency, Ah |  | A_ETA | -3.6 | -3.6 | -3.6 | -3.6 | factor and piping geometry factor | S7501 21 | F_LP | 0.9216 | 0.88354 | 0.79141 | 0.71327
Strouhal number (peak) |  | St_P | 0.3 | =========> | =========> | =========> |  | Strouhal number (peak) |  | St_P | 0.3 | 0.3 | 0.3 | 0.3
Valve inlet internal diameter | inch | D_Vi | 3 | =========> | =========> | =========> |  | Valve inlet internatl diameter | m | D_Vi | 0.0762 | 0.0762 | 0.0762 | 0.0762
Valve outlet internal diameter | inch | D_Vo | 3 | =========> | =========> | =========> |  | Valve outlet internatl diameter | m | D_Vo | 0.0762 | 0.0762 | 0.0762 | 0.0762 |  |  |  | 1
Inlet pipe internal diameter | inch | D_1 | 6 | =========> | =========> | =========> |  | Inlet pipe internal diameter | m | D_1 | 0.1524 | 0.1524 | 0.1524 | 0.1524
Outlet pipe internal diameter | inch | D_2 | 6 | =========> | =========> | =========> |  | Outlet pipe internal diameter | m | D_2 | 0.1524 | 0.1524 | 0.1524 | 0.1524 |  |  |  | 0.0762
Outlet pipe wall thickness | inch | T_S | 0.28 | =========> | =========> | =========> |  | Outlet pipe wall thickness | m | T_S | 0.007112 | 0.007112 | 0.007112 | 0.007112
[8 empty] | Speed of sound in pipe | m/s | C_S | 5000 | 5000 | 5000 | 5000
[8 empty] | Density of pipe material | kg/m3 | RHO_S | 8000 | 8000 | 8000 | 8000
Contraction coeff. for valve outlet or expander inlet*** |  | BETA | 0.75 | =========> | =========> | =========> |  | Beta (β)* |  | BETA | 0.75 | 0.75 | 0.75 | 0.75
Actual atmospheric pressure outside pipe | psiA | p_a | 14.696 | =========> | =========> | =========> |  | External speed of sound (atmospheric) | m/s | c_a | 343 | 343 | 343 | 343
[8 empty] | Actual atmospheric pressure outside pipe | Pa | p_a | 101325.3533 | 101325.3533 | 101325.3533 | 101325.3533
Auto filled based on Flag #
***Contraction coefficient for valve outlet or expander inlet. Requiered only if valve outlet velocity exceeds 0.3 Mach. A value of β = 0,93 seems to be applicable to straight pattern globe valves, but for some rotary valves the value may be as low as 0,7. Check with valve manufacturer.
Unit Selection for user interface | Flag # | Flag Value | Options
Mass Flow | IEC_1 | 3 | 1 = kg/s, 2 = kg/h 3 = lbm/h
Pressure (absolute) | IEC_2 | 4 | 1 = Pa, 2 = kPa, 3 = bar, 4 = psiA
Temperature | IEC_3 | 3 | 1 = K, 2 = C, 3 = F
Density | IEC_4 | 2 | 1 = kg/m3, 2 = lbm/ft3
Length | IEC_5 | 3 | 1 = m, 2 = mm, 3 = in
Flow coefficient | IEC_6 | 1 | 1 = Cv, 2 = Kv
Numerical Constants (Auto filled in based on Flag IEC_6)
N_14 |  | 0.0046
N_16 (Only used with multistage valves) |  | 48900
Universal gas constant | R_ | 8314 | J/kmol × K

## SPL Calcs
Calculations based on IEC 60534-8-3 Edition 3.0 |  |  |  | NO USER INPUT IS REQUIRED FOR THIS TAB.
Lines 6 through 34, Columns D through G are automatically flled trom the UI (User Interface) tab
[7 empty] | DESCRIPTION OF VARIABLE |  | NAME OF VARIABLE
Process Parameters | Units | Name | Case 1 | Case 2 | Case 3 | Case 4 | CALCULATED IN COLUMN "K" | Eqn. # | CALCULATED IN COLUMN "K" | Case 1 | Case 2 | Case 3 | Case 4
Flow | kg/s | m_dot..D | 0.3402 | 0.9072 | 1.8144 | 2.268
Inlet pressure | Pa | P_1..D | 620528.157 | 610875.4968 | 577091.186 | 551580.584 | Differential Pressure ratio | 1 | x | 0.33333 | 0.3228 | 0.28315 | 0.25
Inlet temperature | K | T_1..D | 310.9278 | 310.9278 | 310.9278 | 310.9278 | Absolute VC pressure at subsonic conditions | 2 | p_vc..K | 377580.8944 | 362840.4913 | 339966.562 | 328879.9323 | does not have any dependents
Outlet pressure | Pa | P_2..D | 413685.438 | 413685.438 | 413685.438 | 413685.438 | VC diff. pressure ratio @ critical flow cond. | 3 | x_vcc..K | 0.47172 | 0.47172 | 0.47172 | 0.47172
Inlet density | kg/m3 | RHO_1..D | 6.9543 | 6.8462 | 6.4675 | 6.1815 | Diff press. ratio at critical flow conditions | 4 | x_c..K | 0.40162 | 0.37502 | 0.32507 | 0.29209
Molecular mass |  | M_..D | 28.97 | 28.97 | 28.97 | 28.97 | Recovery correction factor α | 5 | ALPHA..K | 0.88285 | 0.84528 | 0.78272 | 0.74625
Specific heat ratio (g) |  | GAMMA..D | 1.4 | 1.4 | 1.4 | 1.4 | Differential pressure ratio at break point | 6 | x_B..K | 0.65113 | 0.63562 | 0.6065 | 0.58727
Pipe/Valve Parameters | [6 empty] | DP ratio where const acoustical efficiency begins | 7 | x_CE..K | 0.94851 | 0.94623 | 0.94193 | 0.93909
Flow coefficient (Kv or Cv) | Cv | C_..D | 14.3307 | 39.6575 | 92.5767 | 136.2431 | Regime definition |  | Regime..K | Regime I | Regime I | Regime I | Regime I
Valve style modifier |  | F_D..D | 0.78001 | 0.8486 | 0.9233 | 0.95562 | Valve style modifier | 8a | F_d..K | 0.78001 | 0.8486 | 0.9233 | 0.95562
Valve correction - accoustic efficiency, Ah |  | A_ETA..D | -3.6 | -3.6 | -3.6 | -3.6 | Jet Diameter | 9 | D_ j..K | 0.013047 | 0.023212 | 0.037233 | 0.045516
Strouhal number (peak) |  | St_P..D | 0.3 | 0.3 | 0.3 | 0.3 | Mach Number at - Regime I Only | Table 3 | M_vc..K | 0.87323 | 0.89578 | 0.90337 | 0.89223
Valve outlet internatl diameter | m | D_Vo..D | 0.0762 | 0.0762 | 0.0762 | 0.0762 | Freely expanded jet Mach # in regimes II, III, IV | Table 3 | M_j..K | Regimes II-IV only | Regimes II-IV only | Regimes II-IV only | Regimes II-IV only
Outlet pipe internal diameter | m | D_2..D | 0.1524 | 0.1524 | 0.1524 | 0.1524 | Freely expanded jet Mach number in regime V | Table 3 | M_j5..K | Regime V only | Regime V only | Regime V only | Regime V only
[7 empty] | Absolute Temp at VC at subsonic flow conditions | Table 3 | T_vc..K | 269.784 | 267.9294 | 267.3007 | 268.2231
[7 empty] | Absolute Temperature at VC at critical flow cond. | Table 3 | T_vcc..K | Regimes II-V only | Regimes II-V only | Regimes II-V only | Regimes II-V only | does not have any dependents
Outlet pipe wall thickness | m | T_S..D | 0.007112 | 0.007112 | 0.007112 | 0.007112 | Speed of sound at VC at subsonic flow conditions | Table 3 | c_vc..K | 329.2269 | 328.0933 | 327.7081 | 328.2755
Speed of sound in pipe | m/s | C_S..D | 5000 | 5000 | 5000 | 5000 | Speed of sound at VC at critical flow conditions | Table 3 | c_vcc | Regimes II-V only | Regimes II-V only | Regimes II-V only | Regimes II-V only
Density of pipe material | kg/m3 | RHO_S..D | 8000 | 8000 | 8000 | 8000 | Acoustical eff. factor for noise created by valve flow, η | Table 3 | K24 | 0.0001424 | 0.00014354 | 0.00012761 | 0.00011047
Beta (β) |  | BETA..D | 0.75 | 0.75 | 0.75 | 0.75 | Generated peak frequency | Table 3 | f_p..K | 6610.3299 | 3798.4121 | 2385.3289 | 1930.5228
Valve outlet temperature (assumed = Inlet temp) | K | T_2..D | 310.9278 | 310.9278 | 310.9278 | 310.9278 | Stream power of mass flow | Table 3 | W_m..K | 14058.938 | 39180.446 | 79506.7456 | 97283.495
Smaller of valve outlet or expander inlet IDs | m | D_ViS..D | 0.0762 | 0.0762 | 0.0762 | 0.0762 | Sound Power for noise propagating downstream | 11 | W_a..K | 2.002 | 5.624 | 10.1458 | 10.7471
External speed of sound (atmospheric) | m/s | c_a..D | 343 | 343 | 343 | 343 | Outlet density | 13 | RHO_2..K | 4.6362 | 4.6362 | 4.6362 | 4.6362
Actual atmospheric pressure outside pipe | Pa | p_a..D | 101325.3533 | 101325.3533 | 101325.3533 | 101325.3533 | Speed of sound at downstream conditions | 14 | c_2..K | 353.4472 | 353.4472 | 353.4472 | 353.4472
Reducer corrected Recovery factor. F_LP |  | F_LP..D | 0.9216 | 0.88354 | 0.79141 | 0.71327 | Mach number at valve outlet | 15 | M_o..K | 0.045525 | 0.1214 | 0.2428 | 0.3035
Piping geometry factor, F_P |  | F_P..D | 0.9988 | 0.99093 | 0.95336 | 0.90644 | Mach number in downstream pipe ( limited to 0.3 for calculating L_g) | 17 | M_2..K | 0.011381 | 0.03035 | 0.060699 | 0.075875
Universal gas constant | J/kmol × K | R_..D | 8314 | 8314 | 8314 | 8314 | Correction for Mach number | 16 | L_g..K | 0.079538 | 0.21416 | 0.43513 | 0.54831
N14 |  | N14..D | 0.0046 | 0.0046 | 0.0046 | 0.0046 | Overall internal sound-pressure level | 18 | L_pi..K | 146.6309 | 151.2513 | 154.0347 | 154.3978
N16 (Only used with multistage valves) |  |  | 48900 | 48900 | 48900 | 48900 | Frequency dependent internal sound pressure level | 19 | L_pi_f_i | 97.4518 | 106.1622 | 112.3794 | 114.3037 |  | Table_5 Indexed |  | Table_7 - "A" weighting
[7 empty] | (third octave bands) |  | 2 | 99.2742 | 107.9843 | 114.201 | 116.1248 |  | Frequency bands |  | factor at frequency fi
Structural loss factor reference frequency | Hz | f_s..D | 1 | 1 | 1 | 1 |  |  | 3 | 100.9214 | 109.6312 | 115.8472 | 117.7704 |  | Index | Frequency | fi
Standard atmoshperic pressure | Ps | p_s..D | 101325 | 101325 | 101325 | 101325 |  |  | 4 | 102.5685 | 111.2778 | 117.4927 | 119.4151 |  | number | fi | (Hz) | ΔLA(fi)
[9 empty] | 5 | 104.2743 | 112.9827 | 119.1961 | 121.1172 |  | 1 | 12.5 | 12.5 | -63.4
| Auto filled based on Flag IEC_6 | [7 empty] | 6 | 106.0372 | 114.7444 | 120.9553 | 122.8745 |  | 2 | 16 | 16 | -56.7
[9 empty] | 7 | 107.6836 | 116.3891 | 122.5966 | 124.5131 |  | 3 | 20 | 20 | -50.5
[9 empty] | 8 | 109.3882 | 118.0911 | 124.2934 | 126.2058 |  | 4 | 25 | 25 | -44.7
[9 empty] | 9 | 111.1494 | 119.8482 | 126.0425 | 127.9486 |  | 5 | 31.5 | 31.5 | -39.4
[9 empty] | 10 | 112.7933 | 121.4864 | 127.6698 | 129.5673 |  | 6 | 40 | 40 | -34.6
[9 empty] | 11 | 114.4355 | 123.1205 | 129.288 | 131.1731 |  | 7 | 50 | 50 | -30.2
[9 empty] | 12 | 116.2494 | 124.9211 | 131.0625 | 132.9275 |  | 8 | 63 | 63 | -26.2
[9 empty] | 13 | 117.8853 | 126.539 | 132.646 | 134.4846 |  | 9 | 80 | 80 | -22.5
[9 empty] | 14 | 119.5158 | 128.1436 | 134.2014 | 136.0029 |  | 10 | 100 | 100 | -19.1
[9 empty] | 15 | 121.1964 | 129.7852 | 135.7706 | 137.5186 |  | 11 | 125 | 125 | -16.1
[9 empty] | 16 | 122.9207 | 131.4508 | 137.3301 | 139.0023 |  | 12 | 160 | 160 | -13.4
[9 empty] | 17 | 124.5142 | 132.9657 | 138.7085 | 140.287 |  | 13 | 200 | 200 | -10.9
[9 empty] | 18 | 126.1393 | 134.4766 | 140.0309 | 141.4864 |  | 14 | 250 | 250 | -8.6
[9 empty] | 19 | 127.7803 | 135.9535 | 141.255 | 142.5552 |  | 15 | 315 | 315 | -6.6
[9 empty] | 20 | 129.263 | 137.2301 | 142.2389 | 143.3703 |  | 16 | 400 | 400 | -4.8
[9 empty] | 21 | 130.6793 | 138.3805 | 143.0442 | 143.9862 |  | 17 | 500 | 500 | -3.2
[9 empty] | 22 | 132.1422 | 139.4747 | 143.7009 | 144.4088 |  | 18 | 630 | 630 | -1.9
[9 empty] | 23 | 133.3433 | 140.2759 | 144.0582 | 144.5257 |  | 19 | 800 | 800 | -0.8
[9 empty] | 24 | 134.4018 | 140.8764 | 144.161 | 144.3496 |  | 20 | 1000 | 1000 | 0
[9 empty] | 25 | 135.3208 | 141.2629 | 143.9554 | 143.8077 |  | 21 | 1250 | 1250 | 0.6
[9 empty] | 26 | 136.0547 | 141.3767 | 143.354 | 142.8203 |  | 22 | 1600 | 1600 | 1
[9 empty] | 27 | 136.5191 | 141.1773 | 142.3978 | 141.504 |  | 23 | 2000 | 2000 | 1.2
[9 empty] | 28 | 136.7469 | 140.6077 | 141.0085 | 139.7871 |  | 24 | 2500 | 2500 | 1.3
[9 empty] | 29 | 136.6699 | 139.5899 | 139.2005 | 137.7192 |  | 25 | 3150 | 3150 | 1.2
[9 empty] | 30 | 136.2614 | 138.247 | 137.2497 | 135.5999 |  | 26 | 4000 | 4000 | 1
[9 empty] | 31 | 135.4837 | 136.5724 | 135.1229 | 133.3628 |  | 27 | 5000 | 5000 | 0.5
[9 empty] | 32 | 134.1747 | 134.4225 | 132.638 | 130.8034 |  | 28 | 6300 | 6300 | -0.1
[9 empty] | 33 | 132.6173 | 132.2927 | 130.3185 | 128.4441 |  | 29 | 8000 | 8000 | -1.1
[7 empty] | Eqns. 34 through 43 apply only when MO > 0.3 | [7 empty] | 30 | 10000 | 10000 | -2.5
[7 empty] | Gas velocity in downstream pipe | 34 | U_p..K | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 26.8179 |  | 31 | 12500 | 12500 | -4.3
[7 empty] | Gas velocity in the inlet diameter of expander | 35 | U_R | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 143.029 |  | 32 | 16000 | 16000 | -6.6
[7 empty] | Converted stream power in the expander | 36 | W_mR..K | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 17688.9092 |  | 33 | 20000 | 20000 | -9.3
[7 empty] | Peak frequency in valve outlet or reduced diameter of expander | 37 | f_pR..K | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 563.1063
[7 empty] | Mach number in the entrance to expander | 39 | M_R..K | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 0.40467
[7 empty] | Acoustical eff. factor for noise created by outlet flow in expander | 38 | etta_r..K | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 1.6646e-05 | If you are trying to compare the Annex A Example 6
[7 empty] | Sound power for noise generated by the outlet flow and propagating downstream | 40 | W_Ar..K | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 0.29444 | (where the valve outlet Mach number is greater that 0.3)
[7 empty] | Overall internal SPL at pipe wall for noise created by outlet flow in expander | 41 | L_piR..K | N/A Mo<0.3 | N/A Mo<0.3 | N/A Mo<0.3 | 138.7749 | calculations with this worksheet be aware that the
[7 empty] | Frequency dependent internal SPL at pipe wall flow in expander | 42 | L_piR_f_i | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 107.7581 | value shown in Annex A for Equation 38 was based
[9 empty] | 2 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 109.5693 | on an old equation from the 2nd edition of the standard
[9 empty] | 3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 111.2016 | and thus the values in the annex for Equation 38 and many
[9 empty] | 4 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 112.8268 | subsequent calculations are incorrect.
[9 empty] | 5 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 114.4995
[9 empty] | 6 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 116.2118 | The correct equation is shown in the Standard and in Annex A,
[9 empty] | 7 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 117.789 | but the calculated value shown in Annex A for Equatin 38 is incorrect,
[9 empty] | 8 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 119.39 | being the result of using the wrong equation in the calculation.
[9 empty] | 9 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 120.9956
[9 empty] | 10 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 122.4326 | Equation 38 is only applicable when the valve outlet Mach number
[9 empty] | 11 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 123.7879 | is greater than 0.3. In all other cases it is not used.
[9 empty] | 12 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 125.1625
[9 empty] | 13 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 126.2638
[9 empty] | 14 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 127.2041
[9 empty] | 15 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 127.9832
[9 empty] | 16 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.5554
[9 empty] | 17 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.8506
[9 empty] | 18 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.8776
[9 empty] | 19 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.5562
[9 empty] | 20 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 127.8857
[9 empty] | 21 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 126.8301
[9 empty] | 22 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 125.232
[9 empty] | 23 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 123.4604
[9 empty] | 24 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 121.4576
[9 empty] | 25 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 119.2168
[9 empty] | 26 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 116.7876
[9 empty] | 27 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 114.4553
[9 empty] | 28 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 112.0017
[9 empty] | 29 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 109.4414
[9 empty] | 30 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 107.037
[9 empty] | 31 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 104.6253
[9 empty] | 32 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 101.9522
[9 empty] | 33 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 99.5333
[7 empty] | Combined internal sound-pressure level at pipe wall, caused by valve | 43 | L_piS_f_i | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 115.1727
[7 empty] | trim and expander (third octave bands: 12.5 Hz - 20,000 Hz) |  | 2 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 116.9921
[9 empty] | 3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 118.6353
[9 empty] | 4 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 120.2765
[9 empty] | 5 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 121.9733
[9 empty] | 6 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 123.7226
[9 empty] | 7 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 125.3503
[9 empty] | 8 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 127.027
[9 empty] | 9 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.7466
[9 empty] | 10 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 130.3353
[9 empty] | 11 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 131.9014
[9 empty] | 12 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 133.5993
[9 empty] | 13 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 135.094
[9 empty] | 14 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 136.5409
[9 empty] | 15 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 137.9769
[9 empty] | 16 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 139.3774
[9 empty] | 17 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 140.5883
[9 empty] | 18 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 141.7183
[9 empty] | 19 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 142.7248
[9 empty] | 20 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 143.4914
[9 empty] | 21 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 144.069
[9 empty] | 22 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 144.461
[9 empty] | 23 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 144.5595
[9 empty] | 24 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 144.3718
[9 empty] | 25 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 143.8227
[9 empty] | 26 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 142.8311
[9 empty] | 27 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 141.5126
[9 empty] | 28 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 139.7943
[9 empty] | 29 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 137.7256
[9 empty] | 30 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 135.6059
[9 empty] | 31 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 133.3686
[9 empty] | 32 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 130.8091
[9 empty] | 33 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | N/A Mₒ<0.3 | 128.4497
[7 empty] | Ring frequency | 21 | f_r..K | 10443.2377 | 10443.2377 | 10443.2377 | 10443.2377
[7 empty] | Internal coincidence pipe frequency | 22 | f_o..K | 2690.3303 | 2690.3303 | 2690.3303 | 2690.3303
[7 empty] | External coincidence frequency | 23 | f_g..K | 1824.0521 | 1824.0521 | 1824.0521 | 1824.0521
[7 empty] | Frequency factor (3rd octave bands: 12.5 Hz - 20,000 Hz) | Table 6 | G_x_f_i | 1.8868e-10 | 1.8868e-10 | 1.8868e-10 | 1.8868e-10
[9 empty] | 2 | 5.0649e-10 | 5.0649e-10 | 5.0649e-10 | 5.0649e-10
[9 empty] | 3 | 1.2365e-09 | 1.2365e-09 | 1.2365e-09 | 1.2365e-09
[9 empty] | 4 | 3.0189e-09 | 3.0189e-09 | 3.0189e-09 | 3.0189e-09
[9 empty] | 5 | 7.6091e-09 | 7.6091e-09 | 7.6091e-09 | 7.6091e-09
[9 empty] | 6 | 1.9785e-08 | 1.9785e-08 | 1.9785e-08 | 1.9785e-08
[9 empty] | 7 | 4.8303e-08 | 4.8303e-08 | 4.8303e-08 | 4.8303e-08
[9 empty] | 8 | 1.2175e-07 | 1.2175e-07 | 1.2175e-07 | 1.2175e-07
[9 empty] | 9 | 3.1656e-07 | 3.1656e-07 | 3.1656e-07 | 3.1656e-07
[9 empty] | 10 | 7.7284e-07 | 7.7284e-07 | 7.7284e-07 | 7.7284e-07
[9 empty] | 11 | 1.8868e-06 | 1.8868e-06 | 1.8868e-06 | 1.8868e-06
[9 empty] | 12 | 5.0649e-06 | 5.0649e-06 | 5.0649e-06 | 5.0649e-06
[9 empty] | 13 | 1.2365e-05 | 1.2365e-05 | 1.2365e-05 | 1.2365e-05
[9 empty] | 14 | 3.0189e-05 | 3.0189e-05 | 3.0189e-05 | 3.0189e-05
[9 empty] | 15 | 7.6091e-05 | 7.6091e-05 | 7.6091e-05 | 7.6091e-05
[9 empty] | 16 | 0.00019785 | 0.00019785 | 0.00019785 | 0.00019785
[9 empty] | 17 | 0.00048303 | 0.00048303 | 0.00048303 | 0.00048303
[9 empty] | 18 | 0.0012175 | 0.0012175 | 0.0012175 | 0.0012175
[9 empty] | 19 | 0.0031656 | 0.0031656 | 0.0031656 | 0.0031656
[9 empty] | 20 | 0.0077284 | 0.0077284 | 0.0077284 | 0.0077284
[9 empty] | 21 | 0.018868 | 0.018868 | 0.018868 | 0.018868
[9 empty] | 22 | 0.050649 | 0.050649 | 0.050649 | 0.050649
[9 empty] | 23 | 0.12365 | 0.12365 | 0.12365 | 0.12365
[9 empty] | 24 | 0.30189 | 0.30189 | 0.30189 | 0.30189
[9 empty] | 25 | 0.54921 | 0.54921 | 0.54921 | 0.54921
[9 empty] | 26 | 0.61889 | 0.61889 | 0.61889 | 0.61889
[9 empty] | 27 | 0.69194 | 0.69194 | 0.69194 | 0.69194
[9 empty] | 28 | 0.7767 | 0.7767 | 0.7767 | 0.7767
[9 empty] | 29 | 0.87524 | 0.87524 | 0.87524 | 0.87524
[9 empty] | 30 | 0.97855 | 0.97855 | 0.97855 | 0.97855
[9 empty] | 31 | 1 | 1 | 1 | 1
[9 empty] | 32 | 1 | 1 | 1 | 1
[9 empty] | 33 | 1 | 1 | 1 | 1
[7 empty] | Frequency factor (3rd octave bands: 12.5 Hz - 20,000 Hz) | Table 6 | G_y_f_i | 1 | 1 | 1 | 1
[9 empty] | 2 | 1 | 1 | 1 | 1
[9 empty] | 3 | 1 | 1 | 1 | 1
[9 empty] | 4 | 1 | 1 | 1 | 1
[9 empty] | 5 | 1 | 1 | 1 | 1
[9 empty] | 6 | 1 | 1 | 1 | 1
[9 empty] | 7 | 1 | 1 | 1 | 1
[9 empty] | 8 | 1 | 1 | 1 | 1
[9 empty] | 9 | 1 | 1 | 1 | 1
[9 empty] | 10 | 1 | 1 | 1 | 1
[9 empty] | 11 | 1 | 1 | 1 | 1
[9 empty] | 12 | 1 | 1 | 1 | 1
[9 empty] | 13 | 1 | 1 | 1 | 1
[9 empty] | 14 | 1 | 1 | 1 | 1
[9 empty] | 15 | 1 | 1 | 1 | 1
[9 empty] | 16 | 1 | 1 | 1 | 1
[9 empty] | 17 | 1 | 1 | 1 | 1
[9 empty] | 18 | 1 | 1 | 1 | 1
[9 empty] | 19 | 1 | 1 | 1 | 1
[9 empty] | 20 | 1 | 1 | 1 | 1
[9 empty] | 21 | 1 | 1 | 1 | 1
[9 empty] | 22 | 1 | 1 | 1 | 1
[9 empty] | 23 | 1 | 1 | 1 | 1
[9 empty] | 24 | 1 | 1 | 1 | 1
[9 empty] | 25 | 1 | 1 | 1 | 1
[9 empty] | 26 | 1 | 1 | 1 | 1
[9 empty] | 27 | 1 | 1 | 1 | 1
[9 empty] | 28 | 1 | 1 | 1 | 1
[9 empty] | 29 | 1 | 1 | 1 | 1
[9 empty] | 30 | 1 | 1 | 1 | 1
[9 empty] | 31 | 1 | 1 | 1 | 1
[9 empty] | 32 | 1 | 1 | 1 | 1
[9 empty] | 33 | 1 | 1 | 1 | 1
[7 empty] | Frequency-dependent structural loss factor third | 20c | η_s_f_i | 0.028284 | 0.028284 | 0.028284 | 0.028284
[7 empty] | octave bands: 12.5 Hz - 20,000 Hz) |  | 2 | 0.025 | 0.025 | 0.025 | 0.025
[9 empty] | 3 | 0.022361 | 0.022361 | 0.022361 | 0.022361
[9 empty] | 4 | 0.02 | 0.02 | 0.02 | 0.02
[9 empty] | 5 | 0.017817 | 0.017817 | 0.017817 | 0.017817
[9 empty] | 6 | 0.015811 | 0.015811 | 0.015811 | 0.015811
[9 empty] | 7 | 0.014142 | 0.014142 | 0.014142 | 0.014142
[9 empty] | 8 | 0.012599 | 0.012599 | 0.012599 | 0.012599
[9 empty] | 9 | 0.01118 | 0.01118 | 0.01118 | 0.01118
[9 empty] | 10 | 0.01 | 0.01 | 0.01 | 0.01
[9 empty] | 11 | 0.0089443 | 0.0089443 | 0.0089443 | 0.0089443
[9 empty] | 12 | 0.0079057 | 0.0079057 | 0.0079057 | 0.0079057
[9 empty] | 13 | 0.0070711 | 0.0070711 | 0.0070711 | 0.0070711
[9 empty] | 14 | 0.0063246 | 0.0063246 | 0.0063246 | 0.0063246
[9 empty] | 15 | 0.0056344 | 0.0056344 | 0.0056344 | 0.0056344
[9 empty] | 16 | 0.005 | 0.005 | 0.005 | 0.005
[9 empty] | 17 | 0.0044721 | 0.0044721 | 0.0044721 | 0.0044721
[9 empty] | 18 | 0.0039841 | 0.0039841 | 0.0039841 | 0.0039841
[9 empty] | 19 | 0.0035355 | 0.0035355 | 0.0035355 | 0.0035355
[9 empty] | 20 | 0.0031623 | 0.0031623 | 0.0031623 | 0.0031623
[9 empty] | 21 | 0.0028284 | 0.0028284 | 0.0028284 | 0.0028284
[9 empty] | 22 | 0.0025 | 0.0025 | 0.0025 | 0.0025
[9 empty] | 23 | 0.0022361 | 0.0022361 | 0.0022361 | 0.0022361
[9 empty] | 24 | 0.002 | 0.002 | 0.002 | 0.002
[9 empty] | 25 | 0.0017817 | 0.0017817 | 0.0017817 | 0.0017817
[9 empty] | 26 | 0.0015811 | 0.0015811 | 0.0015811 | 0.0015811
[9 empty] | 27 | 0.0014142 | 0.0014142 | 0.0014142 | 0.0014142
[9 empty] | 28 | 0.0012599 | 0.0012599 | 0.0012599 | 0.0012599
[9 empty] | 29 | 0.001118 | 0.001118 | 0.001118 | 0.001118
[9 empty] | 30 | 0.001 | 0.001 | 0.001 | 0.001
[9 empty] | 31 | 0.00089443 | 0.00089443 | 0.00089443 | 0.00089443
[9 empty] | 32 | 0.00079057 | 0.00079057 | 0.00079057 | 0.00079057
[9 empty] | 33 | 0.00070711 | 0.00070711 | 0.00070711 | 0.00070711
[7 empty] | Damping factor for transmission loss, ΔTL | 20b | DeltaTL..K | 3.4652 | 3.4652 | 3.4652 | 3.4652
[7 empty] | Frequency dependent transmission loss 3rd octave bands: | 20a | TL_f_i | -96.7591 | -96.7591 | -96.7591 | -96.759
[7 empty] | 12.5 Hz - 20,000 Hz) |  | 2 | -94.6478 | -94.6478 | -94.6478 | -94.6478
[9 empty] | 3 | -92.7429 | -92.7429 | -92.7429 | -92.7428
[9 empty] | 4 | -90.8415 | -90.8415 | -90.8415 | -90.8415
[9 empty] | 5 | -88.8765 | -88.8765 | -88.8765 | -88.8764
[9 empty] | 6 | -86.8503 | -86.8503 | -86.8503 | -86.8502
[9 empty] | 7 | -84.9626 | -84.9626 | -84.9626 | -84.9626
[9 empty] | 8 | -83.0131 | -83.0131 | -83.0131 | -83.0131
[9 empty] | 9 | -81.0045 | -81.0045 | -81.0045 | -81.0045
[9 empty] | 10 | -79.1348 | -79.1348 | -79.1348 | -79.1348
[9 empty] | 11 | -77.272 | -77.272 | -77.272 | -77.2719
[9 empty] | 12 | -75.2197 | -75.2197 | -75.2197 | -75.2197
[9 empty] | 13 | -73.3731 | -73.3731 | -73.3731 | -73.373
[9 empty] | 14 | -71.535 | -71.535 | -71.535 | -71.5349
[9 empty] | 15 | -69.6409 | -69.6409 | -69.6409 | -69.6409
[9 empty] | 16 | -67.694 | -67.694 | -67.694 | -67.694
[9 empty] | 17 | -65.8862 | -65.8862 | -65.8862 | -65.8862
[9 empty] | 18 | -64.0254 | -64.0254 | -64.0254 | -64.0254
[9 empty] | 19 | -62.1148 | -62.1148 | -62.1148 | -62.1148
[9 empty] | 20 | -60.3425 | -60.3425 | -60.3425 | -60.3425
[9 empty] | 21 | -58.5826 | -58.5826 | -58.5826 | -58.5826
[9 empty] | 22 | -56.6505 | -56.6505 | -56.6505 | -56.6505
[9 empty] | 23 | -54.9178 | -54.9178 | -54.9178 | -54.9177
[9 empty] | 24 | -53.1983 | -53.1983 | -53.1983 | -53.1983
[9 empty] | 25 | -52.8477 | -52.8477 | -52.8477 | -52.8476
[9 empty] | 26 | -54.668 | -54.668 | -54.668 | -54.668
[9 empty] | 27 | -56.3823 | -56.3823 | -56.3823 | -56.3823
[9 empty] | 28 | -58.1719 | -58.1719 | -58.1719 | -58.1719
[9 empty] | 29 | -60.0366 | -60.0366 | -60.0366 | -60.0365
[9 empty] | 30 | -61.7916 | -61.7916 | -61.7916 | -61.7916
[9 empty] | 31 | -63.9496 | -63.9496 | -63.9496 | -63.9496
[9 empty] | 32 | -66.4552 | -66.4552 | -66.4552 | -66.4552
[9 empty] | 33 | -68.7324 | -68.7324 | -68.7324 | -68.7324
[7 empty] | Frequency dependent external sound-pressure level | 24 | L_pe_1m_f_i | -10.4478 | -1.7373 | 4.4799 | 7.2733
[7 empty] | (third octave bands: 12.5 Hz - 20,000 Hz) |  | 2 | -6.5141 | 2.196 | 8.4128 | 11.2039
[9 empty] | 3 | -2.9619 | 5.7479 | 11.9639 | 14.752
[9 empty] | 4 | 0.58654 | 9.2958 | 15.5108 | 18.2945
[9 empty] | 5 | 4.2573 | 12.9658 | 19.1792 | 21.9564
[9 empty] | 6 | 8.0465 | 16.7537 | 22.9646 | 25.7319
[9 empty] | 7 | 11.5805 | 20.286 | 26.4935 | 29.2472
[9 empty] | 8 | 15.2346 | 23.9375 | 30.1398 | 32.8735
[9 empty] | 9 | 19.0044 | 27.7032 | 33.8975 | 36.6016
[9 empty] | 10 | 22.518 | 31.2112 | 37.3945 | 40.0601
[9 empty] | 11 | 26.0231 | 34.7081 | 40.8755 | 43.489
[9 empty] | 12 | 29.8892 | 38.5608 | 44.7023 | 47.2392
[9 empty] | 13 | 33.3717 | 42.0254 | 48.1325 | 50.5805
[9 empty] | 14 | 36.8404 | 45.4681 | 51.526 | 53.8655
[9 empty] | 15 | 40.415 | 49.0038 | 54.9892 | 57.1956
[9 empty] | 16 | 44.0862 | 52.6163 | 58.4956 | 60.543
[9 empty] | 17 | 47.4875 | 55.939 | 61.6818 | 63.5616
[9 empty] | 18 | 50.9734 | 59.3108 | 64.8651 | 66.5525
[9 empty] | 19 | 54.525 | 62.6983 | 67.9997 | 69.4695
[9 empty] | 20 | 57.7801 | 65.7471 | 70.756 | 72.0085
[9 empty] | 21 | 60.9563 | 68.6575 | 73.3212 | 74.346
[9 empty] | 22 | 64.3513 | 71.6837 | 75.9099 | 76.67
[9 empty] | 23 | 67.2851 | 74.2177 | 78 | 78.5013
[9 empty] | 24 | 70.063 | 76.5376 | 79.8222 | 80.0331
[9 empty] | 25 | 71.3326 | 77.2748 | 79.9673 | 79.8346
[9 empty] | 26 | 70.2463 | 75.5683 | 77.5455 | 77.0226
[9 empty] | 27 | 68.9964 | 73.6546 | 74.8751 | 73.9898
[9 empty] | 28 | 67.4346 | 71.2953 | 71.6961 | 70.482
[9 empty] | 29 | 65.4928 | 68.4128 | 68.0235 | 66.5486
[9 empty] | 30 | 63.3293 | 65.3149 | 64.3176 | 62.6738
[9 empty] | 31 | 60.3937 | 61.4823 | 60.0328 | 58.2786
[9 empty] | 32 | 56.579 | 56.8268 | 55.0423 | 53.2134
[9 empty] | 33 | 52.7445 | 52.4199 | 50.4457 | 48.5769
[7 empty] | Summation of L_pe,1m(f_i) and DLA(fi),1m(f_i) and DLA(fi) | 25 | L_pe_fi_plus_delta_LA_fi | 4.1231e-08 | 3.0638e-07 | 1.2823e-06 | 2.4396e-06
[9 empty] | 16 | 4.7708e-07 | 3.5449e-06 | 1.4835e-05 | 2.8209e-05
[7 empty] | Equation (25) has been divided into two parts. |  | 20 | 4.5062e-06 | 3.348e-05 | 0.00014008 | 0.00026619
[7 empty] | This section calculates the portion shown in the red box below. |  | 25 | 3.8784e-05 | 0.00028812 | 0.0012052 | 0.002288
[7 empty] | In the section below the quantities in this section are added |  | 31.5 | 0.00030601 | 0.0022729 | 0.0095042 | 0.018015
[7 empty] | logarithmically and converted to dB(A) |  | 40 | 0.0022113 | 0.01642 | 0.068622 | 0.12977
[9 empty] | 50 | 0.013742 | 0.102 | 0.42594 | 0.80302
[9 empty] | 63 | 0.080069 | 0.59395 | 2.4773 | 4.6489
[9 empty] | 80 | 0.44714 | 3.3137 | 13.796 | 25.7137
[9 empty] | 100 | 2.1968 | 16.2598 | 67.5232 | 124.7405
[9 empty] | 125 | 9.8244 | 72.5788 | 300.2997 | 548.1564
[9 empty] | 160 | 44.5575 | 328.1594 | 1349.6764 | 2420.559
[9 empty] | 200 | 176.6743 | 1295.8201 | 5287.4388 | 9290.6776
[9 empty] | 250 | 666.8634 | 4861.9906 | 19615.3571 | 33615.9724
[9 empty] | 315 | 2407.1503 | 17393.3847 | 69011.3853 | 114699.1995
[9 empty] | 400 | 8484.3832 | 60482.4398 | 234182.8066 | 375228.5505
[9 empty] | 500 | 26837.8612 | 187890.1351 | 704984.6202 | 1086833.2183
[9 empty] | 630 | 80786.9544 | 550908.1211 | 1979286.8626 | 2919090.6059
[9 empty] | 800 | 235778.7783 | 1548199.6148 | 5247728.9136 | 7361289.0878
[9 empty] | 1000 | 599801.7652 | 3755855.5325 | 11901365.6546 | 15880007.6666
[9 empty] | 1250 | 1430952.2162 | 8428414.2672 | 24667091.1332 | 31231996.1523
[9 empty] | 1600 | 3428690.5702 | 18551219.8402 | 49089695.1562 | 58479659.363
[9 empty] | 2000 | 7055166.8208 | 34815217.4273 | 83176028.199 | 93354281.9046
[9 empty] | 2500 | 13686628.8775 | 60779735.7846 | 129484279.6139 | 135927308.035
[9 empty] | 3150 | 17916965.2339 | 70384850.6011 | 130836748.4042 | 126900693.153
[9 empty] | 4000 | 13323827.4761 | 45376235.2297 | 71540519.9132 | 63425525.8928
[9 empty] | 5000 | 8905023.2321 | 26028902.9322 | 34475359.1119 | 28117966.8104
[9 empty] | 6300 | 5413249.9899 | 13168403.6086 | 14441460.4813 | 10919371.9478
[9 empty] | 8000 | 2749691.6422 | 5386220.898 | 4924356.0101 | 3506418.6146
[9 empty] | 10000 | 1210410.3724 | 1912000.3889 | 1519699.7641 | 1040841.1099
[9 empty] | 12500 | 406787.0959 | 522678.1875 | 374352.7043 | 249953.1253
[9 empty] | 16000 | 99517.4268 | 105362.2148 | 69859.9604 | 45850.0669
[9 empty] | 20000 | 22102.7691 | 20511.1221 | 13018.646 | 8466.2027
[7 empty] | A-weighted overall SPL 1 m from pipe wall | 25 | L_pAe_1m..K | 78.8425 | 84.648 | 87.5188 | 87.6417
Note on L47: Jon:

## Valve Travel
VALVE TRAVEL AT GIVEN Cv | [6 empty] | Callculation of Valve capacity in units of Cv and size in units of inch
[9 empty] | Case 1 | Case 2 | Case 3 | Case 4
| Case 1 | Case 2 | Case 3 | Case 4 |  |  | Valve size in Inch | VS_IN | 3 | ===> | ===> | ===>
Valve size (inch) | 3 | [5 empty] | Valve cap. In Cv | VCAP_CV | 14.3307 | 39.6575 | 92.5767 | 136.2431
Calculated Cv | 14.3307 | 39.6575 | 92.5767 | 136.2431
NO USER INPUT IS REQUIRED FOR THIS TAB.
Travel % @ Cv | 22.3954 | 40.1192 | 61.3343 | 73.4643
TheTravel % @ Cv is calculated from the final Cv values on the
|  |  |  | Final results | Valve Sizing tab then copied to Line 24 of the Valve Sizing tab.
Cv table in use | BALL_SEG
[10 empty] | Case 1 | [12 empty] | Case 2 | [12 empty] | Case 3 | [13 empty] | Case 4
[6 empty] | Calc Cv | 14.3307 | [11 empty] | Calc Cv | 39.6575 | [11 empty] | Calc Cv | 92.5767 | [11 empty] | Calc Cv | 136.2431
[5 empty] | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420 | Travel, % | Cv @ travel % | 0 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420
[6 empty] | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
[6 empty] | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471 |  |  | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471 |  |  | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471 |  |  | M | 2.1142 | 1.4556 | 0.87719 | 0.60976 | 0.46296 | 0.36765 | 0.30488 | 0.22727 | 0.12346 | 0.057471
[7 empty] | 30.2975 | 23.9749 | 22.3954 | 24.7139 | 28.3939 | 32.8422 | 37.4789 | 45.757 | 61.3989 | 76.6857 |  |  |  | 83.8425 | 60.8406 | 44.6119 | 40.157 | 40.1192 | 42.1535 | 45.2005 | 51.5131 | 64.5256 | 78.1412 |  |  |  | 195.7223 | 137.8699 | 91.0322 | 72.4248 | 64.6188 | 61.6091 | 61.3343 | 63.5401 | 71.0588 | 81.1826 |  |  |  | 288.0404 | 201.431 | 129.3361 | 99.0507 | 84.8348 | 77.6629 | 74.6473 | 73.4643 | 76.4498 | 83.6921
[6 empty] | Vlv Trav @ Cv | 0: 22.3954 |  | Vlv Trav @ Cv | 40.1192 | [11 empty] | Vlv Trav @ Cv | 61.3343 | [11 empty] | Vlv Trav @ Cv | 73.4643
VALVE Cv TABLES
|  |  | FULL PORT BALL VALVES |  |  | TABLE NAME: | 0: BALL_FP; 30: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 2 | 2.48 | 5.4 | 10.1 | 17.8 | 27.9 | 42.5 | 70.8 | 123 | 224 | 480
[6 empty] | 3 | 5.9 | 15.8 | 29.7 | 49.5 | 75.7 | 109 | 177 | 308 | 560 | 1200
[6 empty] | 4 | 9.7 | 25.9 | 48.6 | 81 | 124 | 179 | 313 | 545 | 989 | 2120
[6 empty] | 6 | 22 | 60 | 112 | 187 | 286 | 413 | 757 | 1318 | 2394 | 5100
[6 empty] | 8 | 40 | 106 | 199 | 331 | 506 | 732 | 1386 | 2413 | 4381 | 9300
[6 empty] | 10 | 63 | 167 | 314 | 523 | 800 | 1160 | 2244 | 3906 | 7092 | 15200
[6 empty] | 12 | 90 | 240 | 449 | 749 | 1150 | 1660 | 3306 | 5757 | 10452 | 22400
[6 empty] | 14 | 112 | 300 | 562 | 936 | 1430 | 2070 | 4177 | 7273 | 13205 | 28300
[6 empty] | 16 | 148 | 394 | 738 | 1230 | 1880 | 2720 | 5565 | 9689 | 17591 | 37700
[6 empty] | 18 | 188 | 502 | 942 | 1570 | 2400 | 3470 | 7085 | 12336 | 22397 | 48000
[6 empty] | 20 | 233 | 621 | 1160 | 1940 | 2790 | 4290 | 8782 | 15292 | 27763 | 59500
[6 empty] | 24 | 338 | 902 | 1690 | 2820 | 4310 | 6230 | 12738 | 22179 | 40268 | 86300
[6 empty] | 28 | 463 | 1240 | 2320 | 3860 | 5910 | 8530 | 17417 | 30326 | 55059 | 118000
[6 empty] | 30 | 533 | 1420 | 2660 | 4440 | 6790 | 9810 | 20074 | 34952 | 63458 | 136000
[6 empty] | 32 | 592 | 1580 | 2960 | 4942 | 7558 | 10915 | 22288 | 38807 | 70457 | 151000
[6 empty] | 36 | 752 | 2010 | 3760 | 6270 | 9590 | 13900 | 28339 | 49344 | 89587 | 192000
|  |  | REDUCED PORT BALL VALVES |  |  | TABLE NAME: | BALL_FP 10: BALL_RP; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  |  | Calc Cv | 39.6575 | [11 empty] | Calc Cv | 92.5767 | [11 empty] | Calc Cv | 136.2431
[6 empty] | Size, Inch | [11 empty] | Travel, % | Cv @ travel % | 0 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350 | Travel, % | Cv @ travel % | 0 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350 | Travel, % | Cv @ travel % | 0 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350 | bar: Valve Travel, % 40
[6 empty] | 0.5 | 0.1 | 0.2 | 0.4 | 0.7 | 1.2 | 1.9 | 2.7 | 4.2 | 6.3 | 9 |  |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100 |  | Travel % | 0 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
[6 empty] | 0.75 | 0.2 | 0.4 | 0.9 | 1.4 | 2.5 | 4 | 5.7 | 9 | 13 | 19 |  |  | M | 3.3333 | 2.5 | 1.25 | 0.90909 | 0.52632 | 0.34483 | 0.32258 | 0.16667 | 0.125 | 0.095238 |  |  | M | 3.3333 | 2.5 | 1.25 | 0.90909 | 0.52632 | 0.34483 | 0.32258 | 0.16667 | 0.125 | 0.095238 |  |  | M | 3.3333 | 2.5 | 1.25 | 0.90909 | 0.52632 | 0.34483 | 0.32258 | 0.16667 | 0.125 | 0.095238
[6 empty] | 1 | 0.4 | 0.9 | 2 | 3.4 | 5.8 | 9.5 | 13.5 | 21 | 32 | 45 |  |  |  | 132.1917 | 101.6438 | 60.8219 | 52.4159 | 47.1882 | 48.1578 | 48.9218 | 59.1096 | 64.3322 | 70.4436 |  |  |  | 308.5888 | 233.9416 | 126.9708 | 100.5242 | 75.0403 | 66.4057 | 65.9925 | 67.9294 | 70.9471 | 75.4835 |  |  |  | 454.1437 | 343.1078 | 181.5539 | 140.221 | 98.0227 | 81.4631 | 80.0784 | 75.2072 | 76.4054 | 79.6422
[6 empty] | 1.5 | 1.1 | 2.4 | 5.6 | 9.4 | 16 | 26 | 38 | 58 | 88 | 125 |  |  | Vlv Trav @ Cv | 47.1882 | [11 empty] | Vlv Trav @ Cv | 65.9925 | [11 empty] | Vlv Trav @ Cv | 75.2072
[6 empty] | 2 | 1.5 | 3.1 | 7.5 | 12 | 21 | 35 | 50 | 78 | 115 | 165
[6 empty] | 3 | 3 | 7 | 15 | 26 | 45 | 74 | 105 | 165 | 245 | 350
[6 empty] | 4 | 2 | 5 | 17 | 32 | 54 | 90 | 135 | 201 | 301 | 550
[6 empty] | 6 | 7 | 15 | 35 | 57 | 100 | 160 | 230 | 360 | 535 | 765
[6 empty] | 8 | 17 | 36 | 85 | 140 | 245 | 395 | 570 | 890 | 1325 | 1890
[6 empty] | 10 | 35 | 74 | 175 | 290 | 505 | 815 | 1180 | 1840 | 2735 | 3900
[6 empty] | 12 | 60 | 127 | 300 | 505 | 870 | 1400 | 2010 | 3150 | 4690 | 6700
[6 empty] | 14 | 42 | 102 | 240 | 400 | 700 | 1130 | 1620 | 2540 | 3780 | 5400
[6 empty] | 16 | 70 | 155 | 375 | 630 | 1100 | 1785 | 2550 | 3990 | 5950 | 8500
[6 empty] | 18 | 100 | 200 | 440 | 760 | 1275 | 2050 | 2940 | 4600 | 6860 | 9800
[6 empty] | 20 | 125 | 260 | 610 | 990 | 1700 | 2750 | 3900 | 6110 | 9100 | 13000
|  |  | SEGMENT BALL VALVES |  |  | TABLE NAME: | BALL_RP 10: BALL_SEG; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 1 | 0.52 | 1.13 | 2.23 | 3.83 | 5.95 | 8.58 | 11.7 | 16.2 | 24.1 | 45
[6 empty] | 1.5 | 1.33 | 3.27 | 6.44 | 11.1 | 17.2 | 24.8 | 33.9 | 46.5 | 69.3 | 110
[6 empty] | 2 | 2.05 | 5.07 | 10 | 17.2 | 26.6 | 38.4 | 52.5 | 72.4 | 108 | 180
[6 empty] | 2.5 | 3.26 | 8.02 | 15.9 | 27.3 | 42.3 | 61 | 83.4 | 114 | 170 | 280
[6 empty] | 3 | 4.73 | 11.6 | 23 | 39.4 | 61 | 88.2 | 121 | 165 | 246 | 420
[6 empty] | 4 | 7.57 | 18.6 | 36.8 | 63.1 | 97.7 | 141 | 193 | 264 | 393 | 620
[6 empty] | 6 | 13.9 | 34.1 | 67.2 | 115 | 178 | 258 | 352 | 484 | 719 | 1260
[6 empty] | 8 | 22.5 | 55.3 | 109 | 187 | 290 | 418 | 571 | 784 | 1164 | 2030
[6 empty] | 10 | 35.3 | 86.9 | 171 | 294 | 455 | 658 | 900 | 1236 | 1831 | 3210
[6 empty] | 12 | 49.8 | 123 | 243 | 418 | 648 | 937 | 1278 | 1754 | 2601 | 4490
[6 empty] | 14 | 63.9 | 158 | 311 | 534 | 827 | 1193 | 1628 | 2237 | 3320 | 6440
[6 empty] | 16 | 85.4 | 210 | 414 | 713 | 1106 | 1599 | 2180 | 2989 | 4432 | 8510
[6 empty] | 20 | 130.6 | 321 | 633 | 1090 | 1692 | 2446 | 3334 | 4571 | 6778 | 13020
[6 empty] | 24 | 198 | 486 | 958 | 1649 | 2560 | 3701 | 5045 | 6916 | 10255 | 19700
[6 empty] | 28 | 254 | 624 | 1230 | 2118 | 3288 | 4753 | 6479 | 8882 | 13171 | 25300
[6 empty] | 32 | 321 | 789 | 1556 | 2679 | 4159 | 6012 | 8195 | 11234 | 16659 | 32000
|  |  | HIGH PERFORMANCE BUTTERFLY |  |  | TABLE NAME: | BALL_SEG 10: HPBF_150; Valve Travel, % 40: Valve Travel, %
|  |  | VALVES CLASS 150 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 2.5 | 4 | 7 | 11 | 16 | 22 | 30 | 43 | 59 | 71 | 78
[6 empty] | 3 | 4 | 12 | 21 | 35 | 46 | 66 | 90 | 125 | 153 | 165
[6 empty] | 4 | 8 | 12 | 55 | 87 | 120 | 165 | 225 | 310 | 380 | 400
[6 empty] | 5 | 10 | 38 | 87 | 143 | 193 | 263 | 356 | 482 | 606 | 650
[6 empty] | 6 | 10 | 58 | 137 | 235 | 310 | 415 | 560 | 745 | 960 | 1050
[6 empty] | 8 | 15 | 130 | 315 | 475 | 695 | 970 | 1370 | 1865 | 2015 | 2200
[6 empty] | 10 | 25 | 155 | 340 | 540 | 835 | 1210 | 1665 | 2225 | 3030 | 3300
[6 empty] | 12 | 55 | 310 | 590 | 895 | 1410 | 2020 | 2790 | 3855 | 4900 | 5100
[6 empty] | 14 | 100 | 435 | 755 | 1220 | 1625 | 2320 | 3190 | 4410 | 5395 | 5800
[6 empty] | 16 | 165 | 630 | 1050 | 1530 | 2190 | 3080 | 4350 | 6100 | 7600 | 8000
[6 empty] | 18 | 285 | 790 | 1365 | 2200 | 2940 | 4200 | 5760 | 7970 | 9750 | 10500
[6 empty] | 20 | 350 | 880 | 1570 | 2540 | 3400 | 5080 | 7150 | 9450 | 12650 | 14000
[6 empty] | 24 | 405 | 1070 | 1980 | 3050 | 4430 | 6500 | 9550 | 13950 | 19100 | 21600
[6 empty] | 28 | 570 | 1562 | 2779 | 4200 | 6000 | 8700 | 12900 | 18882 | 26400 | 30000
[6 empty] | 30 | 650 | 1770 | 3150 | 4760 | 6800 | 9860 | 14620 | 21400 | 29920 | 34000
[6 empty] | 32 | 784 | 2134 | 3799 | 5740 | 8200 | 11890 | 17630 | 25806 | 36080 | 41000
[6 empty] | 36 | 1220 | 2980 | 5230 | 7650 | 11150 | 16100 | 23500 | 34100 | 49200 | 55500
[6 empty] | 40 | 1452 | 3893 | 6987 | 10481 | 15018 | 21688 | 32123 | 47278 | 65880 | 75000
[6 empty] | 42 | 1600 | 4290 | 7700 | 11550 | 16550 | 23900 | 35400 | 52100 | 72600 | 82650
[6 empty] | 48 | 2100 | 5600 | 10100 | 15200 | 21700 | 31400 | 46600 | 68200 | 95300 | 108300
[6 empty] | 54 | 2540 | 6950 | 12400 | 18700 | 26700 | 38700 | 57400 | 84100 | 117500 | 133500
[6 empty] | 56 | 2740 | 7497 | 13375 | 20171 | 28800 | 41744 | 61915 | 90715 | 126742 | 144000
[6 empty] | 60 | 3020 | 8270 | 14800 | 22250 | 31800 | 46100 | 68370 | 100200 | 139900 | 159000
|  |  | HIGH PERFORMANCE BUTTERFLY |  |  | TABLE NAME: | HPBF_150 10: HPBF_300; Valve Travel, % 40: Valve Travel, %
|  |  | VALVES CLASS 300 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 2.5 | 4 | 7 | 11 | 16 | 22 | 30 | 43 | 59 | 71 | 78
[6 empty] | 3 | 4 | 12 | 21 | 35 | 46 | 66 | 90 | 125 | 153 | 165
[6 empty] | 4 | 8 | 12 | 55 | 87 | 120 | 165 | 225 | 310 | 380 | 400
[6 empty] | 6 | 10 | 58 | 137 | 235 | 310 | 415 | 560 | 745 | 960 | 1050
[6 empty] | 8 | 12 | 115 | 260 | 390 | 570 | 795 | 1120 | 1525 | 1650 | 1800
[6 empty] | 10 | 20 | 145 | 325 | 515 | 795 | 1155 | 1590 | 2125 | 2890 | 3150
[6 empty] | 12 | 45 | 280 | 550 | 835 | 1315 | 1880 | 2600 | 3590 | 4570 | 4750
[6 empty] | 14 | 90 | 430 | 750 | 1200 | 1580 | 2250 | 3100 | 4300 | 5100 | 5200
[6 empty] | 16 | 150 | 620 | 1030 | 1500 | 2100 | 2950 | 4050 | 5450 | 6750 | 6900
[6 empty] | 18 | 280 | 780 | 1350 | 2100 | 2790 | 4000 | 5450 | 7350 | 8900 | 9300
[6 empty] | 20 | 340 | 870 | 1550 | 2510 | 3250 | 4800 | 6550 | 8250 | 10600 | 11300
[6 empty] | 24 | 400 | 1020 | 1920 | 2960 | 4300 | 6200 | 9000 | 12700 | 17400 | 18500
|  |  | HIGH PERFORMANCE BUTTERFLY |  |  | TABLE NAME: | HPBF_300 10: HPBF_600; Valve Travel, % 40: Valve Travel, %
|  |  | VALVES CLASS 600 |  |  |  | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
Size, Inch | bar: Valve Travel, % 40
[6 empty] | 3 | 4 | 11 | 20 | 33 | 43 | 62 | 85 | 117 | 144 | 155
[6 empty] | 4 | 5 | 16 | 36 | 57 | 78 | 107 | 146 | 202 | 247 | 260
[6 empty] | 6 | 7 | 41 | 98 | 168 | 221 | 296 | 400 | 532 | 686 | 750
[6 empty] | 8 | 9 | 86 | 195 | 293 | 428 | 596 | 840 | 1144 | 1238 | 1350
[6 empty] | 10 | 13 | 97 | 217 | 343 | 530 | 770 | 1060 | 1417 | 1927 | 2100
[6 empty] | 12 | 27 | 171 | 336 | 510 | 803 | 1148 | 1587 | 2192 | 2790 | 2900
[6 empty] | 14 | 69 | 331 | 577 | 923 | 1215 | 1731 | 2385 | 3308 | 3923 | 4000
[6 empty] | 16 | 111 | 458 | 761 | 1109 | 1552 | 2180 | 2993 | 4028 | 4989 | 5100
[6 empty] | 18 | 166 | 461 | 798 | 1242 | 1650 | 2366 | 3223 | 4347 | 5263 | 5500
[6 empty] | 20 | 239 | 612 | 1090 | 1766 | 2287 | 3377 | 4608 | 5804 | 7458 | 7950
[6 empty] | 24 | 244 | 623 | 1173 | 1808 | 2626 | 3787 | 5497 | 7757 | 10628 | 11300
|  |  | GLOBE CAGE GUIDED EQUALL PERCENT |  |  | TABLE NAME: | HPBF_600 10: GC_EQ; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 |  |  | 2 | 2 | 4 | 6 | 9 | 14 | 21 | 33 | 50 | 66 | 71
|  |  | sizes reduced. |  |  | 2.01 | 1.1 | 3.3 | 5.5 | 7.6 | 9.8 | 12.8 | 17.9 | 26.3 | 39.7 | 50
[6 empty] | 2.02 | 0.6 | 1.2 | 1.6 | 2.5 | 4.6 | 8.2 | 12.9 | 17.7 | 21.6 | 24
[6 empty] | 2.03 | 0.3 | 0.7 | 0.9 | 1.5 | 2.7 | 4.8 | 7.5 | 10.4 | 12.6 | 14
[6 empty] | 3 | 4 | 8.5 | 14.5 | 22 | 33.5 | 51 | 75 | 108 | 128 | 138
[6 empty] | 3.01 | 2.5 | 3.7 | 6.6 | 11.1 | 18.4 | 29.4 | 45.6 | 67.7 | 92 | 110
[6 empty] | 3.02 | 1.2 | 2.5 | 3.3 | 5.2 | 9.5 | 17 | 26.8 | 37 | 45 | 50
[6 empty] | 3.03 | 0.8 | 1.6 | 2.1 | 3.3 | 6.1 | 10.9 | 17.2 | 23.7 | 28.8 | 32
[6 empty] | 4 | 5.6 | 12.9 | 23.4 | 36.9 | 59.6 | 86.5 | 128.2 | 163.9 | 188.6 | 210
[6 empty] | 4.01 | 2.8 | 6.7 | 11.7 | 17.9 | 28.6 | 46.2 | 71.9 | 105.8 | 141.2 | 160
[6 empty] | 4.02 | 2 | 4.1 | 5.5 | 8.5 | 15.6 | 27.9 | 44 | 60.6 | 73.8 | 82
[6 empty] | 4.03 | 1.2 | 2.5 | 3.3 | 5.2 | 9.5 | 17 | 26.8 | 37 | 45 | 50
[6 empty] | 6 | 6.5 | 15 | 27.7 | 47.1 | 77.1 | 123.8 | 198.5 | 265.2 | 316 | 340
[6 empty] | 6.01 | 3.4 | 11.1 | 22 | 32.3 | 50.4 | 81.7 | 126.8 | 187.4 | 246.3 | 270
[6 empty] | 6.02 | 3.3 | 6.8 | 9.1 | 14.1 | 25.9 | 46.2 | 73 | 100.5 | 122.3 | 136
[6 empty] | 6.03 | 2 | 4.1 | 5.5 | 8.5 | 15.6 | 27.9 | 44 | 60.6 | 73.8 | 82
[6 empty] | 8 | 6.5 | 23 | 45 | 83 | 138 | 220 | 325 | 445 | 510 | 560
[6 empty] | 8.01 | 5.6 | 19 | 39 | 58 | 94 | 148 | 222 | 310 | 405 | 450
[6 empty] | 8.02 | 4 | 11.7 | 15.8 | 24.4 | 44.9 | 80.2 | 126.6 | 174.5 | 212.3 | 236
[6 empty] | 8.03 | 3 | 7.1 | 9.5 | 14.7 | 27 | 48.3 | 76.2 | 105 | 127.7 | 142
[6 empty] | 10 | 8.1 | 33.2 | 65.7 | 124.4 | 216.8 | 350.1 | 493.2 | 619.9 | 747.6 | 830
[6 empty] | 10.01 | 6.5 | 26.5 | 47.1 | 76.2 | 126.3 | 219.8 | 343.2 | 460 | 566.2 | 655
[6 empty] | 10.02 | 6.1 | 18.6 | 25 | 38.7 | 71.2 | 127.2 | 200.6 | 276.5 | 336.4 | 374
[6 empty] | 10.03 | 5.5 | 11.1 | 15 | 23.2 | 42.6 | 76.2 | 120.2 | 165.6 | 201.5 | 224
[6 empty] | 12 | 22.4 | 64.3 | 111.1 | 179.8 | 303.1 | 546.8 | 795 | 996 | 1155 | 1240
[6 empty] | 12.01 | 15.5 | 44.7 | 73.7 | 110.5 | 174.2 | 277.6 | 441.3 | 650.5 | 837.5 | 960
[6 empty] | 12.02 | 12.8 | 26 | 35 | 54.2 | 99.7 | 178.1 | 281.1 | 387.4 | 471.4 | 524
[6 empty] | 12.03 | 7.7 | 15.6 | 21 | 32.5 | 59.8 | 106.8 | 168.4 | 232.1 | 282.5 | 314
[6 empty] | 14 | 24.7 | 82.3 | 158.3 | 266.7 | 427 | 693.9 | 1015.8 | 1277.2 | 1514.7 | 1650
[6 empty] | 14.01 | 18.9 | 60.2 | 103.2 | 164.8 | 260.6 | 405.5 | 630.9 | 903.9 | 1141.5 | 1275
[6 empty] | 14.02 | 16.2 | 37.1 | 49.8 | 77.1 | 142 | 253.6 | 400.2 | 551.5 | 671.1 | 746
[6 empty] | 14.03 | 10.9 | 22.2 | 29.8 | 46.1 | 84.9 | 151.6 | 239.2 | 329.7 | 401.2 | 446
[6 empty] | 16 | 35.1 | 100.4 | 167 | 268.4 | 471 | 849.3 | 1265.1 | 1603.9 | 1911.6 | 2090
[6 empty] | 16.01 | 26.3 | 73 | 119.6 | 175.7 | 287 | 477.7 | 773.1 | 1125.4 | 1432.4 | 1680
[6 empty] | 16.02 | 20.9 | 42.4 | 57 | 88.3 | 162.6 | 290.3 | 458.1 | 631.4 | 768.2 | 854
[6 empty] | 16.03 | 12.5 | 25.4 | 34.2 | 52.9 | 97.5 | 174.1 | 274.7 | 378.5 | 460.6 | 512
[6 empty] | 18 | 45.3 | 129.7 | 215.7 | 346.7 | 608.5 | 1097.2 | 1634.3 | 2072 | 2469.5 | 2700
[6 empty] | 18.01 | 29.8 | 82.6 | 135.2 | 198.7 | 324.6 | 540.3 | 874.3 | 1272.8 | 1620 | 1900
[6 empty] | 18.02 | 27.8 | 56.6 | 76.1 | 117.8 | 217 | 387.6 | 611.5 | 842.8 | 1025.5 | 1140
[6 empty] | 18.03 | 16.6 | 33.8 | 45.4 | 70.3 | 129.4 | 231.2 | 364.8 | 502.7 | 611.7 | 680
[6 empty] | 20 | 60.5 | 172.9 | 287.7 | 462.3 | 811.3 | 1462.9 | 2179.1 | 2762.7 | 3292.7 | 3600
[6 empty] | 20.01 | 39.2 | 108.7 | 177.9 | 261.5 | 427.1 | 710.9 | 1150.4 | 1674.7 | 2131.6 | 2500
[6 empty] | 20.02 | 36.6 | 74.5 | 100.2 | 155 | 285.5 | 509.9 | 804.6 | 1108.9 | 1349.3 | 1500
[6 empty] | 20.03 | 22 | 44.7 | 60.1 | 93 | 171.3 | 306 | 482.8 | 665.4 | 809.6 | 900
[6 empty] | 24 | 87.3 | 249.8 | 415.5 | 667.8 | 1171.9 | 2113.1 | 3147.6 | 3990.6 | 4756.1 | 5200
[6 empty] | 24.01 | 57.2 | 158.7 | 259.7 | 381.7 | 623.5 | 1037.9 | 1679.6 | 2445.1 | 3112.1 | 3650
[6 empty] | 24.03 | 53.7 | 109.3 | 146.9 | 227.4 | 418.7 | 747.9 | 1180.1 | 1626.4 | 1979 | 2200
[6 empty] | 24.03 | 31.7 | 64.6 | 86.8 | 134.4 | 247.5 | 441.9 | 697.4 | 961.1 | 1169.4 | 1300
|  |  | GLOBE CAGE GUIDED LINEAR |  |  | TABLE NAME: | GC_EQ 10: GC_LIN; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 |  |  | 2 | 4.9 | 13.9 | 22.2 | 30.3 | 39.5 | 48.6 | 57.3 | 64.7 | 69.5 | 74
|  |  | sizes reduced. |  |  | 2.01 | 3.5 | 7.6 | 12.5 | 17.3 | 22.4 | 27.6 | 33.1 | 38.5 | 43.6 | 48
[6 empty] | 2.02 | 2.6 | 5.2 | 7.7 | 10.3 | 12.9 | 15.4 | 18 | 20.6 | 23.2 | 26
[6 empty] | 2.03 | 1.6 | 3.2 | 4.8 | 6.3 | 7.9 | 9.5 | 11.1 | 12.7 | 14.3 | 16
[6 empty] | 3 | 8 | 22 | 39 | 59 | 75 | 90 | 105 | 119 | 130 | 142
[6 empty] | 3.01 | 6.2 | 16.6 | 26.9 | 36.9 | 46.6 | 56.8 | 67.4 | 78 | 87.8 | 98
[6 empty] | 3.02 | 4.5 | 11.1 | 16.6 | 22.2 | 27.7 | 33.3 | 38.8 | 44.4 | 49.9 | 56
[6 empty] | 3.03 | 3.4 | 6.7 | 10.1 | 13.5 | 16.8 | 20.2 | 23.6 | 26.9 | 30.3 | 34
[6 empty] | 4 | 19.3 | 41.5 | 74.4 | 105.3 | 133.4 | 164.5 | 187.6 | 206.4 | 219.3 | 230
[6 empty] | 4.01 | 8 | 25.4 | 43.1 | 60.4 | 77.2 | 93.8 | 110.7 | 127.6 | 143.9 | 160
[6 empty] | 4.02 | 6 | 17 | 25.5 | 34.1 | 42.6 | 51.1 | 59.6 | 68.1 | 76.6 | 86
[6 empty] | 4.03 | 5.2 | 10.3 | 15.4 | 20.6 | 25.7 | 30.9 | 36 | 41.2 | 46.3 | 52
[6 empty] | 6 | 23 | 62 | 123.5 | 181 | 229.1 | 269.3 | 315.2 | 349.9 | 370.1 | 380
[6 empty] | 6.01 | 12 | 40.9 | 71.4 | 101.4 | 130.6 | 158.9 | 186.7 | 214.7 | 242.2 | 275
[6 empty] | 6.02 | 9.5 | 29.7 | 44.6 | 59.4 | 74.3 | 89.1 | 104 | 118.8 | 133.7 | 150
[6 empty] | 6.03 | 8 | 17.8 | 26.7 | 35.6 | 44.6 | 53.5 | 62.4 | 71.3 | 80.2 | 90
[6 empty] | 8 | 28.2 | 94.2 | 185.6 | 288 | 377.1 | 449.1 | 514.1 | 571.9 | 590 | 600
[6 empty] | 8.01 | 14.5 | 52.5 | 108 | 172 | 232 | 299 | 365 | 417 | 430 | 455
[6 empty] | 8.02 | 10 | 45 | 75.4 | 100.6 | 125.7 | 150.9 | 176 | 201.2 | 226.3 | 254
[6 empty] | 8.03 | 9 | 30.1 | 45.1 | 60.2 | 75.2 | 90.3 | 105.3 | 120.4 | 135.4 | 152
[6 empty] | 10 | 45.9 | 189.3 | 329.3 | 461.8 | 583.3 | 689.9 | 778.5 | 847.7 | 897.9 | 950
[6 empty] | 10.01 | 25 | 103.6 | 183.3 | 260.7 | 337.5 | 414.1 | 489.4 | 562.3 | 631.5 | 700
[6 empty] | 10.02 | 17 | 78.8 | 118.2 | 157.6 | 197 | 236.4 | 275.8 | 315.2 | 354.6 | 398
[6 empty] | 10.03 | 12 | 46.7 | 70.1 | 93.5 | 116.8 | 140.2 | 163.6 | 186.9 | 210.3 | 238
[6 empty] | 12 | 93.2 | 250 | 463.3 | 660 | 840 | 990 | 1115 | 1205 | 1250 | 1270
[6 empty] | 12.01 | 66.7 | 167.8 | 276.8 | 382.9 | 485.5 | 586.9 | 692.1 | 796.9 | 893 | 970
[6 empty] | 12.02 | 25 | 108.9 | 163.4 | 218 | 272.3 | 326.7 | 381.2 | 435.6 | 490.1 | 550
[6 empty] | 12.03 | 17 | 67.3 | 101 | 134.6 | 168.3 | 202 | 235.6 | 269.3 | 302.9 | 340
[6 empty] | 14.01 | 127.4 | 407.5 | 673.4 | 915.6 | 1128.5 | 1316.5 | 1474.2 | 1593.1 | 1671.4 | 1740
[6 empty] | 14.01 | 91.3 | 233.3 | 393 | 548.1 | 696.8 | 838 | 976.4 | 1105.4 | 1221.2 | 1300
[6 empty] | 14.02 | 52 | 153.7 | 230.5 | 307.3 | 384.1 | 460.9 | 537.8 | 614.6 | 691.4 | 776
[6 empty] | 14.03 | 27 | 91.9 | 137.8 | 183.7 | 229.7 | 275.6 | 321.6 | 367.5 | 413.4 | 464
[6 empty] | 16 | 189 | 497 | 891.8 | 1248 | 1535.4 | 1791.5 | 1950 | 2063 | 2161.6 | 2215
[6 empty] | 16.01 | 101.3 | 276.5 | 448.1 | 615 | 779.1 | 941.9 | 1101.6 | 1255.7 | 1398.9 | 1530
[6 empty] | 16.02 | 71 | 186.1 | 279.2 | 372.2 | 465.3 | 558.4 | 651.4 | 744.5 | 837.5 | 940
[6 empty] | 16.03 | 47 | 112.5 | 168.7 | 224.9 | 281.2 | 337.4 | 393.6 | 449.9 | 506.1 | 568
[6 empty] | 18 | 230.4 | 605.8 | 1087.1 | 1521.3 | 1871.6 | 2183.8 | 2377 | 2514.7 | 2634.9 | 2700
[6 empty] | 18.01 | 125.8 | 343.4 | 556.4 | 763.8 | 967.6 | 1169.7 | 1368 | 1559.4 | 1737.2 | 1900
[6 empty] | 18.02 | 86.1 | 225.7 | 338.6 | 451.4 | 564.3 | 677.2 | 790 | 902.9 | 1015.7 | 1140
[6 empty] | 18.03 | 56.3 | 134.6 | 202 | 269.3 | 336.6 | 403.9 | 471.2 | 538.6 | 605.9 | 680
[6 empty] | 20 | 307.2 | 807.8 | 1449.4 | 2028.4 | 2495.5 | 2911.7 | 3169.3 | 3353 | 3513.2 | 3600
[6 empty] | 20.01 | 165.5 | 451.8 | 732.1 | 1005 | 1273.1 | 1539 | 1800 | 2051.8 | 2285.8 | 2500
[6 empty] | 20.02 | 113.3 | 297 | 445.5 | 594 | 742.5 | 891 | 1039.5 | 1188 | 1336.5 | 1500
[6 empty] | 20.03 | 74.5 | 178.2 | 267.3 | 356.4 | 445.5 | 534.6 | 623.7 | 712.8 | 801.9 | 900
[6 empty] | 24 | 443.7 | 1166.8 | 2093.6 | 2929.8 | 3604.6 | 4205.8 | 4577.9 | 4843.2 | 5074.6 | 5200
[6 empty] | 24.01 | 241.6 | 659.6 | 1068.9 | 1467.3 | 1858.7 | 2247 | 2628 | 2995.6 | 3337.2 | 3650
[6 empty] | 24.02 | 166.2 | 435.6 | 653.4 | 871.2 | 1089 | 1306.8 | 1524.6 | 1742.4 | 1960.2 | 2200
[6 empty] | 24.03 | 107.6 | 257.4 | 386.1 | 514.8 | 643.5 | 772.2 | 900.9 | 1029.6 | 1158.3 | 1300
|  |  | GLOBE PARABOLIC PLUG EQUAL % |  |  | 20.03: TABLE NAME:; 74.5: GP_EQ; 356.4: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 … |  |  | 0.5 | 0.164 | 0.355 | 0.562 | 0.888 | 1.378 | 2.163 | 3.417 | 4.842 | 6.441 | 7
|  |  | sizes reduced. |  |  | 0.501 | 0.057 | 0.159 | 0.307 | 0.488 | 0.78 | 1.456 | 2.173 | 2.884 | 3.533 | 4
[6 empty] | 0.502 | 0.083 | 0.155 | 0.228 | 0.336 | 0.585 | 0.941 | 1.37 | 1.702 | 2.005 | 2.3
[6 empty] | 0.503 | 0.048 | 0.092 | 0.137 | 0.202 | 0.35 | 0.56 | 0.818 | 1.113 | 1.329 | 1.5
[6 empty] | 0.504 | 0.02 | 0.037 | 0.057 | 0.083 | 0.161 | 0.28 | 0.413 | 0.538 | 0.656 | 0.8
[6 empty] | 0.505 | 0.009 | 0.022 | 0.035 | 0.054 | 0.096 | 0.168 | 0.253 | 0.334 | 0.414 | 0.5
[6 empty] | 0.506 | 0.005 | 0.011 | 0.02 | 0.033 | 0.063 | 0.105 | 0.15 | 0.197 | 0.245 | 0.3
[6 empty] | 0.75 | 0.239 | 0.452 | 0.668 | 1.069 | 1.849 | 2.928 | 4.022 | 5.229 | 7.131 | 9
[6 empty] | 0.751 | 0.057 | 0.198 | 0.399 | 0.669 | 1.109 | 1.785 | 2.787 | 3.712 | 4.739 | 5.5
[6 empty] | 0.752 | 0.05 | 0.169 | 0.276 | 0.453 | 0.776 | 1.204 | 1.802 | 2.352 | 2.723 | 3
[6 empty] | 0.753 | 0.044 | 0.093 | 0.15 | 0.214 | 0.405 | 0.684 | 0.999 | 1.299 | 1.667 | 2
[6 empty] | 0.754 | 0.034 | 0.061 | 0.086 | 0.131 | 0.248 | 0.418 | 0.62 | 0.817 | 1.011 | 1.2
[6 empty] | 0.755 | 0.012 | 0.029 | 0.051 | 0.082 | 0.142 | 0.234 | 0.34 | 0.451 | 0.58 | 0.7
[6 empty] | 0.756 | 0.009 | 0.019 | 0.03 | 0.044 | 0.082 | 0.141 | 0.207 | 0.271 | 0.333 | 0.4
[6 empty] | 1 | 0.268 | 0.568 | 0.913 | 1.549 | 2.754 | 4.657 | 7.075 | 9.487 | 11.626 | 13.5
[6 empty] | 1.001 | 0.118 | 0.287 | 0.507 | 0.825 | 1.557 | 2.695 | 4.14 | 5.605 | 7.028 | 8.5
[6 empty] | 1.002 | 0.073 | 0.185 | 0.331 | 0.525 | 0.966 | 1.672 | 2.647 | 3.588 | 4.366 | 5.4
[6 empty] | 1.003 | 0.027 | 0.09 | 0.186 | 0.317 | 0.583 | 0.997 | 1.52 | 2.05 | 2.54 | 3.1
[6 empty] | 1.004 | 0.03 | 0.075 | 0.134 | 0.215 | 0.397 | 0.67 | 1.002 | 1.354 | 1.701 | 2
[6 empty] | 1.005 | 0.025 | 0.053 | 0.077 | 0.131 | 0.248 | 0.433 | 0.643 | 0.853 | 1.056 | 1.2
[6 empty] | 1.006 | 0.011 | 0.025 | 0.041 | 0.073 | 0.143 | 0.239 | 0.345 | 0.462 | 0.589 | 0.8
[6 empty] | 1.5 | 0.453 | 1.124 | 2 | 3.071 | 5.909 | 10.566 | 16.175 | 21.567 | 25.661 | 28
[6 empty] | 1.501 | 0.226 | 0.582 | 1.056 | 1.694 | 3.155 | 5.364 | 7.974 | 10.692 | 13.438 | 16
[6 empty] | 1.502 | 0.203 | 0.437 | 0.705 | 1.021 | 1.877 | 3.245 | 4.93 | 6.712 | 8.593 | 10.5
[6 empty] | 1.503 | 0.086 | 0.219 | 0.398 | 0.617 | 1.131 | 2.022 | 3.169 | 4.256 | 5.211 | 6
[6 empty] | 1.504 | 0.053 | 0.141 | 0.262 | 0.412 | 0.789 | 1.363 | 2.078 | 2.828 | 3.453 | 4
[6 empty] | 1.505 | 0.031 | 0.076 | 0.134 | 0.21 | 0.391 | 0.691 | 1.071 | 1.431 | 1.736 | 2.2
[6 empty] | 1.506 | 0.027 | 0.056 | 0.085 | 0.128 | 0.234 | 0.396 | 0.588 | 0.784 | 0.981 | 1.2
[6 empty] | 2 | 1.209 | 2.459 | 3.305 | 5.116 | 9.421 | 16.828 | 26.55 | 36.591 | 44.523 | 49
[6 empty] | 2.01 | 0.315 | 0.817 | 1.505 | 2.87 | 5.482 | 9.305 | 13.774 | 18.306 | 23.17 | 28
[6 empty] | 2.02 | 0.171 | 0.467 | 0.882 | 1.633 | 3.179 | 5.473 | 8.207 | 11.089 | 13.683 | 17
[6 empty] | 2.03 | 0.146 | 0.369 | 0.662 | 1.023 | 1.894 | 3.286 | 5.007 | 6.711 | 8.407 | 10
[6 empty] | 3 | 2.007 | 4.467 | 7.366 | 12.276 | 22.522 | 38.624 | 62.018 | 79.573 | 90.094 | 100
[6 empty] | 3.01 | 1.004 | 2.505 | 4.499 | 6.963 | 12.945 | 23.649 | 36.145 | 47.819 | 58.698 | 70
[6 empty] | 3.02 | 0.727 | 1.606 | 2.636 | 3.946 | 7.53 | 13.569 | 21.257 | 28.974 | 34.99 | 42
[6 empty] | 3.03 | 0.355 | 0.887 | 1.588 | 2.455 | 4.505 | 8.075 | 12.547 | 16.822 | 20.779 | 25
[6 empty] | 4 | 2.896 | 6.719 | 11.479 | 17.159 | 29.352 | 56.255 | 86.653 | 120.896 | 153.844 | 190
[6 empty] | 4.01 | 1.558 | 3.765 | 6.626 | 10.108 | 18.418 | 32.827 | 55.269 | 77.526 | 98.631 | 120
[6 empty] | 4.02 | 1.45 | 3.05 | 4.822 | 8.099 | 14.857 | 24.2 | 35.222 | 49.808 | 61.142 | 72
[6 empty] | 4.03 | 0.882 | 1.818 | 2.839 | 4.443 | 8.424 | 14.384 | 21.124 | 27.793 | 34.167 | 42
[6 empty] | 6 | 4.225 | 9.715 | 16.432 | 25.732 | 49.583 | 89.691 | 140.008 | 195.766 | 256.778 | 295
[6 empty] | 6.01 | 2.829 | 6.733 | 11.683 | 17.723 | 31.528 | 53.903 | 88.375 | 113.113 | 140.553 | 165
[6 empty] | 6.02 | 1.364 | 3.606 | 6.678 | 10.62 | 17.821 | 28.656 | 42.883 | 57.38 | 71.534 | 85
[6 empty] | 6.03 | 0.911 | 1.895 | 2.949 | 4.261 | 7.768 | 13.68 | 21.418 | 29.715 | 37.963 | 50
|  |  | GLOBE PARABOLIC PLUG LINEAR |  |  | TABLE NAME: | GP_EQ 10: GP_LIN; Valve Travel, % 40: Valve Travel, %
[7 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  | Decimal sizes N.01, N.02, N.03 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  | represent "N" inch valve , 1, 2, 3 … |  |  | 0.5 | 0.531 | 1.268 | 1.949 | 2.659 | 3.377 | 4.085 | 4.764 | 5.51 | 6.672 | 7
|  |  | sizes reduced. |  |  | 0.501 | 0.358 | 0.744 | 1.225 | 1.61 | 1.992 | 2.365 | 2.719 | 3.049 | 3.411 | 4
[6 empty] | 0.502 | 0.278 | 0.532 | 0.785 | 1.069 | 1.319 | 1.52 | 1.707 | 1.879 | 2.033 | 2.3
[6 empty] | 0.503 | 0.19 | 0.356 | 0.515 | 0.669 | 0.819 | 0.971 | 1.15 | 1.275 | 1.377 | 1.5
[6 empty] | 0.504 | 0.092 | 0.172 | 0.249 | 0.324 | 0.397 | 0.47 | 0.542 | 0.612 | 0.683 | 0.8
[6 empty] | 0.505 | 0.055 | 0.105 | 0.154 | 0.202 | 0.251 | 0.3 | 0.351 | 0.401 | 0.452 | 0.5
[6 empty] | 0.506 | 0.035 | 0.065 | 0.095 | 0.124 | 0.153 | 0.182 | 0.211 | 0.24 | 0.27 | 0.3
[6 empty] | 0.75 | 0.845 | 1.678 | 2.573 | 3.311 | 4.036 | 4.743 | 5.425 | 6.179 | 7.609 | 9
[6 empty] | 0.751 | 0.347 | 0.819 | 1.402 | 2.167 | 2.779 | 3.388 | 3.977 | 4.53 | 5.031 | 5.5
[6 empty] | 0.752 | 0.294 | 0.742 | 1.078 | 1.403 | 1.731 | 2.125 | 2.372 | 2.597 | 2.799 | 3
[6 empty] | 0.753 | 0.237 | 0.438 | 0.628 | 0.811 | 0.987 | 1.155 | 1.317 | 1.47 | 1.615 | 2
[6 empty] | 0.754 | 0.125 | 0.241 | 0.358 | 0.478 | 0.599 | 0.721 | 0.842 | 0.964 | 1.084 | 1.2
[6 empty] | 0.755 | 0.078 | 0.148 | 0.215 | 0.284 | 0.352 | 0.42 | 0.49 | 0.559 | 0.63 | 0.7
[6 empty] | 0.756 | 0.048 | 0.089 | 0.129 | 0.169 | 0.207 | 0.245 | 0.284 | 0.322 | 0.36 | 0.4
[6 empty] | 1 | 1.288 | 2.619 | 4.023 | 5.415 | 6.826 | 8.125 | 8.899 | 10.246 | 11.931 | 13.5
[6 empty] | 1.001 | 0.773 | 1.538 | 2.307 | 3.147 | 3.919 | 4.679 | 5.415 | 6.122 | 7.003 | 8.5
[6 empty] | 1.002 | 0.463 | 0.939 | 1.433 | 1.937 | 2.458 | 3.02 | 3.519 | 3.997 | 4.441 | 5.4
[6 empty] | 1.003 | 0.277 | 0.562 | 0.857 | 1.16 | 1.468 | 1.772 | 2.071 | 2.358 | 2.658 | 3.1
[6 empty] | 1.004 | 0.178 | 0.367 | 0.566 | 0.775 | 0.988 | 1.201 | 1.408 | 1.606 | 1.789 | 2
[6 empty] | 1.005 | 0.114 | 0.23 | 0.348 | 0.468 | 0.589 | 0.711 | 0.831 | 0.949 | 1.065 | 1.2
[6 empty] | 1.006 | 0.07 | 0.138 | 0.207 | 0.276 | 0.344 | 0.413 | 0.482 | 0.55 | 0.619 | 0.8
[6 empty] | 1.5 | 2.636 | 5.382 | 8.457 | 11.766 | 15.22 | 18.767 | 21.562 | 24.09 | 26.5 | 28
[6 empty] | 1.501 | 1.625 | 3.16 | 4.699 | 6.25 | 7.896 | 9.519 | 11.12 | 12.681 | 14.181 | 16
[6 empty] | 1.502 | 0.946 | 1.885 | 2.86 | 3.86 | 4.875 | 5.884 | 6.901 | 7.918 | 8.855 | 10.5
[6 empty] | 1.503 | 0.565 | 1.128 | 1.72 | 2.333 | 2.955 | 3.579 | 4.19 | 4.779 | 5.332 | 6
[6 empty] | 1.504 | 0.369 | 0.743 | 1.135 | 1.543 | 1.961 | 2.379 | 2.788 | 3.182 | 3.549 | 4
[6 empty] | 1.505 | 0.188 | 0.377 | 0.573 | 0.777 | 0.985 | 1.194 | 1.4 | 1.598 | 1.784 | 2.2
[6 empty] | 1.506 | 0.123 | 0.239 | 0.355 | 0.472 | 0.59 | 0.71 | 0.828 | 0.946 | 1.063 | 1.2
[6 empty] | 2 | 4.13 | 9.242 | 14.478 | 19.708 | 25.087 | 30.564 | 35.974 | 40.012 | 44.642 | 49
[6 empty] | 2.01 | 2.274 | 4.969 | 7.877 | 10.938 | 13.724 | 16.509 | 19.277 | 22.026 | 24.965 | 28
[6 empty] | 2.02 | 1.264 | 2.764 | 4.372 | 6.054 | 7.773 | 9.527 | 11.227 | 12.727 | 14.317 | 17
[6 empty] | 2.03 | 0.816 | 1.779 | 2.804 | 3.86 | 4.927 | 5.981 | 7.006 | 7.98 | 8.889 | 10
[6 empty] | 3 | 9.958 | 21.061 | 32.395 | 42.652 | 52.98 | 63.698 | 76.666 | 86.071 | 91.149 | 100
[6 empty] | 3.01 | 5.353 | 11.637 | 18.738 | 26.583 | 33.661 | 40.457 | 47.179 | 53.741 | 60.338 | 70
[6 empty] | 3.02 | 3.465 | 7.212 | 11.2 | 15.378 | 19.686 | 24.058 | 28.448 | 31.986 | 35.659 | 42
[6 empty] | 3.03 | 2.171 | 4.467 | 6.858 | 9.318 | 11.806 | 14.291 | 16.726 | 19.075 | 21.29 | 25
[6 empty] | 4 | 12.667 | 27.122 | 47.273 | 66.038 | 85.993 | 106.882 | 127.853 | 147.47 | 167.929 | 190
[6 empty] | 4.01 | 7.319 | 15.766 | 25.332 | 36.426 | 51.054 | 63.296 | 75.776 | 88.317 | 103.943 | 120
[6 empty] | 4.02 | 7.018 | 13.838 | 20.643 | 27.411 | 34.071 | 43.442 | 50.854 | 57.09 | 63.09 | 72
[6 empty] | 4.03 | 4.032 | 8.164 | 12.452 | 16.817 | 21.179 | 25.44 | 29.513 | 33.306 | 37.671 | 42
[6 empty] | 6 | 28.431 | 57.146 | 86.052 | 112.257 | 136.072 | 159.161 | 181.587 | 212.574 | 263.118 | 295
[6 empty] | 6.01 | 16.09 | 32.01 | 47.67 | 63.09 | 78.18 | 93.11 | 105.76 | 117.42 | 137.91 | 165
[6 empty] | 6.02 | 8.775 | 17.429 | 25.904 | 34.147 | 42.126 | 49.781 | 57.066 | 63.938 | 71.485 | 85
[6 empty] | 6.03 | 4.321 | 9.065 | 14.143 | 19.449 | 24.875 | 30.315 | 35.638 | 40.718 | 45.424 | 50
|  |  |  | ECCENTRIC ROTARY PLUG |  |  | GP_LIN 10: TABLE NAME:; GP_LIN 20: ROT_PLUG; Valve Travel, % 50: Valve Travel, %
[8 empty] | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
|  |  |  | Decimal sizes N.01 |  |  | Size, Inch | bar: Valve Travel, % 40
|  |  |  | represent "N" inch valve , 1 |  |  | 1 | 1.09 | 2.01 | 2.97 | 3.86 | 4.97 | 6.19 | 8.04 | 10.1 | 12.4 | 14.5
|  |  |  | size reduced. |  |  | 1.01 | 0.74 | 1.65 | 2.13 | 2.66 | 3.18 | 3.72 | 4.58 | 5.72 | 7.01 | 7.9
[7 empty] | 1.5 | 2.1 | 4.6 | 7.5 | 10.2 | 13.7 | 17.6 | 21.7 | 26 | 29.4 | 31
[7 empty] | 1.51 | 2.1 | 4.6 | 6.2 | 7.4 | 9.4 | 11.4 | 13.5 | 14.8 | 15.2 | 15.5
[7 empty] | 2 | 4.3 | 9 | 14 | 19 | 25 | 31 | 39 | 45 | 50 | 52
[7 empty] | 2.01 | 3.8 | 8 | 10 | 13 | 16 | 19 | 23 | 25 | 25.5 | 26
[7 empty] | 3 | 10 | 20 | 30 | 41 | 52 | 66 | 85 | 103 | 121 | 137
[7 empty] | 3.01 | 10 | 20 | 26 | 32 | 40 | 48 | 57 | 63 | 65 | 66
[7 empty] | 4 | 17 | 35 | 50 | 70 | 89 | 113 | 145 | 176 | 206 | 239
[7 empty] | 4.01 | 17 | 35 | 48 | 58 | 73 | 88 | 104 | 114 | 117 | 120
[7 empty] | 6 | 49 | 103 | 160 | 216 | 272 | 328 | 380 | 434 | 485 | 520
[7 empty] | 6.01 | 37 | 75 | 104 | 125 | 158 | 191 | 226 | 247 | 254 | 260
[7 empty] | 8 | 75 | 151 | 220 | 301 | 388 | 499 | 603 | 719 | 823 | 870
[7 empty] | 8.01 | 58 | 128 | 175 | 211 | 267 | 323 | 383 | 419 | 431 | 440
[7 empty] | 10 | 115 | 231 | 336 | 460 | 593 | 763 | 922 | 1099 | 1258 | 1330
[7 empty] | 10.01 | 85 | 188 | 271 | 326 | 412 | 500 | 592 | 647 | 666 | 680

## Wall Thck.
NO USER INPUT IS REQUIRED FOR THIS TAB.
PIPE WALL THICKNESS
Note: this data is believed to be accurate, but it is the user's responsibility to determine its applicability to their purpose.
| NPS | Outside Diameter | Schedule
| (in) | (in) (mm) | 10 | 20 | 30 | STD | 40 | 60 | XS | 80 | 100 | 120 | 140 | 160 | XXS
Wall Thickness (in) (mm)
| 1/8 | 0.405 |  |  |  | 0.068 | 0.068 |  | 0.095 | 0.095
|  | 10.3 |  |  |  | 1.73 | 1.73 |  | 2.41 | 2.41
| 1/4 | 0.54 |  |  |  | 0.088 | 0.088 |  | 0.119 | 0.119
|  | 13.7 |  |  |  | 2.24 | 2.24 |  | 3.02 | 3.02
| 3/8 | 0.675 |  |  |  | 0.091 | 0.091 |  | 0.126 | 0.126
|  | 17.1 |  |  |  | 2.31 | 2.31 |  | 3.2 | 3.2
| 1/2 | 0.84 |  |  |  | 0.109 | 0.109 |  | 0.147 | 0.147 |  |  |  | 0.187 | 0.294
|  | 21.3 |  |  |  | 2.77 | 2.77 |  | 3.73 | 3.73 |  |  |  | 4.75 | 7.47
| 3/4 | 1.05 |  |  |  | 0.113 | 0.113 |  | 0.154 | 0.154 |  |  |  | 0.219 | 0.308
|  | 26.7 |  |  |  | 2.87 | 2.87 |  | 3.91 | 3.91 |  |  |  | 5.56 | 7.82
| 1 | 1.315 |  |  |  | 0.133 | 0.133 |  | 0.179 | 0.179 |  |  |  | 0.25 | 0.358
|  | 33.4 |  |  |  | 3.38 | 3.38 |  | 4.55 | 4.55 |  |  |  | 6.35 | 9.09
| 1.25 | 1.66 |  |  |  | 0.14 | 0.14 |  | 0.191 | 0.191 |  |  |  | 0.25 | 0.382
|  | 42.2 |  |  |  | 3.56 | 3.56 |  | 4.85 | 4.85 |  |  |  | 6.35 | 9.7
| 1.5 | 1.9 |  |  |  | 0.145 | 0.145 |  | 0.2 | 0.2 |  |  |  | 0.281 | 0.4
|  | 48.3 |  |  |  | 3.68 | 3.68 |  | 5.08 | 5.08 |  |  |  | 7.14 | 10.2
| 2 | 2.375 |  |  |  | 0.154 | 0.154 |  | 0.218 | 0.218 |  |  |  | 0.344 | 0.436
|  | 60.3 |  |  |  | 3.91 | 3.91 |  | 5.54 | 5.54 |  |  |  | 8.74 | 11.1
| 2.5 | 2.875 |  |  |  | 0.203 | 0.203 |  | 0.276 | 0.276 |  |  |  | 0.375 | 0.552
|  | 73 |  |  |  | 5.16 | 5.16 |  | 7.01 | 7.01 |  |  |  | 9.52 | 14
| 3 | 3.5 |  |  |  | 0.216 | 0.216 |  | 0.3 | 0.3 |  |  |  | 0.438 | 0.6
|  | 88.9 |  |  |  | 5.49 | 5.49 |  | 7.62 | 7.62 |  |  |  | 11.1 | 15.2
| 3.5 | 4 |  |  |  | 0.226 | 0.226 |  | 0.318 | 0.318
|  | 102 |  |  |  | 5.74 | 5.74 |  | 8.08 | 8.08
| 4 | 4.5 |  |  |  | 0.237 | 0.237 |  | 0.337 | 0.337 |  | 0.438 |  | 0.531 | 0.674
|  | 114 |  |  |  | 6.02 | 6.02 |  | 8.56 | 8.56 |  | 11.1 |  | 13.5 | 17.1
| 5 | 5.563 |  |  |  | 0.258 | 0.258 |  | 0.375 | 0.375 |  | 0.5 |  | 0.625 | 0.75
|  | 141 |  |  |  | 6.55 | 6.55 |  | 9.52 | 9.52 |  | 12.7 |  | 15.9 | 19
| 6 | 6.625 |  |  |  | 0.28 | 0.28 |  | 0.432 | 0.432 |  | 0.562 |  | 0.719 | 0.864
|  | 168 |  |  |  | 7.11 | 7.11 |  | 11 | 11 |  | 14.3 |  | 18.3 | 21.9
| 8 | 8.625 |  | 0.25 | 0.277 | 0.322 | 0.322 | 0.406 | 0.5 | 0.5 | 0.594 | 0.719 | 0.812 | 0.906 | 0.875
|  | 219 |  | 6.35 | 7.04 | 8.18 | 8.18 | 10.3 | 12.7 | 12.7 | 15.1 | 18.3 | 20.6 | 23 | 22.2
| 10 | 10.75 |  | 0.25 | 0.307 | 0.365 | 0.365 | 0.5 | 0.5 | 0.594 | 0.719 | 0.844 | 1 | 1.125 | 1
|  | 273 |  | 6.35 | 7.8 | 9.27 | 9.27 | 12.7 | 12.7 | 15.1 | 18.3 | 21.4 | 25.4 | 28.6 | 25.4
| 12 | 12.75 |  | 0.25 | 0.33 | 0.375 | 0.406 | 0.562 | 0.5 | 0.688 | 0.844 | 1 | 1.125 | 1.312 | 1
|  | 324 |  | 6.35 | 8.38 | 9.52 | 10.3 | 14.3 | 12.7 | 17.5 | 21.4 | 25.4 | 28.6 | 33.3 | 25.4
| 14 | 14 | 0.25 | 0.312 | 0.375 | 0.375 | 0.438 | 0.594 | 0.5 | 0.75 | 0.938 | 1.094 | 1.25 | 1.406
|  | 356 | 6.35 | 7.92 | 9.52 | 9.52 | 11.1 | 15.1 | 12.7 | 19 | 23.8 | 27.8 | 31.8 | 35.7
| 16 | 16 | 0.25 | 0.312 | 0.375 | 0.375 | 0.5 | 0.656 | 0.5 | 0.844 | 1.031 | 1.219 | 1.438 | 1.594
|  | 406 | 6.35 | 7.92 | 9.52 | 9.52 | 12.7 | 16.7 | 12.7 | 21.4 | 26.2 | 31 | 36.5 | 40.5
| 18 | 18 | 0.25 | 0.312 | 0.438 | 0.375 | 0.562 | 0.75 | 0.5 | 0.938 | 1.156 | 1.375 | 1.562 | 1.781
|  | 457 | 6.35 | 7.92 | 11.1 | 9.52 | 14.3 | 19 | 12.7 | 23.8 | 29.4 | 34.9 | 39.7 | 45.2
| 20 | 20 | 0.25 | 0.375 | 0.5 | 0.375 | 0.594 | 0.812 | 0.5 | 1.031 | 1.281 | 1.5 | 1.75 | 1.969
|  | 508 | 6.35 | 9.52 | 12.7 | 9.52 | 15.1 | 20.6 | 12.7 | 26.2 | 32.5 | 38.1 | 44.4 | 50
| 22 | 22 | 0.25 | 0.375 | 0.5 | 0.375 |  | 0.875 | 0.5 | 1.125 | 1.375 | 1.625 | 1.875 | 2.125
|  | 559 | 6.35 | 9.52 | 12.7 | 9.52 |  | 22.2 | 12.7 | 28.6 | 34.9 | 41.3 | 47.6 | 54
| 24 | 24 | 0.25 | 0.375 | 0.562 | 0.375 | 0.688 | 0.969 | 0.5 | 1.219 | 1.531 | 1.812 | 2.062 | 2.344
|  | 610 | 6.35 | 9.52 | 14.3 | 9.52 | 17.5 | 24.6 | 12.7 | 31 | 38.9 | 46 | 52.4 | 59.5
| 30 | 30 | 0.312 | 0.5 | 0.625 | 0.375 |  |  | 0.5
|  | 762 | 7.92 | 12.7 | 15.9 | 9.52 |  |  | 12.7
| 32 | 32 | 0.312 | 0.5 | 0.625 | 0.375 | 0.688
|  | 813 | 7.92 | 12.7 | 15.9 | 9.52 | 17.5
| 34 | 34 | 0.312 | 0.5 | 0.625 | 0.375 | 0.688
|  | 864 | 7.92 | 12.7 | 15.9 | 9.52 | 17.5
| 36 | 36 | 0.312 | 0.5 | 0.625 | 0.375 | 0.75
|  | 914 | 7.92 | 12.7 | 15.9 | 9.52 | 19
| 42 | 42 |  | 0.5 | 0.625 | 0.375 | 0.75
|  | 1067 |  | 12.7 | 15.9 | 9.52 | 19