## Hydrodynamic Noise ABC
Control Valve Hydrodynamic Noise | Calculation method by Hans D. Baumann
ABC Method | Worksheet by Jon F. Monsen
USER INTERFACE
|  | Variable | User inputs
| Unit | Name | Case 1 | Case 2 | Case 3 | Case 4
Process Parameters
Inlet pressurre, P1 | psia | P_1_ | 100 | 100 | 100 | 100
Outlet pressure, P2 | psia | P_2_ | 40 | 40 | 40 | 40
Liquid vapor pressure, Pv | psia | P_v_ | 0.5 | 0.5 | 0.5 | 0.5
Valve/Pipe Parameters
Downstream pipe diameter | inch | D_ | 6 | 6 | 6 | 6
Valve capacity, Cv |  | C_v | 85 | 85 | 85 | 85
Liquid pressure recovery factor, FL |  | F_L | 0.7 | 0.7 | 0.7 | 0.7
Diff press ratio of incipient cavitation noise, xFz |  | x_Fz | 0.28 | 0.28 | 0.28 | 0.28
Modifiers
Downstream Pipe schedule (40=0, 80=4 160=8 ) | dB | ps | 0 | 0 | 0 | 0
Valve Style, rw (globe = 3, others = 0) | dB | rw | 0 | 0 | 0 | 0
Calculated SPL (LpAe1m) | dB(A) | SPL | 90.3987 | 90.3987 | 90.3987 | 90.3987
Units Selection
Presssure: 1 = psia 2 = bar 3 = kPa | 1
Size: 1 = inch 2 = mm | 1
NO USER INPUT IS REQUIRED IN THIS SECTION
WORKSHEET UNITS CONVERTED TO UNITS REQUIRED BY THE CALCULATIONS. ALL OTHER VARIABLES ARE INDEPENDENT OF UNITS
Variable name
P_1(Calculation uses psia) |  | P_1 | 100 | 100 | 100 | 100
P_2 (Calculation uses psia) |  | P_2 | 40 | 40 | 40 | 40
P_v (Calculation uses psia) |  | p_v | 0.5 | 0.5 | 0.5 | 0.5
D (Calculation uses inch) |  | D | 6 | 6 | 6 | 6
FINAL CALCULATIONS
X, Pressure ratio |  | X | 0.60302 | 0.60302 | 0.60302 | 0.60302
X at max cavitation, Xy |  | Xy | 0.64 | 0.64 | 0.64 | 0.64
A | dB | A | 14.7026 | 14.7026 | 14.7026 | 14.7026
B | dB | B | 35 | 35 | 35 | 35
C1 | dB | C_1 | 20.7059 | 20.7059 | 20.7059 | 20.7059
C2 | dB | C_2 | 19.9902 | 19.9902 | 19.9902 | 19.9902
C3 | dB | C_3 | 0 | 0 | 0 | 0
C = C1+C2-C3 | dB(A) | C_ | 40.6961 | 40.6961 | 40.6961 | 40.6961
LpAe1m = A+B+C-rw-ps | dB(A) | LpAe1m | 90.3987 | 90.3987 | 90.3987 | 90.3987
(This calculated value of noise is copied to the user interface.)

## Calculation Method
ABC Method for predicting control vavle hydrodynamic noise.
Calculation method by Hans D. Baumann
Excel worksheet by Jon Monsen
P_1 upstram pressure (Calculation uses psia)
P_2 downstream pressure (Calculation uses psia)
P_v liquid vapor pressure (Calculation uses psia)
downstram pipe size (Calculation uses inch)
The worksheet includes the capability to easily specify other units that are often used:
Pressure: psia, bar, kPa(a), Pipe size inch, mm
Initial intermediate calculations:
X = (P1 – P2)/(P1- Pv)
Xy = (1.00+Xfz)/2
A = 8 log(D) + 12log(CV/D2) +4 in dB
B = 35 log(P1) – 35
C1 = 30 log(10X), X maximim = FL2.
C2 if X is larger than Xfz but below Xy then
C2 = 60 log(X/Xfz). if X is above Xy then
C2 = 60 log(Xy/Xfz); otherwise use zero.
C3 if X is larger than Xy then c3 = 120 log(X/Xy), otherwise use zero
C = C1 + C2 - C3 in dB(A).
The final calculation combines the above intermediate calculations to obtain the estimated hydrodynamic noise,
LpAe1m = A + B + C - rw - ps
Nomenclature:
X: Pressure ratio
Xy: X at max. cavitation
A: SPL due to downstream pipe size and Cv
B: SPL due to upstream pressure
C1: Turbulent sound level
C2: Correction to C when X is larger than Xfz
C3: Decreasing sound level if X is greater than Xy
C: C1 + C2 - C3
FL: Valve Liquid pressure recovery factor at operating valve travel
P1, P2: pressure upstream and downstream of valve (psia)
PV, vapor pressure of the liquid
D: Pipe size downstream of valve (inch)
Cv: Valve flow coefficient at operating valve travel
rw: SPL correction for globe valves, rw = 3. For all others rw = 0
ps: Correction for downstream pipe schedule. (40 = 0, 80 = 4, 160 = 8)

## Stop Cavitation Valve World
This is the December 2019 Valve World Magazine article that the worksheet is base on